## 500F C EUT
[16 empty] | Issued: | 2015-12-31
[16 empty] | Last Revised: | 2017-10-10
ID Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage | Number of Phases | SCCR, kA | Full Load Current, A | HP rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP Rating | Enclosure Volume, Cu Ft
AB500F-A…-EUTB42_01-..200V_C_140G-G6*_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..200V_C_140G-G3*_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..200V_C_50kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 2.5 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..230V_C_140G-G6*_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..230V_C_140G-G3*_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..230V_C _50kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 2.2 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..480V_C_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..480V_C_35kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.1 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..480V_C_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.1 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..600V_C_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..600V_C_18kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 0.9 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..600V_C_14kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 0.9 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..200V_C_140G-G6*_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..200V_C_140G-G3*_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..200V_C _50kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 3.7 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..230V_C_140G-G6*_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..230V_C_140G-G3*_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..230V_C_50kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 3.2 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..480V_C_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..480V_C_35kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.6 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..480V_C_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.6 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..600V_C_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..600V_C_18kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 1.3 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..600V_C_14kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 1.3 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..200V_C_140G-G6*_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..200V_C_140G-G3*_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..200V_C_50kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 4.8 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..230V_C_140G-G6*_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..230V_C_140G-G3*_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..230V_C_50kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 4.2 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..480V_C_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..480V_C_35kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 2.1 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..480V_C_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 2.1 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..600V_C_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..600V_C_18kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 1.7 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..600V_C_14kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 1.7 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..200V_C_140G-G6*_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..200V (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1-1/2HP-..200V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..200V_C_140G-G3*_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..200V (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1-1/2HP-..200V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..200V_C_50kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 6.9 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..200V (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1-1/2HP-..200V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..230V_C_140G-G6*_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..230V (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1-1/2HP-..230V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..230V_C_140G-G3*_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..230V (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1-1/2HP-..230V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..230V_C_50kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..230V (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1-1/2HP-..230V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..480V_C_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..480V (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1-1/2HP-..480V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..480V_C_35kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..480V (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1-1/2HP-..480V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..480V_C_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..480V (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1-1/2HP-..480V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..600V_C _25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..600V_C_18kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 2.4 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..600V_C_14kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 2.4 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..200V_C_140G-G6*_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..200V (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_2HP-..200V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..200V_C_140G-G3*_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..200V (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_2HP-..200V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..200V_C_50kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 7.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..200V (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_2HP-..200V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..230V_C_140G-G6*_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..230V (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_2HP-..230V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..230V_C_140G-G3*_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..230V (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_2HP-..230V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..230V_C_50kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..230V (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_2HP-..230V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..480V_C_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..480V (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_2HP-..480V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..480V_C_35kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3.4 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..480V (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_2HP-..480V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..480V_C_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3.4 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..480V (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_2HP-..480V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..600V_C_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..600V_C_18kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 2.7 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..600V_C_14kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 2.7 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..200V_C_140G-G6*_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..200V (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3HP-..200V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..200V_C_140G-G3*_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..200V (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3HP-..200V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..200V_C_50kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 11 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..200V (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3HP-..200V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..230V_C_140G-G6*_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..230V (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3HP-..230V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..230V_C_140G-G3*_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..230V (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3HP-..230V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..230V_C_50kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 9.6 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..230V (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3HP-..230V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..480V_C_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..480V (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3HP-..480V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..480V_C_35kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 4.8 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..480V (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3HP-..480V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..480V_C_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 4.8 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..480V (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3HP-..480V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..600V_C_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..600V_C_18kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 3.9 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..600V_C_14kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 3.9 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_07-..480V_C_65kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..480V (AB500DAB007) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_5HP-..480V (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_07-..480V_C_35kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..480V (AB500DAB007) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_5HP-..480V (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_07-..480V_C_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..480V (AB500DAB007) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_5HP-..480V (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_07-..600V_C_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_07-..600V_C_18kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 6.1 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_07-..600V_C_14kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 6.1 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..200V_C_140G-G6*_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..200V (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_5HP-..200V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..200V_C_140G-G3*_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..200V (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_5HP-..200V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..200V_C_50kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 17.5 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..200V (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_5HP-..200V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..230V_C_140G-G6*_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..230V (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_5HP-..230V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..230V_C_140G-G63*_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..230V (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_5HP-..230V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..230V_C_50kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 15.2 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..230V (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_5HP-..230V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..480V_C_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..480V (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_5HP-..480V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..480V_C_35kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..480V (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_5HP-..480V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..480V_C_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..480V (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_5HP-..480V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..600V_C_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..600V_C_18kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 6.1 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..600V_C _14kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 6.1 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..230V_C_140G-G6*_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..200V (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_7-1/2HP-..200V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..230V_C_140G-G3*_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..200V (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_7-1/2HP-..200V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..230V_C_50kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 22 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..200V (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_7-1/2HP-..200V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..480V_C_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..480V (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_7-1/2HP-..480V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..480V_C_35kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 11 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..480V (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_7-1/2HP-..480V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..480V_C_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 11 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..480V (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_7-1/2HP-..480V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..600V_C_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..600V_C_18kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 9 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..600V_C_14kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 9 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_10-..480V_C_65kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..480V (AB500DAB010) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_10HP-..480V (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_10-..480V_C_35kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..480V (AB500DAB010) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_10HP-..480V (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_10-..480V_C_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..480V (AB500DAB010) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_10HP-..480V (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_10-..600V_C_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_10-..600V_C_18kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 11 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_10-..600V_C_14kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 11 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-C…-EUTC42_11-..200V_C_140G-G6* _65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..200V_C_140G-G3*_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..200V_C_50kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*50 | 200 | 3 | 50 | 50 | --- | 200 | 3 | 50 | 32.2 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..230V_C_140G-G6*_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..230V_C_140G-G3*_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..230V_C_50kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*50 | 230 | 3 | 50 | 50 | --- | 230 | 3 | 50 | 28 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..480V_C_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..480V (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_10HP-..480V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..480V_C _35kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..480V (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_10HP-..480V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..480V_C_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..480V (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_10HP-..480V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..600V_C_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..600V_C_18kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 11 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..600V_C14kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 11 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..230V_C_140G-G6_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..230V (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_15HP-..230V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..230V_C_140G-G3_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..230V (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_15HP-..230V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..230V_C_50kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 42 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..230V (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_15HP-..230V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..480V_C_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..480V (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_15HP-..480V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..480V_C_35kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..480V (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_15HP-..480V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..480V_C_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..480V (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_15HP-..480V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..600V_C_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..600V_C_18kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 18 | 17 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..600V_C_14kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 17 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_13-..480V_C_65kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..480V (AB500DAB013) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_20HP-..480V (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_13-..480V_C_35kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..480V (AB500DAB013) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_20HP-..480V (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_13-..480V_C_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..480V (AB500DAB013) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_20HP-..480V (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_13-..600V_C_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_13-..600V_C_18kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 22 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_13-..600V_C_14kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 22 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_14-..480V_C_65kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..480V (AB500DAB014) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_25HP-..480V (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_14-..480V_C_35kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..480V (AB500DAB014) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_25HP-..480V (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_14-..480V_C_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..480V (AB500DAB014) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_25HP-..480V (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_14-..600V_C_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_14-..600V_C_18kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 27 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_14-..600V_C_14kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 27 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-D…-EUTD42_15-..200V_C_140G-G6*_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..200V_C_140G-G3*_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..200V_C_50kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 48.3 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..230V_C_140G-G6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..230V_C_140G-G3_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..230V_C_50kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 42 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..480V_C_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..480V (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_15HP-..480V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..480V_C_35kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..480V (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_15HP-..480V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..480V_C_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..480V (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_15HP-..480V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..600V_C_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..600V_C_18kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 17 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..600V_C_14kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 17 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..200V_C_140G-H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..200V_C_140G-H3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..200V_C_140G-H2_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..230V_C_140G-H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..230V_C_140G-H3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..230V_C_140G-H2_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..480V_C _65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..480V_C_35kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..480V_C_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..600V_C_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-J6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..600V_C_18kA (AB500DAB016) | C | CB | Allen Bradley | 140G-J3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 22 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..600V_C_14kA (AB500DAB016) | C | CB | Allen Bradley | 140G-J6*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 22 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..200V_C_140G-H6-65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..200V_C_140G-H3-65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..200V_C_140G-H2-65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..230V_C_140G-H6-65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..230V_C_140G-H3-65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..230V_C_140G-H2-65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..480V_C_140G-H6-65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..480V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_25HP-..480V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..480V_C_140G-H3-35kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..480V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_25HP-..480V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..480V_C_140G-H2-25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..480V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_25HP-..480V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..600V_C_140G-J6-25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-J6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..600V_C_140G-J3-18kA (AB500DAB017) | C | CB | Allen Bradley | 140G-J3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 27 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..600V_C_140G-J2-14kA (AB500DAB017) | C | CB | Allen Bradley | 140G-J2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 27 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..230V_C_140G-H6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..230V_C_140G-H3_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..230V_C_140G-H2_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..480V_C_140G-H6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..480V_C_140G-H3_35kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..480V_C_140G-H2_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..600V_C_140G-J6_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..600V_C_140G-J3_18kA (AB500DAB018) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 32 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..600V_C_140G-J2_14kA (AB500DAB018) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 32 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_19-..480V_C_140G-H6_65kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_19-..480V_C_140G-H3_35kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 52 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_19-..480V_C_140G-H2_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 52 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_19-..600V_C_140G-J6_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 41 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_19-..600V_C_140G-J3_18kA (AB500DAB019) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 41 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_19-..600V_C_140G-J2_14kA (AB500DAB019) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 41 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_20-..480V_C_140G-H6_65kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_20-..480V_C_140M-H3_35kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_20-..480V_C_140M-H2_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_20-..600V_C_140M-J6_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_20-..600V_C_140M-J3_18kA (AB500DAB020) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 52 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_20-..600V_C_140M-J2_14kA (AB500DAB020) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 52 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-E…-EUTE42_21-..200V_C_140G-J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..200V_C_140G-J3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..200V_C_140G-J2_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..230V_C_140G-J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..230V_C_140G-J3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..230V_C_140G-J2_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..480V_C_140G-J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..480V_C_140G-J3_35kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..480V_C_140G-I3_35kA (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..480V_C_140G-J2_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..480V_C_140G-I2_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..600V_C_140G-J6_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..600V_C_140G-J3_18kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 32 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..600V_C_140G-J2_14kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 32 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..230V_C_140G-J6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..230V_C_140G-J3_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..230V_C_140G-J2_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..480V_C_140G-J6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..480V_C_140G-J3_35kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..480V_C_140G-I3_35kA (AB500DAB022) | C | CB | Allen Bradley | 140G-I3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..480V_C_140G-J2_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..480V_C_140G-I2_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-I2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..600V_C_140G-J6_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..600V_C_140G-J3_18kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 52 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..600V_C_140G-J2_14kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 52 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..480V_C_140G-J6_65kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..480V_C_140G-J3_35kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..480V_C_140G-I3_35kA (AB500DAB023) | C | CB | Allen Bradley | 140G-I3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..480V_C_140G-J2_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..480V_C_140G-I2_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-I2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..600V_C_140G-J6_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 62 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..600V_C_140G-J3_18kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 62 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..600V_C_140G-J2_14kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 62 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_24-..480V_C_140G-J6-65kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_24-..480V_C_140G-J3-35kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_24-..480V_C_140G-I3-35kA (AB500DAB024) | C | CB | Allen Bradley | 140G-I3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_24-..480V_C_140G-J2-25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_24-..480V_C_140G-I2-25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-I2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_24-..600V_C_140G-J6-25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_24-..600V_C_140G-J3-18kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 77 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_24-..600V_C_140G-J2-14kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 77 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_25-..600V_C_140G-J6_25kA (AB500DAB025) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 99 | 100 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_25-..600V_C_140G-J3_18kA (AB500DAB025) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 99 | 100 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_25-..600V_C_140G-J2_14kA (AB500DAB025) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 99 | 100 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-F…-EUTF42_26-..200V_C_140G-K6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K6*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 200 | 3 | 10 | 221 | 75
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 200 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_26-..200V_C_140G-K3_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K3*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 200 | 3 | 10 | 221 | 75
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 200 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_26-..200V_C_140G-K2_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K2*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 200 | 3 | 10 | 221 | 75
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 200 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_26-..230V_C_140G-K6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_26-..230V_C_140G-K3_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K3*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_26-..230V_C_140G-K2_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K2*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_26-..480V_C_140G-K6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_26-..480V_C_140G-K3_35kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K3*300 | 480 | 3 | 35 | 300 | --- | 480 | 3 | 35 | 96 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_26-..480V_C_140G-K2_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K2*300 | 480 | 3 | 25 | 300 | --- | 480 | 3 | 25 | 96 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_26-..600V_C_140G-J6_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 125 | ---
AB500F-F…-EUTF42_26-..600V_C_140G-J3_18kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 77 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 125 | ---
AB500F-F…-EUTF42_26-..600V_C_140G-J2_14kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 77 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 125 | ---
AB500F-F…-EUTF42_27-..230V_C_140G-K6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_27-..230V_C_140G-K3_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K3*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_27-..230V_C_140G-K2_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K2*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_27-..480V_C_140G-K6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_27-..480V_C_140G-K3_35kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K3*300 | 480 | 3 | 35 | 300 | --- | 480 | 3 | 35 | 124 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_27-..480V_C_140G-K2_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K2*300 | 480 | 3 | 25 | 300 | --- | 480 | 3 | 25 | 124 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_27-..600V_C_140G-J6_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_27-..600V_C_140G-J3_18kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 99 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_27-..600V_C_140G-J2_14kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 99 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_28-..600V_C_140G-J6_25kA (AB500DAB028) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_28-..600V_C_140G-J3_18kA (AB500DAB028) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 192 | 200 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_28-..600V_C_140G-J2_14kA (AB500DAB028) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 192 | 200 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-A…-EUTB42_01-..200V_C_2_140G-H6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..200V_C_2_140G-H3_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..200V_C_2_140G-H2_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..230V_C_2_140G-H6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..230V_C_2_140G-H3_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..230V_C_2_140G-H2_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..480V_C_2_140G-H6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..480V_C_2_140G-H3_35kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.1 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..480V_C_2_140G-H2_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.1 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..200V_C_2_140G-H6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..200V_C_2_140G-H3_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..200V_C_2_140G-H2_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..230V_C_2_140G-H6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..230V_C_2_140G-H3_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..230V_C_2_140G-H2_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..480V_C_2_140G-H6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..480V_C_2_140G-H3_35kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.6 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..480V_C_2_140G-H2_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.6 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..200V_C_2_140G-H6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..200V_C_2_140G-H3_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..200V_C_2_140G-H2_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..230V_C_2_140G-H6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..230V_C_2_140G-H3_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..230V_C_2_140G-H2_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..480V_C_2_140G-H6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..480V_C_2_140G-H3_35kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 2.1 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..480V_C_2_140G-H2_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 2.1 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..200V_C_2_140G-H6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..200V_C_2_140G-H3_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..200V_C_2_140G-H2_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..230V_C_2_140G-H6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..230V_C_2_140G-H3_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..230V_C_2_140G-H2_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..480V_C_2_140G-H6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..480V_C_2_140G-H3_35kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..480V_C_2_140G-H2_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..200V_C_2_140G-H6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..200V_C_2_140G-H3_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..200V_C_2_140G-H2_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..230V_C_2_140G-H6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..230V_C_2_140G-H3_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..230V_C_2_140G-H2_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..480V_C_2_140G-H6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..480V_C_2_140G-H3_35kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3.4 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..480V_C_2_140G-H2_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3.4 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..200V_C_2_140G-H6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..200V_C_2_140G-H3_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..200V_C_2_140G-H2_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..230V_C_2_140G-H6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..230V_C_2_140G-H4_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..230V_C_2_140G-H2_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..480V_C_2_140G-H6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..480V_C_2_140G-H3_35kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 4.8 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..480V_C_2_140G-H2_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 4.8 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_07-..480V_C_2_140G-H6_65kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_07-..480V_C_2_140G-H3_35kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H36*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_07-..480V_C_2_140G-H2_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..200V_C_2_140G-H6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..200V_C_2_140G-H3_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..200V_C_2_140G-H2_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..230V_C_2_140G-H6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..230V_C_2_140G-H3_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..230V_C_2_140G-H2_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..480V_C_2_140G-H6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..480V_C_2_140G-H3_35kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..480V_C_2_140G-H2_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..200V_C_2_140G-H6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 25.3 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..200V_2 (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_7-1/2HP-..200V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..200V_C_2_140G-H3_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 25.3 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..200V_2 (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_7-1/2HP-..200V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..200V_C_2_140G-H2_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 25.3 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..200V_2 (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_7-1/2HP-..200V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..480V_C_2_140G-H6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..480V_C_2_140G-H3_35kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 11 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..480V_C_2_140G-H2_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 11 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_10-..480V_C_2_140G-H6_65kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_10-..480V_C_2_140G-H3_35kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_10-..480V_C_2_140G-H2_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-C…-EUTC42_11-..200V_C_2_140G-H6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..200V_C_2_140G-H3_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..200V_C_2_140G-H2_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..230V_C_2_140G-H6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..230V_C_2_140G-H3_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..230V_C_2_140G-H2_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..480V_C_2_140G-H6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..480V_C_2_140G-H3_35kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..480V_C_2_140G-H2_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..230V_C_2_140G-H6_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..230V_2 (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_15HP-..230V_2 (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..230V_C_2_140G-H3_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..230V_2 (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_15HP-..230V_2 (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..230V_C_2_140G-H2_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..230V_2 (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_15HP-..230V_2 (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..480V_C_2_140G-H6_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..480V_C_2_140G-H3_35kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..480V_C_2_140G-H2_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_13-..480V_C_2_140G-H6_65k (AB500DAB013) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_13-..480V_C_2_140G-H3_35k (AB500DAB013) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_13-..480V_C_2_140G-H2_25k (AB500DAB013) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_14-..480V_C_2_140G-H6_65k (AB500DAB014) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_14-..480V_C_2_140G-H3_35k (AB500DAB014) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_14-..480V_C_2_140G-H2_25k (AB500DAB014) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-D…-EUTD42_15-..200V_C_2_140G-H6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..200V_C_2_140G-H3_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..200V_C_2_140G-H2_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..200V_C_2_140G-I3_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..200V_C_2_140G-I2_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-I2*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..230V_C_2_140G-H6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..230V_C_2_140G-H3_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..230V_C_2_140G-H2_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..230V_C_2_140G-I3_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..230V_C_2_140G-I2_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..480V_C_2_140G-H6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..480V_C_2_140G-H3_35kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 35 | 50
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..480V_C_2_140G-H2_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 25 | 50
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..200V_C_2_140G-H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..200V_C_2_140G-H3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..200V_C_2_140G-H2_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..200V_C_2_140G-I3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..200V_C_2_140G-I2_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-I2*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..230V_C_2_140G-H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..230V_C_2_140G-H3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..230V_C_2_140G-H2_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..230V_C_2_140G-I3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..230V_C_2_140G-I2_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..480V_C_2_140G-H2_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..480V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_20HP-..480V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..200V_C_2_140G-H6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..200V_C_2_140G-H3_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..200V_C_2_140G-H2_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..200V_C_2_140G-I3_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..200V_C_2_140G-I2_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-I2*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..230V_C_2_140G-H6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..230V_C_2_140G-H3_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..230V_C_2_140G-H2_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..230V_C_2_140G-I3_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..230V_C_2_140G-I2_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..480V_C_2_140G-H2_25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..480V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_25HP-..480V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..230V_C_2_140G-H6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..230V_C_2_140G-H3_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..230V_C_2_140G-H2_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..230V_C_2_140G-I3_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..230V_C_2_140G-I2_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..480V_C_2_140G-H6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..480V_C_2_140G-H3_35kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..480V_C_2_140G-H2_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_19-..480V_C_2_140G-H6_65kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_19-..480V_C_2_140G-H3_35kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 52 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_19-..480V_C_2_140G-H2_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 52 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_20-..480V_C_2_140G-H6_65kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_20-..480V_C_2_140G-H3_35kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_20-..480V_C_2_140G-H2_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-E…-EUTE42_21-..200V_C_2_140G-J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..200V_C_2_140G-J3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..200V_C_2_140G-J2_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..200V_C_2_140G-I3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..200V_C_2_140G-I2_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*150 | 200 | 3 | 50 | 150 | --- | 200 | 3 | 50 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..230V_C_2_140G-J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..230V_C_2_140G-J3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..230V_C_2_140G-J2_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..230V_C_2_140G-I3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..230V_C_2_140G-I2_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*125 | 230 | 3 | 50 | 125 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..480V_C_2_140G-J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..480V_C_2_140G-J3_35kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..480V_C_2_140G-I3_35kA (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..480V_C_2_140G-J2_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..480V_C_2_140G-I2_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..230V_C_2_140G-J6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*150 | 230 | 3 | 65 | 150 | --- | 230 | 3 | 65 | 143 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..230V_C_2_140G-J3_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*150 | 230 | 3 | 65 | 150 | --- | 230 | 3 | 65 | 143 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..230V_C_2_140G-J2_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*150 | 230 | 3 | 65 | 150 | --- | 230 | 3 | 65 | 143 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..230V_C_2_140G-I3_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-I3*150 | 230 | 3 | 65 | 150 | --- | 230 | 3 | 65 | 143 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..230V_C_2_140G-I2_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-I2*150 | 230 | 3 | 50 | 150 | --- | 230 | 3 | 50 | 143 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..480V_C_2_140G-J6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..480V_C_2_140G-J3_35kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..480V_C_2_140G-I3_35kA (AB500DAB022) | C | CB | Allen Bradley | 140G-I3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..480V_C_2_140G-J2_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..480V_C_2_140G-I2_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-I2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..480V_C_2_140G-J6_65kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..480V_C_2_140G-J3_35kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..480V_C_2_140G-I3_35kA (AB500DAB023) | C | CB | Allen Bradley | 140G-I3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..480V_C_2_140G-J2_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..480V_C_2_140G-I2_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-I2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_24-..480V_C_2_140G-J6_65kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_24-..480V_C_2_140G-J3_35kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_24-..480V_C_2_140G-I3_35kA (AB500DAB024) | C | CB | Allen Bradley | 140G-I3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_24-..480V_C_2_140G-J2_25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_24-..480V_C_2_140G-I2_25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-I2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-F…-EUTF42_26-..600V_C_2_140G-J6_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_26-..600V_C_2_140G-J3_18kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 77 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_26-..600V_C_2_140G-J2_14kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 77 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_27-..600V_C_2_140G-J6_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_27-..600V_C_2_140G-J3_18kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 99 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_27-..600V_C_2_140G-J2_14kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 99 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_29-..600V_C_2_140G-J6_25kA (AB500DAB029) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_29-..600V_C_2_140G-J3_18kA (AB500DAB029) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 192 | 200 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_29-..600V_C_2_140G-J2_14kA (AB500DAB029) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 192 | 200 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-D…-EUTD42_30-..230V_C_2_140G-J6_65kA (AB500DAB030) | C | CB | Allen Bradley | 140G-J6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_30-..230V_C_2_140G-J3_65kA (AB500DAB030) | C | CB | Allen Bradley | 140G-J3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_30-..230V_C_2_140G-J3_65kA (AB500DAB030) | C | CB | Allen Bradley | 140G-J2*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_30-..230V_C_2_140G-I3_65kA (AB500DAB030) | C | CB | Allen Bradley | 140G-I3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_30-..230V_C_2_140G-I3_65kA (AB500DAB030) | C | CB | Allen Bradley | 140G-I2*125 | 230 | 3 | 50 | 125 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-E…-EUTE42_31-..230V_C_2_140G-J6_65kA (AB500DAB031) | C | CB | Allen Bradley | 140G-J6*-175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB031) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB031) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_31-..230V_C_2_140G-J3_65kA (AB500DAB031) | C | CB | Allen Bradley | 140G-J3*-175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB031) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB031) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_31-..230V_C_2_140G-J2_65kA (AB500DAB031) | C | CB | Allen Bradley | 140G-J2*-175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB031) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB031) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-A…-EUTB42_01-..600V_C_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..600V_C_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..600V_C_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..600V_C _25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..600V_C_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..600V_C_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_07-..600V_C_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..600V_C_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..600V_C_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_10-..600V_C_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-C…-EUTC42_11-..600V_C_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..600V_C_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_13-..600V_C_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_14-..600V_C_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-D…-EUTD42_15-..600V_C_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..200V_C_140G-HC6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..230V_C_140G-HC6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..230V_C_140G-_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..230V_C_140G-_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..480V_C _65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..600V_C_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-JC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..200V_C_140G-HC6-65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..230V_C_140G-HC6-65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..600V_C_140G-JC6-25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-JC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..230V_C_140G-HC6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..480V_C_140G-HC6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..600V_C_140G-JC6_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_19-..480V_C_140G-HC6_65kA (AB500DAB019) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_19-..600V_C_140G-JC6_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 41 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_20-..480V_C_140G-HC6_65kA (AB500DAB020) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_20-..600V_C_140M-JC6_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-E…-EUTE42_21-..200V_C_140G-JC6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..230V_C_140G-JC6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..480V_C_140G-JC6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..600V_C_140G-JC6_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..230V_C_140G-JC6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..480V_C_140G-JC6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..600V_C_140G-JC6_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..480V_C_140G-JC6_65kA (AB500DAB023) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..600V_C_140G-JC6_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 62 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_24-..480V_C_140G-JC6-65kA (AB500DAB024) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_24-..600V_C_140G-JC6-25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_25-..600V_C_140G-JC6_25kA (AB500DAB025) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 99 | 100 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-F…-EUTF42_26-..200V_C_140G-KC6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-KC6*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 200 | 3 | 10 | 221 | 75
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 200 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_26-..230V_C_140G-KC6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-KC6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_26-..480V_C_140G-KC6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-KC6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_26-..600V_C_140G-JC6_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 125 | ---
AB500F-F…-EUTF42_27-..230V_C_140G-KC6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-KC6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_27-..480V_C_140G-KC6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-KC6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_27-..600V_C_140G-JC6_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_28-..600V_C_140G-JC6_25kA (AB500DAB028) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-A…-EUTB42_01-..200V_C_2_140G-HC6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..230V_C_2_140G-HC6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..480V_C_2_140G-HC6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..200V_C_2_140G-HC6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..230V_C_2_140G-HC6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..480V_C_2_140G-HC6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..200V_C_2_140G-HC6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..230V_C_2_140G-HC6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..480V_C_2_140G-HC6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..200V_C_2_140G-HC6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..230V_C_2_140G-HC6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..480V_C_2_140G-HC6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..200V_C_2_140G-HC6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..230V_C_2_140G-HC6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..480V_C_2_140G-HC6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..200V_C_2_140G-HC6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..230V_C_2_140G-HC6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..480V_C_2_140G-HC6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_07-..480V_C_2_140G-HC6_65kA (AB500DAB007) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..200V_C_2_140G-HC6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..230V_C_2_140G-HC6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..480V_C_2_140G-HC6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..200V_C_2_140G-HC6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 25.3 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..200V_2 (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_7-1/2HP-..200V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..480V_C_2_140G-HC6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_10-..480V_C_2_140G-HC6_65kA (AB500DAB010) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-C…-EUTC42_11-..200V_C_2_140G-HC6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..230V_C_2_140G-HC6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..480V_C_2_140G-HC6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..230V_C_2_140G-HC6_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..230V_2 (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_15HP-..230V_2 (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..480V_C_2_140G-HC6_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_13-..480V_C_2_140G-HC6_65k (AB500DAB013) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_14-..480V_C_2_140G-HC6_65k (AB500DAB014) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-D…-EUTD42_15-..200V_C_2_140G-HC6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..230V_C_2_140G-HC6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..480V_C_2_140G-HC6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..200V_C_2_140G-HC6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..230V_C_2_140G-HC6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..480V_C_2_140G-HC6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..480V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_20HP-..480V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..200V_C_2_140G-HC6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..230V_C_2_140G-HC6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..480V_C_2_140G-HC6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..480V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_25HP-..480V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..230V_C_2_140G-HC6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..480V_C_2_140G-HC6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_19-..480V_C_2_140G-HC6_65kA (AB500DAB019) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_20-..480V_C_2_140G-HC6_65kA (AB500DAB020) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-E…-EUTE42_21-..200V_C_2_140G-JC6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..230V_C_2_140G-JC6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..480V_C_2_140G-JC6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..230V_C_2_140G-JC6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*150 | 230 | 3 | 65 | 150 | --- | 230 | 3 | 65 | 143 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..480V_C_2_140G-JC6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..480V_C_2_140G-JC6_65kA (AB500DAB023) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_24-..480V_C_2_140G-JC6_65kA (AB500DAB024) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-F…-EUTF42_26-..600V_C_2_140G-JC6_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_27-..600V_C_2_140G-JC6_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_29-..600V_C_2_140G-JC6_25kA (AB500DAB029) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-D…-EUTD42_30-..230V_C_2_140G-JC6_65kA (AB500DAB030) | C | CB | Allen Bradley | 140G-JC6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-E…-EUTE42_31-..230V_C_2_140G-JC6_65kA (AB500DAB031) | C | CB | Allen Bradley | 140G-JC6*-175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB031) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB031) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
Size 0-4; use Table 152 for W elements and Table 163 for J elements; Size 5 use Table 347 for W elements and Table 547 for J elements
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(7) = See Table 7 for minimum internal power wiring.
Table 7 - Minimum Internal Power Wiring
1/32in. thick thermoplastic insulation, rated 105C
Wire Code |  | Wire Size
7a |  | 10 AWG
7b |  | 10 AWG
7c |  | 8 AWG
7d |  | 4 AWG
7e |  | 1AWG
7f |  | 250 MCM

## 500F C E1+
[16 empty] | Issued: | 2015-12-31
[16 empty] | Last Revised: | 2017-10-10
ID Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage | Number of Phases | SCCR, kA | Full Load Current, A | HP rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP Rating | Enclosure Volume, CU Ft
AB500F-A…-E1+EEEC_01-..200V_C_140G_G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_01-..200V_C_140G_G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_01-..200V_C_140G-G2_50kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 2.5 | 0.5 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_01-..230V_C_140G_G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_01-..230V_C_140G-G3_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_01-..230V_C_140-G2_50kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 2.2 | 0.5 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_01-..480V_C_140G_G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_01-..480V_C_140G-G3_35kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_01-..480V_C_140-G2_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.1 | 0.5 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_01-..600V_C_140G_H6_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEBC | 600 | 3 | 5 | 0.2-1 | ---
AB500F-A…-E1+EEEC_01-..600V_C_140G-H3_18kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEBC | 600 | 3 | 5 | 0.2-1 | ---
AB500F-A…-E1+EEEC_01-..600V_C_140G-H2_14kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEBC | 600 | 3 | 5 | 0.2-1 | ---
AB500F-A…-E1+EEEC_02-..200V_C_140G_G6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_02-..200V_C_140G-G3_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_02-..200V_C_140-G2_50kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 3.7 | 0.75 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_02-..230V_C_140G_G6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_02-..230V_C_140G-G3_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_02-..230V_C_140-G2_50kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 3.2 | 0.75 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_02-..480V_C_140G_G6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_02-..480V_C_140G-G3_35kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_02-..480V_C_140-G2_25kA (AB500DAB002) | C | x | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.6 | 0.75 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_02-..600V_C_140G_H6_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_02-..600V_C_140G-H3_18kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_02-..600V_C_140G-H2_14kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_03-..200V_C_140G_G6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_03-..200V_C_140G-G3_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_03-..200V_C_140-G2_50kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 4.8 | 1 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_03-..230V_C_140G_G6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_03-..230V_C_140G-G3_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_03-..230V_C_140-G2_50kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 4.2 | 1 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_03-..480V_C_140G_G6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_03-..480V_C_140G-G3_35kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_03-..480V_C_140-G2_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 2.1 | 1 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_03-..600V_C_140G_H6_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_03-..600V_C_140G-H3_18kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_03-..600V_C_140G-H2_14kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..200V_C_140G_G6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..200V_C_140G-G3_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..200V_C_140-G2_50kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 6.9 | 1.5 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..230V_C_140G_G6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..230V_C_140G-G3_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..230V_C_140-G2_50kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6 | 1.5 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..480V_C_140G_G6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..480V_C_140G-G3_35kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..480V_C_140-G2_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3 | 1.5 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..600V_C_140G_H6_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..600V_C_140G-H3_18kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..600V_C_140G-H2_14kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_05-..200V_C_140G_G6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_05-..200V_C_140G-G3_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_05-..200V_C_140-G2_50kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 7.8 | 2 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_05-..230V_C_140G_G6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_05-..230V_C_140G-G3_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_05-..230V_C_140-G2_50kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6.8 | 2 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_05-..480V_C_140G_G6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_05-..480V_C_140G-G3_35kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_05-..480V_C_140-G2_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3.4 | 2 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_05-..600V_C_140G_H6_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_05-..600V_C_140G-H3_18kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_05-..600V_C_140G-H2_14kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_06-..200V_C_140G_G6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_06-..200V_C_140G-G3_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_06-..200V_C_140-G2_50kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 11 | 3 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_06-..230V_C_140G_G6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_06-..230V_C_140G-G3_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_06-..230V_C_140-G2_50kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 9.6 | 3 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_06-..480V_C_140G_G6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_06-..480V_C_140G-G3_35kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_06-..480V_C_140-G2_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 4.8 | 3 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_06-..600V_C_140G_H6_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_06-..600V_C_140G-H3_18kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_06-..600V_C_140G-H2_14kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_07-..480V_C_140G_G6_65kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_07-..480V_C_140G-G3_35kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_07-..480V_C_140-G2_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_07-..600V_C_140G_H6_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_07-..600V_C_140G-H3_18kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_07-..600V_C_140G-H2_14kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_08-..200V_C_140G_G6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 200 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_08-..200V_C_140G-G3_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 200 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_08-..200V_C_140-G2_50kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 17.5 | 5 | 1.14 | 1, 7b | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 14.3 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 200 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_08-..230V_C_140G_G6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_08-..230V_C_140G-G3_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_08-..230V_C_140-G2_50kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 15.2 | 5 | 1.14 | 1, 7b | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_08-..480V_C_140G_G6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_08-..480V_C_140G-G3_35kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_08-..480V_C_140-G2_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.14 | 1, 7b | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_08-..600V_C_140G_H6_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_08-..600V_C_140G-H3_18kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_08-..600V_C_140G-H2_14kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..230V_C_140G_G6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..230V_C_140G-G3_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..230V_C_140-G2_50kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 22 | 7.5 | 1.14 | 1, 7b | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..480V_C_140G_G6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..480V_C_140G-G3_35kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..480V_C_140-G2_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 11 | 7.5 | 1.14 | 1, 7b | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..600V_C_140G_H6_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..600V_C_140G-H3_18kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..600V_C_140G-H2_14kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_10-..480V_C_140G_G6_65kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_10-..480V_C_140G-G3_35kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_10-..480V_C_140-G2_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.14 | 1, 7b | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_10-..600V_C_140G_H6_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_10-..600V_C_140G-H3_18kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_10-..600V_C_140G-H2_14kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-C…-E1+EEFC_11-..200V_C_140G_G6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..200V_C_140G-G3_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..200V_C_140-G2_50kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*50 | 200 | 3 | 50 | 50 | --- | 200 | 3 | 50 | 32.2 | 10 | 1.14 | 1, 7c | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..230V_C_140G_G6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..230V_C_140G-G3_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..230V_C_140-G2_50kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*50 | 230 | 3 | 50 | 50 | --- | 230 | 3 | 50 | 28 | 10 | 1.14 | 1, 7c | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..480V_C_140G_G6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-C…-E1+EEFC_11-..480V_C_140G-G3_35kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-C…-E1+EEFC_11-..480V_C_140-G2_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.14 | 1, 7c | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 14
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-C…-E1+EEFC_11-..600V_C_140G_H6_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-C…-E1+EEFC_11-..600V_C_140G-H3_18kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-C…-E1+EEFC_11-..600V_C_140G-H2_14kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-C…-E1+EEFC_12-..480V_C_140G_G6_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_12-..480V_C_140G-G3_35kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_12-..480V_C_140-G2_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 1.14 | 1, 7c | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 14
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_12-..600V_C_140G_H6_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_12-..600V_C_140G-H3_18kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_12-..600V_C_140G-H2_14kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_13-..480V_C_140G_G6_65kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_13-..480V_C_140G-G3_35kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_13-..480V_C_140-G2_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 1.14 | 1, 7c | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 14
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_13-..600V_C_140G_H6_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_13-..600V_C_140G-H3_18kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_13-..600V_C_140G-H2_14kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_14-..480V_C_140G_G6_65kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEFC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_14-..480V_C_140G-G3_35kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEFC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_14-..480V_C_140-G2_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 14 | 1.14 | 1, 7c | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 14
|  | OLR | Allen Bradley | 592-EEFC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_14-..600V_C_140G_H6_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_14-..600V_C_140G-H3_18kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_14-..600V_C_140G-H2_14kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB500F-D…-E1+EEGD_15-..200V_C_140G_G6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..200V_C_140G-G3_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..200V_C_140-G2_50kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 48.3 | 15 | 3.47 | 1, 7d | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 14
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..230V_C_140G_G6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..230V_C_140G-G3_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..230V_C_140-G2_50kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 42 | 15 | 3.47 | 1, 7d | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..480V_C_140G_G6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_15-..480V_C_140G-G3_35kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_15-..480V_C_140-G2_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 3.47 | 1, 7d | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_15-..600V_C_140G_H6_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_15-..600V_C_140G-H3_18kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 17 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_15-..600V_C_140G-H2_14kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 17 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_16-..200V_C_140G_H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..200V_C_140G-H3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..200V_C_140G-H2_50kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..230V_C_140G_H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..230V_C_140G-H3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..230V_C_140G-H2_50kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..480V_C_140G_H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_16-..480V_C_140G-H3_35kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_16-..480V_C_140G-H2_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_16-..600V_C_140G_J6_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-J6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_16-..600V_C_140G-J3_18kA (AB500DAB016) | C | CB | Allen Bradley | 140G-J3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 22 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_16-..600V_C_140G-J2_14kA (AB500DAB016) | C | CB | Allen Bradley | 140G-J2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 22 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_17-..200V_C_140G_H6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..200V_C_140G-H3_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..200V_C_140G-H2_50kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..230V_C_140G_H6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..230V_C_140G-H3_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..230V_C_140G-H2_50kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..480V_C_140G_H6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_17-..480V_C_140G-H3_35kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_17-..480V_C_140G-H2_25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_17-..600V_C_140G_J6_25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-J6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_17-..600V_C_140G-J3_18kA (AB500DAB017) | C | CB | Allen Bradley | 140G-J3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 27 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_17-..600V_C_140G-J2_14kA (AB500DAB017) | C | CB | Allen Bradley | 140G-J2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 27 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_18-..230V_C_140G_H6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_18-..230V_C_140G-H3_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_18-..230V_C_140G-H2_50kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_18-..480V_C_140G_H6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_18-..480V_C_140G-H3_35kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_18-..480V_C_140G-H2_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_18-..600V_C_140G_J6_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_18-..600V_C_140G-J3_18kA (AB500DAB018) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 32 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_18-..600V_C_140G-J2_14kA (AB500DAB018) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 32 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_19-..480V_C_140G_H6_65kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_19-..480V_C_140G-H3_35kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_19-..480V_C_140G-H2_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_19-..600V_C_140G_J6_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 41 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_19-..600V_C_140G-J3_18kA (AB500DAB019) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 41 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_19-..600V_C_140G-J2_14kA (AB500DAB019) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 41 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_20-..480V_C_140G_H6_65kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_20-..480V_C_140G-H3_35kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_20-..480V_C_140G-H2_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_20-..600V_C_140G_J6_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEGD | 600 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_20-..600V_C_140G-J3_18kA (AB500DAB020) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 52 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEGD | 600 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_20-..600V_C_140G-J2_14kA (AB500DAB020) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 52 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEGD | 600 | 3 | 5 | 18-90 | ---
AB500F-E…-E1+EEHE_21-..200V_C_140G_J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..200V_C_140G-J3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..200V_C_140G-J2_50kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*150 | 200 | 3 | 50 | 150 | --- | 200 | 3 | 50 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..230V_C_140G_J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..230V_C_140G-J3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..230V_C_140G-J2_50kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*125 | 230 | 3 | 50 | 125 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..480V_C_140G_J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..480V_C_140G-J3_35kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..480V_C_140G-J2_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..600V_C_140G_J6_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..600V_C_140G-J3_18kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 32 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..600V_C_140G-J2_14kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 32 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..230V_C_140G_J6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..230V_C_140G-J3_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..230V_C_140G-J2_50kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*175 | 230 | 3 | 50 | 175 | --- | 230 | 3 | 50 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..480V_C_140G_J6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..480V_C_140G-J3_35kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..480V_C_140G-J2_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..600V_C_140G_J6_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..600V_C_140G-J3_18kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 52 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..600V_C_140G-J2_14kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 52 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..480V_C_140G_J6_65kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..480V_C_140G-J3_35kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..480V_C_140G-J2_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..600V_C_140G_J6_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 62 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..600V_C_140G-J3_18kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 62 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..600V_C_140G-J2_14kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 62 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..480V_C_140G_J6_65kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..480V_C_140G-J3_35kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..480V_C_140G-J2_25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..600V_C_140G_J6_25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..600V_C_140G-J3_18kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 77 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..600V_C_140G-J2_14kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 77 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_25-..600V_C_140G_J6_25kA (AB500DAB025) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 99 | 100 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_25-..600V_C_140G-J3_18kA (AB500DAB025) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 99 | 100 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_25-..600V_C_140G-J2_14kA (AB500DAB025) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 99 | 100 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-F…-E1+EEKF_26-..200V_C_140G_G6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K6*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EEKF | 200 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..200V_C_140G-K3_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K3*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EEKF | 200 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..200V_C_140G-K2_50kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K2*400 | 200 | 3 | 50 | 400 | --- | 200 | 3 | 50 | 221 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EEKF | 200 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..230V_C_140G_G6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EEKF | 230 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..230V_C_140G-K3_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K3*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EEKF | 230 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..230V_C_140G-K2_50kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K2*400 | 230 | 3 | 50 | 400 | --- | 230 | 3 | 50 | 192 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EEKF | 230 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..480V_C_140G_G6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..480V_C_140G-K3_35kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K3*300 | 480 | 3 | 35 | 300 | --- | 480 | 3 | 35 | 96 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..480V_C_140G-K2_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K2*300 | 480 | 3 | 25 | 300 | --- | 480 | 3 | 25 | 96 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..600V_C_140G_J6_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..600V_C_140G-J3_18kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..600V_C_140G-J2_14kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..230V_C_140G_G6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EEKF | 230 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..230V_C_140G-K3_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K3*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EEKF | 230 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..230V_C_140G-K2_50kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K2*400 | 230 | 3 | 50 | 400 | --- | 230 | 3 | 50 | 248 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EEKF | 230 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..480V_C_140G_G6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..480V_C_140G-K3_35kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K3*300 | 480 | 3 | 35 | 300 | --- | 480 | 3 | 35 | 124 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..480V_C_140G-K2_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K2*300 | 480 | 3 | 25 | 300 | --- | 480 | 3 | 25 | 124 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..600V_C_140G_J6_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..600V_C_140G-J3_18kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..600V_C_140G-J2_14kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_28-..600V_C_140G_J6_25kA (AB500DAB028) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_28-..600V_C_140G-J3_18kA (AB500DAB028) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_28-..600V_C_140G-J2_14kA (AB500DAB028) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-A…-E1+EEEC_01-..200V_C_140G_H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_01-..200V_C_140G-H3_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_01-..200V_C_140G-H2_50kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_01-..230V_C_140G_H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_01-..230V_C_140G-H3_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_01-..230V_C_140G-H2_50kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_01-..480V_C_140G_H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_01-..480V_C_140G-H3_35kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_01-..480V_C_140G-H2_25kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_02-..200V_C_140G_H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_02-..200V_C_140G-H3_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_02-..200V_C_140G-H2_50kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_02-..230V_C_140G_H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_02-..230V_C_140G-H3_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_02-..230V_C_140G-H2_50kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_02-..480V_C_140G_H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_02-..480V_C_140G-H3_35kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_02-..480V_C_140G-H2_25kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_03-..200V_C_140G_H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_03-..200V_C_140G-H3_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_03-..200V_C_140G-H2_50kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_03-..230V_C_140G_H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_03-..230V_C_140G-H3_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_03-..230V_C_140G-H2_50kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_03-..480V_C_140G_H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_03-..480V_C_140G-H3_35kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_03-..480V_C_140G-H2_25kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..200V_C_140G_H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..200V_C_140G-H3_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..200V_C_140G-H2_50kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..230V_C_140G_H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..230V_C_140G-H3_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..230V_C_140G-H2_50kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..480V_C_140G_H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..480V_C_140G-H3_35kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..480V_C_140G-H2_25kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_05-..200V_C_140G_H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_05-..200V_C_140G-H3_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_05-..200V_C_140G-H2_50kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_05-..230V_C_140G_H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_05-..230V_C_140G-H3_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_05-..230V_C_140G-H2_50kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_05-..480V_C_140G_H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_05-..480V_C_140G-H3_35kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_05-..480V_C_140G-H2_25kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_06-..200V_C_140G_H6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_06-..200V_C_140G-H3_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_06-..200V_C_140G-H2_50kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_06-..230V_C_140G_H6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_06-..230V_C_140G-H3_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_06-..230V_C_140G-H2_50kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_06-..480V_C_140G_H6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_06-..480V_C_140G-H3_35kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_06-..480V_C_140G-H2_25kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_07-..480V_C_140G_H6_65kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_07-..480V_C_140G-H3_35kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_07-..480V_C_140G-H2_25kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_08-..200V_C_140G_H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 200 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_08-..200V_C_140G-H3_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 200 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_08-..200V_C_140G-H2_50kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 200 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_08-..230V_C_140G_H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_08-..230V_C_140G-H3_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_08-..230V_C_140G-H2_50kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_08-..480V_C_140G_H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_08-..480V_C_140G-H3_35kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_08-..480V_C_140G-H2_25kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..230V_C_140G_H6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..230V_C_140G-H3_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..230V_C_140G-H2_50kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..480V_C_140G_H6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..480V_C_140G-H3_35kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..480V_C_140G-H2_25kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_10-..480V_C_140G_H6_65kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_10-..480V_C_140G-H3_35kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_10-..480V_C_140G-H2_25kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_11-..200V_C_140G_H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..200V_C_140G-H3_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..200V_C_140G-H2_50kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*50 | 200 | 3 | 50 | 50 | --- | 200 | 3 | 50 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..230V_C_140G_H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..230V_C_140G-H3_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..230V_C_140G-H2_50kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*50 | 230 | 3 | 50 | 50 | --- | 230 | 3 | 50 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..480V_C_140G_H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_11-..480V_C_140G-H3_35kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_11-..480V_C_140G-H2_25kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_12-..480V_C_140G_H6_65kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_12-..480V_C_140G-H3_35kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_12-..480V_C_140G-H2_25kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_13-..480V_C_140G_H6_65kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_13-..480V_C_140G-H3_35kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_13-..480V_C_140G-H2_25kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_14-..480V_C_140G_H6_65kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEFC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_14-..480V_C_140G-H3_35kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEFC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_14-..480V_C_140G-H2_25kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEFC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_15-..200V_C_140G_H6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..200V_C_140G-H3_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..200V_C_140G-H2_50kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..200V_C_140G-I3_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..200V_C_140G-I2_50kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-I2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..230V_C_140G_H6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..230V_C_140G-H3_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..230V_C_140G-H2_50kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..230V_C_140G-I3_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..230V_C_140G-I2_50kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..480V_C_140G_H6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_15-..480V_C_140G-H3_35kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_15-..480V_C_140G-H2_25kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_16-..200V_C_140G_H6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..200V_C_140G-H3_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..200V_C_140G-H2_50kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..200V_C_140G-I3_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..200V_C_140G-I2_50kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-I2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..230V_C_140G_H6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..230V_C_140G-H3_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..230V_C_140G-H2_50kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..230V_C_140G-I3_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..230V_C_140G-I2_50kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..480V_C_140G_H6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_16-..480V_C_140G-H3_35kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_16-..480V_C_140G-H2_25kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_17-..200V_C_140G_H6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..200V_C_140G-H3_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..200V_C_140G-H2_50kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..200V_C_140G-I3_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..200V_C_140G-I2_50kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-I2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..230V_C_140G_H6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..230V_C_140G-H3_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..230V_C_140G-H2_50kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..230V_C_140G-I3_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..230V_C_140G-I2_50kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..480V_C_140G_H6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_17-..480V_C_140G-H3_35kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_17-..480V_C_140G-H2_25kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_18-..230V_C_140G_H6_65kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_18-..230V_C_140G-H3_65kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_18-..230V_C_140G-H2_50kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_18-..230V_C_140G-I3_65kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_18-..230V_C_140G-I2_50kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_18-..480V_C_140G_H6_65kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_18-..480V_C_140G-H3_35kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_18-..480V_C_140G-H2_25kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_19-..480V_C_140G_H6_65kA_2 (AB500DAB019) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_19-..480V_C_140G-H3_35kA_2 (AB500DAB019) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_19-..480V_C_140G-H2_25kA_2 (AB500DAB019) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_20-..480V_C_140G_H6_65kA_2 (AB500DAB020) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_20-..480V_C_140G-H3_35kA_2 (AB500DAB020) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_20-..480V_C_140G-H2_25kA_2 (AB500DAB020) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-E…-E1+EEHE_21-..200V_C_140G_J6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..200V_C_140G-J3_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..200V_C_140G-J2_50kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*150 | 200 | 3 | 50 | 150 | --- | 200 | 3 | 50 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..200V_C_140G-I3_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..200V_C_140G-I2_50kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*150 | 200 | 3 | 50 | 150 | --- | 200 | 3 | 50 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..230V_C_140G_J6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..230V_C_140G-J3_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..230V_C_140G-J2_50kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*125 | 230 | 3 | 50 | 125 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..230V_C_140G-I3_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..230V_C_140G-I2_50kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*125 | 230 | 3 | 50 | 125 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..480V_C_140G_J6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..480V_C_140G-J3_35kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..480V_C_140G-J2_25kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..480V_C_140G-I3_35kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..480V_C_140G-I2_25kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..230V_C_140G_J6_65kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..230V_C_140G-J3_65kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..230V_C_140G-J2_50kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*175 | 230 | 3 | 50 | 175 | --- | 230 | 3 | 50 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..480V_C_140G_J6_65kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..480V_C_140G-J3_35kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..480V_C_140G-J2_25kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..480V_C_140G-I3_35kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-I3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..480V_C_140G-I2_25kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-I2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..480V_C_140G_J6_65kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..480V_C_140G-J3_35kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..480V_C_140G-J2_25kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..480V_C_140G-I3_35kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-I3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..480V_C_140G-I2_25kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-I2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..480V_C_140G_J6_65kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..480V_C_140G-J3_35kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..480V_C_140G-J2_25kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..480V_C_140G-I3_35kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-I3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..480V_C_140G-I2_25kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-I2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-F…-E1+EEKF_26-..600V_C_140G_J6_25kA_2 (AB500DAB026) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..600V_C_140G-J3_18kA_2 (AB500DAB026) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..600V_C_140G-J2_14kA_2 (AB500DAB026) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..600V_C_140G_J6_25kA_2 (AB500DAB027) | C | CB | Allen Bradley | 140G-J6*200 | 600 | 3 | 25 | 200 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..600V_C_140G-J3_18kA_2 (AB500DAB027) | C | CB | Allen Bradley | 140G-J3*200 | 600 | 3 | 18 | 200 | --- | 600 | 3 | 18 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..600V_C_140G-J2_14kA_2 (AB500DAB027) | C | CB | Allen Bradley | 140G-J2*200 | 600 | 3 | 14 | 200 | --- | 600 | 3 | 14 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_28-..600V_C_140G_J6_25kA_2 (AB500DAB028) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_28-..600V_C_140G-J3_18kA_2 (AB500DAB028) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_28-..600V_C_140G-J2_14kA_2 (AB500DAB028) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-D…-E1+EEGD_30-..230V_C_140G_J6_65kA_2 (AB500DAB030) | C | CB | Allen Bradley | 140G-J6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_30-..230V_C_140G-J3_65kA_2 (AB500DAB030) | C | CB | Allen Bradley | 140G-J3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_30-..230V_C_140G-J2_50kA_2 (AB500DAB030) | C | CB | Allen Bradley | 140G-J2*125 | 230 | 3 | 50 | 125 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-E…-E1+EEHE_31-..230V_C_140G_J6_65kA_2 (AB500DAB031) | C | CB | Allen Bradley | 140G-J6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_31-..230V_C_140G-J3_65kA_2 (AB500DAB031) | C | CB | Allen Bradley | 140G-J3*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_31-..230V_C_140G-J2_50kA_2 (AB500DAB031) | C | CB | Allen Bradley | 140G-J2*175 | 230 | 3 | 50 | 175 | --- | 230 | 3 | 50 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-A…-E1+EEEC_01-..600V_C_140G_6_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEBC | 600 | 3 | 5 | 0.2-1 | ---
AB500F-A…-E1+EEEC_02-..600V_C_140G_6_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_03-..600V_C_140G_6_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..600V_C_140G_6_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_05-..600V_C_140G_6_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_06-..600V_C_140G_6_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_07-..600V_C_140G_6_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_08-..600V_C_140G_6_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..600V_C_140G_6_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_10-..600V_C_140G_6_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-C…-E1+EEFC_11-..600V_C_140G_6_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-C…-E1+EEFC_12-..480V_C_140G_G6_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_12-..600V_C_140G_6_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_13-..600V_C_140G_6_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_14-..600V_C_140G_6_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB500F-D…-E1+EEGD_15-..600V_C_140G_6_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_16-..200V_C_140G_6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..230V_C_140G_6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..480V_C_140G_6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_16-..600V_C_140G_6_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-JC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_17-..200V_C_140G_6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..230V_C_140G_6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..480V_C_140G_6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_17-..600V_C_140G_6_25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-JC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_18-..230V_C_140G_6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_18-..480V_C_140G_6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_18-..600V_C_140G_6_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_19-..480V_C_140G_6_65kA (AB500DAB019) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_19-..600V_C_140G_6_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 41 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_20-..480V_C_140G_6_65kA (AB500DAB020) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_20-..600V_C_140G_6_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEGD | 600 | 3 | 5 | 18-90 | ---
AB500F-E…-E1+EEHE_21-..200V_C_140G_6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..230V_C_140G_6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..480V_C_140G_6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..600V_C_140G_6_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..230V_C_140G_6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..480V_C_140G_6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..600V_C_140G_6_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..480V_C_140G_6_65kA (AB500DAB023) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..600V_C_140G_6_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 62 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..480V_C_140G_6_65kA (AB500DAB024) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..600V_C_140G_6_25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_25-..600V_C_140G_6_25kA (AB500DAB025) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 99 | 100 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-F…-E1+EEKF_26-..200V_C_140G_G6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-KC6*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EEKF | 200 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..230V_C_140G_G6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-KC6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EEKF | 230 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..480V_C_140G_G6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-KC6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..600V_C_140G_6_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..230V_C_140G_G6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-KC6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EEKF | 230 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..480V_C_140G_G6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-KC6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..600V_C_140G_6_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_28-..600V_C_140G_6_25kA (AB500DAB028) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-A…-E1+EEEC_01-..200V_C_140G_6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_01-..230V_C_140G_6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_01-..480V_C_140G_6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_02-..200V_C_140G_6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_02-..230V_C_140G_6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_02-..480V_C_140G_6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_03-..200V_C_140G_6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_03-..230V_C_140G_6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_03-..480V_C_140G_6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..200V_C_140G_6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..230V_C_140G_6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..480V_C_140G_6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_05-..200V_C_140G_6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_05-..230V_C_140G_6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_05-..480V_C_140G_6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_06-..200V_C_140G_6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_06-..230V_C_140G_6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_06-..480V_C_140G_6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_07-..480V_C_140G_6_65kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_08-..200V_C_140G_6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 200 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_08-..230V_C_140G_6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_08-..480V_C_140G_6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..230V_C_140G_6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..480V_C_140G_6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_10-..480V_C_140G_6_65kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_11-..200V_C_140G_6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..230V_C_140G_6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..480V_C_140G_6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_12-..480V_C_140G_6_65kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_13-..480V_C_140G_6_65kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_14-..480V_C_140G_6_65kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEFC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_15-..200V_C_140G_6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..230V_C_140G_6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..480V_C_140G_6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_16-..200V_C_140G_6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..230V_C_140G_6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..480V_C_140G_6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_17-..200V_C_140G_6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..230V_C_140G_6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..480V_C_140G_6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_18-..230V_C_140G_6_65kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_18-..480V_C_140G_6_65kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_19-..480V_C_140G_6_65kA_2 (AB500DAB019) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_20-..480V_C_140G_6_65kA_2 (AB500DAB020) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-E…-E1+EEHE_21-..200V_C_140G_6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..230V_C_140G_6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..480V_C_140G_6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..230V_C_140G_6_65kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..480V_C_140G_6_65kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..480V_C_140G_6_65kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..480V_C_140G_6_65kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-F…-E1+EEKF_26-..600V_C_140G_6_25kA_2 (AB500DAB026) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..600V_C_140G_6_25kA_2 (AB500DAB027) | C | CB | Allen Bradley | 140G-JC6*200 | 600 | 3 | 25 | 200 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_28-..600V_C_140G_6_25kA_2 (AB500DAB028) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-D…-E1+EEGD_30-..230V_C_140G_6_65kA_2 (AB500DAB030) | C | CB | Allen Bradley | 140G-JC6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-E…-E1+EEHE_31-..230V_C_140G_6_65kA_2 (AB500DAB031) | C | CB | Allen Bradley | 140G-JC6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(7) = See Table 7 for minimum internal power wiring.
Table 7 - Minimum Internal Power Wiring
1/32in. thick thermoplastic insulation, rated 105C
Wire Code |  | Wire Size
7a |  | 10 AWG
7b |  | 10 AWG
7c |  | 8 AWG
7d |  | 4 AWG
7e |  | 1AWG
7f |  | 250 MCM

## 500F C E3
[16 empty] | Issued: | 2015-12-31
[16 empty] | Last Revised: | 2017-10-10
ID Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage | Number of Phases | SCCR, kA | Full Load Current, A | HP rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP Rating | Enclosure Volume, CU Ft
AB500F-A…-E3EC*D_01-..200V_C_140G-G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..200V_C_140G-G3_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..200V_C_140G-G2_50kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..230V_C_140G-G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..230V_C_140G-G3_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..230V_C_140G-G2_50kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..480V_C_140G-G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..480V_C_140G-G3_35kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..480V_C_140G-G2_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..600V_C_140G-H6_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*PC | 600 | 3 | 5 | 0.4-2 | ---
AB500F-A…-E3EC*D_01-..600V_C_140G-H3_18kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*PC | 600 | 3 | 5 | 0.4-2 | ---
AB500F-A…-E3EC*D_01-..600V_C_140G-H2_14kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*PC | 600 | 3 | 5 | 0.4-2 | ---
AB500F-A…-E3EC*D_02-..200V_C_140G-G6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..200V_C_140G-G3_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..200V_C_140G-G2_50kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..230V_C_140G-G6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..230V_C_140G-G3_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..230V_C_140G-G2_50kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..480V_C_140G-G6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..480V_C_140G-G3_35kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..480V_C_140G-G2_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 35 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..600V_C_140G-H6_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..600V_C_140G-H3_18kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..600V_C_140G-H2_14kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..200V_C_140G-G6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..200V_C_140G-G3_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..200V_C_140G-G2_50kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..230V_C_140G-G6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | 3 | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..230V_C_140G-G3_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | 3 | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..230V_C_140G-G2_50kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | 3 | 230 | 3 | 50 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..480V_C_140G-G6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..480V_C_140G-G3_35kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..480V_C_140G-G2_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..600V_C_140G-H6_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..600V_C_140G-H3_18kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..600V_C_140G-H2_14kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_04-04/2HP-..200V_C_140G-G6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_04-04/2HP-..200V_C_140G-G3_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_04-04/2HP-..200V_C_140G-G2_50kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_04-04/2HP-..230V_C_140G-G6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_04-04/2HP-..230V_C_140G-G3_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_04-04/2HP-..230V_C_140G-G2_50kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_04-04/2HP-..480V_C_140G-G6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_04-04/2HP-..480V_C_140G-G3_35kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_04-04/2HP-..480V_C_140G-G2_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_04-04/2HP-..600V_C_140G-H6_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_04-04/2HP-..600V_C_140G-H3_18kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_04-04/2HP-..600V_C_140G-H2_14kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_05-..200V_C_140G-G6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_05-..200V_C_140G-G3_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_05-..200V_C_140G-G2_50kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_05-..230V_C_140G-G6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_05-..230V_C_140G-G3_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_05-..230V_C_140G-G2_50kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_05-..480V_C_140G-G6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_05-..480V_C_140G-G3_35kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_05-..480V_C_140G-G2_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_05-..600V_C_140G-H6_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_05-..600V_C_140G-H3_18kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_05-..600V_C_140G-H2_14kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_06-..200V_C_140G-G6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_06-..200V_C_140G-G3_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_06-..200V_C_140G-G2_50kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_06-..480V_C_140G-G6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_06-..480V_C_140G-G3_35kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_06-..480V_C_140G-G2_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_06-..600V_C_140G-H6_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_06-..600V_C_140G-H3_18kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_06-..600V_C_140G-H2_14kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_07-..480V_C_140G-G6_65kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_07-..480V_C_140G-G3_35kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_07-..480V_C_140G-G2_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_07-..600V_C_140G-H6_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_07-..600V_C_140G-H3_18kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_07-..600V_C_140G-H2_14kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_08-..200V_C_140G-G6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 200 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_08-..200V_C_140G-G3_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 200 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_08-..200V_C_140G-G2_50kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 200 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_08-..230V_C_140G-G6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_08-..230V_C_140G-G3_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_08-..230V_C_140G-G2_50kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_08-..480V_C_140G-G6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_08-..480V_C_140G-G3_35kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_08-..480V_C_140G-G2_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_08-..600V_C_140G-H6_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_08-..600V_C_140G-H3_18kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_08-..600V_C_140G-H2_14kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_09-1/2HP-..200V_C_140G-G6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-B…-E3EC*D_09-1/2HP-..200V_C_140G-G3_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-B…-E3EC*D_09-1/2HP-..200V_C_140G-G2_50kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-B…-E3EC*D_09-1/2HP-..480V_C_140G-G6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_09-1/2HP-..480V_C_140G-G3_35kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_09-1/2HP-..480V_C_140G-G2_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_09-1/2HP-..600V_C_140G-H6_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_09-1/2HP-..600V_C_140G-H3_18kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_09-1/2HP-..600V_C_140G-H2_14kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_10-..480V_C_140G-G6_65kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*D | 480 | 3 | 5 | 9.0-45 | ---
AB500F-B…-E3EC*D_10-..480V_C_140G-G3_35kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*D | 480 | 3 | 5 | 9.0-45 | ---
AB500F-B…-E3EC*D_10-..480V_C_140G-G2_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*D | 480 | 3 | 5 | 9.0-45 | ---
AB500F-B…-E3EC*D_10-..600V_C_140G-H6_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_10-..600V_C_140G-H3_18kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_10-..600V_C_140G-H2_14kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-C…-E3EC*D_11-..200V_C_140G-G6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..200V_C_140G-G3_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..200V_C_140G-G2_50kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*50 | 200 | 3 | 50 | 50 | --- | 200 | 3 | 50 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..230V_C_140G-G6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..230V_C_140G-G3_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..230V_C_140G-G2_50kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*50 | 230 | 3 | 50 | 50 | --- | 230 | 3 | 50 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..480V_C_140G-G6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-C…-E3EC*D_11-..480V_C_140G-G3_35kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-C…-E3EC*D_11-..480V_C_140G-G2_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-C…-E3EC*D_11-..600V_C_140G-H6_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-C…-E3EC*D_11-..600V_C_140G-H3_18kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-C…-E3EC*D_11-..600V_C_140G-H2_14kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-C…-E3EC*D_12-..480V_C_140G-G6_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 480 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_12-..480V_C_140G-G3_35kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 480 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_12-..480V_C_140G-G2_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 480 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_12-..600V_C_140G-H6_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_12-..600V_C_140G-H3_18kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_12-..600V_C_140G-H2_14kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_13-..480V_C_140G-G6_65kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_13-..480V_C_140G-G3_35kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_13-..480V_C_140G-G2_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_13-..600V_C_140G-H6_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_13-..600V_C_140G-H3_18kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_13-..600V_C_140G-H2_14kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_14-..480V_C_140G-G6_65kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_14-..480V_C_140G-G3_35kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_14-..480V_C_140G-G2_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_14-..600V_C_140G-H6_25kA_140G-H6_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 600 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_14-..600V_C_140G-H3_18kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 600 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_14-..600V_C_140G-H2_14kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_15-..200V_C_140G-G6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..200V_C_140G-G3_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..200V_C_140G-G2_50kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..230V_C_140G-G6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..230V_C_140G-G3_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..230V_C_140G-G2_50kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..480V_C_140G-G6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_15-..480V_C_140G-G3_35kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_15-..480V_C_140G-G2_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_15-..600V_C_140G-H6_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_15-..600V_C_140G-H3_18kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 17 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_15-..600V_C_140G-H2_14kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 17 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_16-..200V_C_140G-H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..200V_C_140G-H3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..200V_C_140G-H2_50kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..230V_C_140G-H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..230V_C_140G-H3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..230V_C_140G-H2_50kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..480V_C_140G-H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_16-..480V_C_140G-H3_35kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_16-..480V_C_140G-H2_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_16-..600V_C_140G-J6_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-J6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_16-..600V_C_140G-J3_18kA (AB500DAB016) | C | CB | Allen Bradley | 140G-J3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 22 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_16-..600V_C_140G-J2_14kA (AB500DAB016) | C | CB | Allen Bradley | 140G-J2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 22 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_17-..200V_C_140G-H6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..200V_C_140G-H3_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..200V_C_140G-H2_50kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..230V_C_140G-H6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..230V_C_140G-H3_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..230V_C_140G-H2_50kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..480V_C_140G-H6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_17-..480V_C_140G-H3_35kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_17-..480V_C_140G-H2_25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_17-..600V_C_140G-J6_25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-J6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_17-..600V_C_140G-J3_18kA (AB500DAB017) | C | CB | Allen Bradley | 140G-J3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 27 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_17-..600V_C_140G-J2_14kA (AB500DAB017) | C | CB | Allen Bradley | 140G-J2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 27 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_18-..480V_C_140G-H6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_18-..480V_C_140G-H3_35kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_18-..480V_C_140G-H2_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_18-..600V_C_140G-J6_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_18-..600V_C_140G-J3_18kA (AB500DAB018) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 32 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_18-..600V_C_140G-J2_14kA (AB500DAB018) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 32 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_19-..480V_C_140G-H6_65kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_19-..480V_C_140G-H3_35kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_19-..480V_C_140G-H2_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_19-..600V_C_140G-J6_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 41 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_19-..600V_C_140G-J3_18kA (AB500DAB019) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 41 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_19-..600V_C_140G-J2_14kA (AB500DAB019) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 41 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_20-..480V_C_140G-H6_65kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_20-..480V_C_140G-H3_35kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_20-..480V_C_140G-H2_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_20-..600V_C_140G-J6_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 600 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_20-..600V_C_140G-J3_18kA (AB500DAB020) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 52 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 600 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_20-..600V_C_140G-J2_14kA (AB500DAB020) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 52 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 600 | 3 | 5 | 18-90 | ---
AB500F-E…-E3EC*F_21-..200V_C_140G-J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..200V_C_140G-J3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..200V_C_140G-J2_50kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*150 | 200 | 3 | 50 | 150 | --- | 200 | 3 | 50 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..230V_C_140G-J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..230V_C_140G-J3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..230V_C_140G-J2_50kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*125 | 230 | 3 | 50 | 125 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..480V_C_140G-J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..480V_C_140G-J3_35kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..480V_C_140G-J2_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..600V_C_140G-J6_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..600V_C_140G-J3_18kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 32 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..600V_C_140G-J2_14kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 32 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..480V_C_140G-J6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..480V_C_140G-J3_35kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..480V_C_140G-J2_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..600V_C_140G-J6_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..600V_C_140G-J3_18kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 52 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..600V_C_140G-J2_14kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 52 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..480V_C_140G-J6_65kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..480V_C_140G-J3_35kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..480V_C_140G-J2_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..600V_C_140G-J6_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 62 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..600V_C_140G-J3_18kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 62 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..600V_C_140G-J2_14kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 62 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..480V_C_140G-J6_65kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..480V_C_140G-J3_35kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..480V_C_140G-J2_25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..600V_C_140G-J6_25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..600V_C_140G-J3_18kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 77 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..600V_C_140G-J2_14kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 77 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_25-..600V_C_140G-J6_25kA (AB500DAB025) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 99 | 100 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_25-..600V_C_140G-J3_18kA (AB500DAB025) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 99 | 100 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_25-..600V_C_140G-J2_14kA (AB500DAB025) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 99 | 100 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-F…-E3EC*H_26-..200V_C_140G-K6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K6*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EC*HF | 200 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..200V_C_140G-K3_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K3*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EC*HF | 200 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..200V_C_140G-K2_50kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K2*400 | 200 | 3 | 50 | 400 | --- | 200 | 3 | 50 | 221 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EC*HF | 200 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..230V_C_140G-K6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EC*HF | 230 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..230V_C_140G-K3_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K3*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EC*HF | 230 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..230V_C_140G-K2_50kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K2*400 | 230 | 3 | 50 | 400 | --- | 230 | 3 | 50 | 192 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EC*HF | 230 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..480V_C_140G-K6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..480V_C_140G-K3_35kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K3*300 | 480 | 3 | 35 | 300 | --- | 480 | 3 | 35 | 96 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..480V_C_140G-K2_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K2*300 | 480 | 3 | 25 | 300 | --- | 480 | 3 | 25 | 96 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..600V_C_140G-J6_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..600V_C_140G-J3_18kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..600V_C_140G-J2_14kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..230V_C_140G-K6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EC*HF | 230 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..230V_C_140G-K3_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K3*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EC*HF | 230 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..230V_C_140G-K2_50kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K2*400 | 230 | 3 | 50 | 400 | --- | 230 | 3 | 50 | 248 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EC*HF | 230 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..480V_C_140G-K6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..480V_C_140G-K3_35kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K3*300 | 480 | 3 | 35 | 300 | --- | 480 | 3 | 35 | 124 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..480V_C_140G-K2_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K2*300 | 480 | 3 | 25 | 300 | --- | 480 | 3 | 25 | 124 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..600V_C_140G-J6_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J6*200 | 600 | 3 | 25 | 200 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..600V_C_140G-J3_18kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J3*200 | 600 | 3 | 18 | 200 | --- | 600 | 3 | 18 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..600V_C_140G-J2_14kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J2*200 | 600 | 3 | 14 | 200 | --- | 600 | 3 | 14 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_28-..600V_C_140G-J6_25kA (AB500DAB028) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_28-..600V_C_140G-J3_18kA (AB500DAB028) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_28-..600V_C_140G-J2_14kA (AB500DAB028) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-A…-E3EC*D_01-..200V_C_140G-H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..200V_C_140G-H3_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..200V_C_140G-H2_50kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..230V_C_140G-H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..230V_C_140G-H3_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..230V_C_140G-H2_50kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..480V_C_140G-H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..480V_C_140G-H3_35kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..480V_C_140G-H2_25kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..200V_C_140G-H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..200V_C_140G-H3_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..200V_C_140G-H2_50kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..230V_C_140G-H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..230V_C_140G-H3_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..230V_C_140G-H2_50kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..480V_C_140G-H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..480V_C_140G-H3_35kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..480V_C_140G-H2_25kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..200V_C_140G-H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..200V_C_140G-H3_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..200V_C_140G-H2_50kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..230V_C_140G-H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..230V_C_140G-H3_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..230V_C_140G-H2_50kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..480V_C_140G-H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..480V_C_140G-H3_35kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..480V_C_140G-H2_25kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_04-04/2HP-..200V_C_140G-H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_04-04/2HP-..200V_C_140G-H3_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_04-04/2HP-..200V_C_140G-H2_50kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_04-04/2HP-..230V_C_140G-H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_04-04/2HP-..230V_C_140G-H3_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_04-04/2HP-..230V_C_140G-H2_50kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_04-04/2HP-..480V_C_140G-H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_04-04/2HP-..480V_C_140G-H3_35kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_04-04/2HP-..480V_C_140G-H2_25kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_05-..200V_C_140G-H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_05-..200V_C_140G-H3_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_05-..200V_C_140G-H2_50kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_05-..230V_C_140G-H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_05-..230V_C_140G-H3_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_05-..230V_C_140G-H2_50kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_05-..480V_C_140G-H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_05-..480V_C_140G-H3_35kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_05-..480V_C_140G-H2_25kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_06-..200V_C_140G-H6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_06-..200V_C_140G-H3_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_06-..200V_C_140G-H2_50kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_06-..480V_C_140G-H6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_06-..480V_C_140G-H3_35kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_06-..480V_C_140G-H2_25kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_07-..480V_C_140G-H6_65kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_07-..480V_C_140G-H3_35kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_07-..480V_C_140G-H2_25kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_08-..200V_C_140G-H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 200 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_08-..200V_C_140G-H3_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 200 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_08-..200V_C_140G-H2_50kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 200 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_08-..230V_C_140G-H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_08-..230V_C_140G-H3_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_08-..230V_C_140G-H2_50kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_08-..480V_C_140G-H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_08-..480V_C_140G-H3_35kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_08-..480V_C_140G-H2_25kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_09-1/2HP-..200V_C_140G-H6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-B…-E3EC*D_09-1/2HP-..200V_C_140G-H3_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-B…-E3EC*D_09-1/2HP-..200V_C_140G-H2_50kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-B…-E3EC*D_09-1/2HP-..480V_C_140G-H6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_09-1/2HP-..480V_C_140G-H3_35kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_09-1/2HP-..480V_C_140G-H2_25kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_10-..480V_C_140G-H6_65kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-B…-E3EC*D_10-..480V_C_140G-H3_35kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-B…-E3EC*D_10-..480V_C_140G-H2_25kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..200V_C_140G-H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..200V_C_140G-H3_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..200V_C_140G-H2_50kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*50 | 200 | 3 | 50 | 50 | --- | 200 | 3 | 50 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..230V_C_140G-H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..230V_C_140G-H3_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..230V_C_140G-H2_50kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*50 | 230 | 3 | 50 | 50 | --- | 230 | 3 | 50 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..480V_C_140G-H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-C…-E3EC*D_11-..480V_C_140G-H3_35kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-C…-E3EC*D_11-..480V_C_140G-H2_25kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-C…-E3EC*D_12-..480V_C_140G-H6_65kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 480 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_12-..480V_C_140G-H3_35kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 480 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_12-..480V_C_140G-H2_25kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 480 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_13-..480V_C_140G-H6_65kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 65 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_13-..480V_C_140G-H3_35kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 65 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_13-..480V_C_140G-H2_25kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 65 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_14-..480V_C_140G-H6_65kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_14-..480V_C_140G-H3_35kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_14-..480V_C_140G-H2_25kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_15-..200V_C_140G-H6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..200V_C_140G-H3_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..200V_C_140G-H2_50kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..200V_C_140G-I3_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..200V_C_140G-I2_50kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-I2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..230V_C_140G-H6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..230V_C_140G-H3_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..230V_C_140G-H2_50kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..230V_C_140G-I3_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..230V_C_140G-I2_50kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..480V_C_140G-H6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_15-..480V_C_140G-H3_35kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_15-..480V_C_140G-H2_25kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_16-..200V_C_140G-H6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..200V_C_140G-H3_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..200V_C_140G-H2_50kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..200V_C_140G-I3_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..200V_C_140G-I2_50kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-I2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..230V_C_140G-H6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..230V_C_140G-H3_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..230V_C_140G-H2_50kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..230V_C_140G-I3_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..230V_C_140G-I2_50kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..480V_C_140G-H6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_16-..480V_C_140G-H3_35kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_16-..480V_C_140G-H2_25kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_17-..200V_C_140G-H6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..200V_C_140G-H3_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..200V_C_140G-H2_50kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..200V_C_140G-I3_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..200V_C_140G-I2_50kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-I2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..230V_C_140G-H6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..230V_C_140G-H3_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..230V_C_140G-H2_50kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..230V_C_140G-I3_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..230V_C_140G-I2_50kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..480V_C_140G-H6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_17-..480V_C_140G-H3_35kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_17-..480V_C_140G-H2_25kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_18-..480V_C_140G-H6_65kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_18-..480V_C_140G-H3_35kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_18-..480V_C_140G-H2_25kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_19-..480V_C_140G-H6_65kA_2 (AB500DAB019) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_19-..480V_C_140G-H3_35kA_2 (AB500DAB019) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_19-..480V_C_140G-H2_25kA_2 (AB500DAB019) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_20-..480V_C_140G-H6_65kA_2 (AB500DAB020) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_20-..480V_C_140G-H3_35kA_2 (AB500DAB020) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_20-..480V_C_140G-H2_25kA_2 (AB500DAB020) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-E…-E3EC*F_21-..200V_C_140G-J6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..200V_C_140G-J3_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..200V_C_140G-J2_50kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*150 | 200 | 3 | 50 | 150 | --- | 200 | 3 | 50 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..200V_C_140G-I3_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..200V_C_140G-I2_50kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*150 | 200 | 3 | 50 | 150 | --- | 200 | 3 | 50 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..230V_C_140G-J6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..230V_C_140G-J3_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..230V_C_140G-J2_50kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*125 | 230 | 3 | 50 | 125 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..230V_C_140G-I3_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..230V_C_140G-I2_50kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*125 | 230 | 3 | 50 | 125 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..480V_C_140G-J6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..480V_C_140G-J3_35kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..480V_C_140G-J2_25kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..480V_C_140G-I3_35kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..480V_C_140G-I2_25kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..480V_C_140G-J6_65kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..480V_C_140G-J3_35kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..480V_C_140G-J2_25kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..480V_C_140G-I3_35kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-I3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..480V_C_140G-I2_25kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-I2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..480V_C_140G-J6_65kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..480V_C_140G-J3_35kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..480V_C_140G-J2_25kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..480V_C_140G-I3_35kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-I3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..480V_C_140G-I2_25kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-I2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..480V_C_140G-J6_65kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..480V_C_140G-J3_35kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..480V_C_140G-J2_25kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..480V_C_140G-I3_35kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-I3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..480V_C_140G-I2_25kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-I2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-F…-E3EC*H_26-..600V_C_140G-J6_25kA_2 (AB500DAB026) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..600V_C_140G-J3_18kA_2 (AB500DAB026) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..600V_C_140G-J2_14kA_2 (AB500DAB026) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..600V_C_140G-J6_25kA_2 (AB500DAB027) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..600V_C_140G-J3_18kA_2 (AB500DAB027) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..600V_C_140G-J2_14kA_2 (AB500DAB027) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_28-..600V_C_140G-J6_25kA_2 (AB500DAB028) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_28-..600V_C_140G-J3_18kA_2 (AB500DAB028) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_28-..600V_C_140G-J2_14kA_2 (AB500DAB028) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-A…-E3EC*D_01-..600V_C_140G-6_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*PC | 600 | 3 | 5 | 0.4-2 | ---
AB500F-A…-E3EC*D_02-..600V_C_140G-6_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..600V_C_140G-6_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_04-04/2HP-..600V_C_140G-6_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_05-..600V_C_140G-6_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_06-..600V_C_140G-6_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_07-..600V_C_140G-6_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_08-..600V_C_140G-6_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_09-1/2HP-..600V_C_140G-6_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_10-..600V_C_140G-6_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-C…-E3EC*D_11-..600V_C_140G-6_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-C…-E3EC*D_12-..600V_C_140G-6_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_13-..600V_C_140G-6_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_14-..600V_C_140G-6_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_15-..600V_C_140G-6_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_16-..200V_C_140G-6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..230V_C_140G-6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..480V_C_140G-6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_16-..600V_C_140G-6_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-JC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_17-..200V_C_140G-6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..230V_C_140G-6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..480V_C_140G-6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_17-..600V_C_140G-6_25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-JC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_18-..480V_C_140G-6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_18-..600V_C_140G-6_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_19-..480V_C_140G-6_65kA (AB500DAB019) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_19-..600V_C_140G-6_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 41 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_20-..480V_C_140G-6_65kA (AB500DAB020) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_20-..600V_C_140G-6_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 600 | 3 | 5 | 18-90 | ---
AB500F-E…-E3EC*F_21-..200V_C_140G-6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..230V_C_140G-6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..480V_C_140G-6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..600V_C_140G-6_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..480V_C_140G-6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..600V_C_140G-6_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..480V_C_140G-6_65kA (AB500DAB023) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..600V_C_140G-6_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 62 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..480V_C_140G-6_65kA (AB500DAB024) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..600V_C_140G-6_25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_25-..600V_C_140G-6_25kA (AB500DAB025) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 99 | 100 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-F…-E3EC*H_26-..200V_C_140G-KC6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-KC6*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EC*HF | 200 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..230V_C_140G-KC6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-KC6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EC*HF | 230 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..480V_C_140G-KC6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-KC6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..600V_C_140G-6_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..230V_C_140G-KC6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-KC6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EC*HF | 230 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..480V_C_140G-KC6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-KC6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..600V_C_140G-6_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-JC6*200 | 600 | 3 | 25 | 200 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_28-..600V_C_140G-6_25kA (AB500DAB028) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-A…-E3EC*D_01-..200V_C_140G-6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..230V_C_140G-6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..480V_C_140G-6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..200V_C_140G-6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..230V_C_140G-6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..480V_C_140G-6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..200V_C_140G-6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..230V_C_140G-6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..480V_C_140G-6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_04-04/2HP-..200V_C_140G-6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_04-04/2HP-..230V_C_140G-6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_04-04/2HP-..480V_C_140G-6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_05-..200V_C_140G-6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_05-..230V_C_140G-6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_05-..480V_C_140G-6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_06-..200V_C_140G-6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_06-..480V_C_140G-6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_07-..480V_C_140G-6_65kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_08-..200V_C_140G-6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 200 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_08-..230V_C_140G-6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_08-..480V_C_140G-6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_09-1/2HP-..200V_C_140G-6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-B…-E3EC*D_09-1/2HP-..480V_C_140G-6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_10-..480V_C_140G-6_65kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..200V_C_140G-6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..230V_C_140G-6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..480V_C_140G-6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-C…-E3EC*D_12-..480V_C_140G-6_65kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 480 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_13-..480V_C_140G-6_65kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 65 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_14-..480V_C_140G-6_65kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_15-..200V_C_140G-6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..230V_C_140G-6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..480V_C_140G-6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_16-..200V_C_140G-6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..230V_C_140G-6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..480V_C_140G-6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_17-..200V_C_140G-6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..230V_C_140G-6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..480V_C_140G-6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_18-..480V_C_140G-6_65kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_19-..480V_C_140G-6_65kA_2 (AB500DAB019) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_20-..480V_C_140G-6_65kA_2 (AB500DAB020) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-E…-E3EC*F_21-..200V_C_140G-6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..230V_C_140G-6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..480V_C_140G-6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..480V_C_140G-6_65kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..480V_C_140G-6_65kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..480V_C_140G-6_65kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-F…-E3EC*H_26-..600V_C_140G-6_25kA_2 (AB500DAB026) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..600V_C_140G-6_25kA_2 (AB500DAB027) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_28-..600V_C_140G-6_25kA_2 (AB500DAB028) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(7) = See Table 7 for minimum internal power wiring.
Table 7 - Minimum Internal Power Wiring
1/32in. thick thermoplastic insulation, rated 105C
Wire Code |  | Wire Size
7a |  | 10 AWG
7b |  | 10 AWG
7c |  | 8 AWG
7d |  | 4 AWG
7e |  | 1AWG
7f |  | 250 MCM

## 500F C E300
[16 empty] | Issued: | 2015-12-31
[16 empty] | Last Revised: | 2017-10-10
ID Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number [1] | Voltage | Number of Phases | SCCR, kA | Full Load Current, A | HP rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP Rating | Enclosure Volume, Cu Ft
AB500F-A…-E300ESM-*-30A-S2_01-..200V_C_140G-G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..200V_C_140G-G3_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..200V_C_140G-G2_50kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..230V_C_140G-G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..230V_C_140G-G3_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..230V_C_140G-G2_50kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..480V_C_140G-G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..480V_C_140G-G3_35kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..480V_C_140G-G2_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..600V_C_140G-H6_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..600V_C_140G-H3_18kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..600V_C_140G-H2_14kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..200V_C_140G-G6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..200V_C_140G-G3_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..200V_C_140G-G2_50kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..230V_C_140G-G6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..230V_C_140G-G3_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..230V_C_140G-G2_50kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..480V_C_140G-G6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..480V_C_140G-G3_35kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..480V_C_140G-G2_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..600V_C (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..600V_C (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..600V_C (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..200V_C_140G-G6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..200V_C_140G-G3_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..200V_C_140G-G2_50kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..230V_C_140G-G6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..230V_C_140G-G3_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..230V_C_140G-G2_50kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..480V_C_140G-G6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..480V_C_140G-G3_35kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..480V_C_140G-G2_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..600V_C_140G-H6_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..600V_C_140G-H3_18kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..600V_C_140G-H2_14kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..200V_C_140G-G6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..200V_C_140G-G3_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..200V_C_140G-G2_50kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..230V_C_140G-G6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..230V_C_140G-G3_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..230V_C_140G-G2_50kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..480V_C_140G-G6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..480V_C_140G-G3_35kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..480V_C_140G-G2_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..600V_C_140G-H6_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..600V_C_140G-H3_18kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..600V_C_140G-H2_14kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..200V_C_140G-G6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..200V_C_140G-G3_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..200V_C_140G-G2_50kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..230V_C_140G-G6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..230V_C_140G-G3_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..230V_C_140G-G2_50kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..480V_C_140G-G6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..480V_C_140G-G3_35kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..480V_C_140G-G2_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..600V_C_140G-H6_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..600V_C_140G-H3_18kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..600V_C_140G-H2_14kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..200V_C_140G-G6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..200V_C_140G-G3_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..200V_C_140G-G2_50kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..480V_C_140G-G6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..480V_C_140G-G3_35kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..480V_C_140G-G2_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..600V_C_140G-H6_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | 600 | 3 | 5 | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | 600 | 3 | 5 | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..600V_C_140G-H3_18kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | 600 | 3 | 5 | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | 600 | 3 | 5 | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..600V_C_140G-H2_14kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | 600 | 3 | 5 | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | 600 | 3 | 5 | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_07-..480V_C_140G-G6_65kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_07-..480V_C_140G-G3_35kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_07-..480V_C_140G-G2_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_07-..600V_C_140G-H6_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_07-..600V_C_140G-H3_18kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_07-..600V_C_140G-H2_14kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..200V_C_140G-G6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..200V_C_140G-G3_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..200V_C_140G-G2_50kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..230V_C_140G-G6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..230V_C_140G-G3_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..230V_C_140G-G2_50kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..480V_C_140G-G6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..480V_C_140G-G3_35kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..480V_C_140G-G2_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..600V_C_140G-H6_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..600V_C_140G-H3_18kA (AB500DAB008) | C | x | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..600V_C_140G-H2_14kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..200V_C_140G-G6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..200V_C_140G-G3_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..200V_C_140G-G2_50kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..480V_C_140G-G6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..480V_C_140G-G3_35kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..480V_C_140G-G2_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..600V_C_140G-H6_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..600V_C_140G-H3_18kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..600V_C_140G-H2_14kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_10-..480V_C_140G-G6_65kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_10-..480V_C_140G-G3_35kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_10-..480V_C_140G-G2_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_10-..600V_C_140G-H6_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_10-..600V_C_140G-H3_18kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_10-..600V_C_140G-H2_14kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..200V_C_140G-G6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 200 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..200V_C_140G-G3_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 200 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..200V_C_140G-G2_50kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*50 | 200 | 3 | 50 | 50 | --- | 200 | 3 | 50 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 200 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..230V_C_140G-G6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..230V_C_140G-G3_65kA (AB500DAB011) | C | xv | Allen Bradley | 140G-G3*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..230V_C_140G-G2_50kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*50 | 230 | 3 | 50 | 50 | --- | 230 | 3 | 50 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..480V_C_140G-G6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..480V_C_140G-G3_35kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..480V_C_140G-G2_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..600V_C_140G-H6_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..600V_C_140G-H3_18kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..600V_C_140G-H2_14kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_12-..480V_C_140G-G6_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_12-..480V_C_140G-G3_35kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_12-..480V_C_140G-G2_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_12-..600V_C_140G-H6_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_12-..600V_C_140G-H3_18kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_12-..600V_C_140G-H2_14kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_13-..480V_C_140G-G6_65kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_13-..480V_C_140G-G3_35kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_13-..480V_C_140G-G2_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_13-..600V_C_140G-H6_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_13-..600V_C_140G-H3_18kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_13-..600V_C_140G-H2_14kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_14-..480V_C_140G-G6_65kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_14-..480V_C_140G-G3_35kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_14-..480V_C_140G-G2_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_14-..600V_C_140G-H6_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_14-..600V_C_140G-H3_18kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_14-..600V_C_140G-H2_14kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..200V_C_140G-H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..200V_C_140G-H3_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..200V_C_140G-H2_50kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..230V_C_140G-H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..230V_C_140G-H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..230V_C_140G-H2_50kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..480V_C_140G-H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..480V_C_140G-H3_35kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..480V_C_140G-H2_25kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..200V_C_140G-H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..200V_C_140G-H3_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..200V_C_140G-H2_50kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..230V_C_140G-H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..230V_C_140G-H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..230V_C_140G-H2_50kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..480V_C_140G-H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | 480 | 3 | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | 480 | 3 | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..480V_C_140G-H3_35kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | 480 | 3 | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | 480 | 3 | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..480V_C_140G-H2_25kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | 480 | 3 | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | 480 | 3 | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..200V_C_140G-H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..200V_C_140G-H3_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..200V_C_140G-H2_50kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..230V_C_140G-H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..230V_C_140G-H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..230V_C_140G-H2_50kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..480V_C_140G-H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..480V_C_140G-H3_35kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..480V_C_140G-H2_25kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..200V_C_140G-H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..200V_C_140G-H3_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..200V_C_140G-H2_50kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..230V_C_140G-H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..230V_C_140G-H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..230V_C_140G-H2_50kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..480V_C_140G-H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..480V_C_140G-H3_35kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..480V_C_140G-H2_25kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..200V_C_140G-H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..200V_C_140G-H3_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..200V_C_140G-H2_50kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..230V_C_140G-H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..230V_C_140G-H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..230V_C_140G-H2_50kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..480V_C_140G-H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..480V_C_140G-H3_35kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..480V_C_140G-H2_25kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..200V_C_140G-H6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..200V_C_140G-H3_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..200V_C_140G-H2_50kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..230V_C_140G-H6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..230V_C_140G-H6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..230V_C_140G-H2_50kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..480V_C_140G-H6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..480V_C_140G-H3_35kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..480V_C_140G-H2_25kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_07-..480V_C_140G-H6_65kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_07-..480V_C_140G-H3_35kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_07-..480V_C_140G-H2_25kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..200V_C_140G-H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..200V_C_140G-H3_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..200V_C_140G-H2_50kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..230V_C_140G-H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..230V_C_140G-H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..230V_C_140G-H2_50kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..480V_C_140G-H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..480V_C_140G-H3_35kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..480V_C_140G-H2_25kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..200V_C_140G-H6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..200V_C_140G-H3_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..200V_C_140G-H2_50kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..480V_C_140G-H6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..480V_C_140G-H3_35kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..480V_C_140G-H2_25kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_10-..480V_C_140G-H6_65kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_10-..480V_C_140G-H3_35kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_10-..480V_C_140G-H2_25kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..200V_C_140G-H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 200 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..200V_C_140G-H3_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 200 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..200V_C_140G-H2_50kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*50 | 200 | 3 | 50 | 50 | --- | 200 | 3 | 50 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 200 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..230V_C_140G-H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..230V_C_140G-H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..230V_C_140G-H2_50kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*50 | 230 | 3 | 50 | 50 | --- | 230 | 3 | 50 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..480V_C_140G-H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..480V_C_140G-H3_35kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..480V_C_140G-H2_25kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_12-..230V_C_140G-H6_65kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_12-..230V_C_140G-H6_65kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_12-..230V_C_140G-H2_50kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 42 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_12-..480V_C_140G-H6_65kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_12-..480V_C_140G-H3_35kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_12-..480V_C_140G-H2_25kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_13-..480V_C_140G-H6_65kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_13-..480V_C_140G-H3_35kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_13-..480V_C_140G-H2_25kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_14-..480V_C_140G-H6_65kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_14-..480V_C_140G-H3_35kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_14-..480V_C_140G-H2_25kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..600V_C_140G-6_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..600V_C (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..600V_C_140G-6_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..600V_C_140G-6_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..600V_C_140G-6_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_07-..480V_C_140G-G6_65kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_07-..600V_C_140G-6_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..600V_C_140G-6_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..600V_C_140G-6_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_10-..600V_C_140G-6_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..600V_C_140G-6_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_12-..600V_C_140G-6_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_13-..600V_C_140G-6_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_14-..600V_C_140G-6_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..200V_C_140G-6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..230V_C_140G-6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..480V_C_140G-6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..200V_C_140G-6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..230V_C_140G-6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..480V_C_140G-6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | 480 | 3 | 5 | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | 480 | 3 | 5 | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..200V_C_140G-6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..230V_C_140G-6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..480V_C_140G-6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..200V_C_140G-6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..230V_C_140G-6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..480V_C_140G-6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..200V_C_140G-6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..230V_C_140G-6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..480V_C_140G-6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..200V_C_140G-6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..230V_C_140G-6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..480V_C_140G-6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_07-..480V_C_140G-6_65kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..200V_C_140G-6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..230V_C_140G-6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..480V_C_140G-6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..200V_C_140G-6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..480V_C_140G-6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_10-..480V_C_140G-6_65kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..200V_C_140G-6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 200 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..230V_C_140G-6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..480V_C_140G-6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_12-..230V_C_140G-6_65kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_12-..480V_C_140G-6_65kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_13-..480V_C_140G-6_65kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_14-..480V_C_140G-6_65kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-G6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-G6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-G6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-H6*100 | 600 | 3 | 65 | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J6*100 | 600 | 3 | 65 | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J6*175 | 200 | 3 | 65 | 175 | --- | 200 | 3 | 22 | 120 | 40 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 5 | 120 | 40
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 200 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 22 | 139 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 5 | 139 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 230 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J6*175 | 480 | 3 | 65 | 175 | --- | 480 | 3 | 22 | 124 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 5 | 124 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 480 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J6*175 | 600 | 3 | 65 | 175 | --- | 600 | 3 | 14 | 99 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 5 | 99 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 600 | 3 | 5 | 20-135 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-HC6*100 | 600 | 3 | 65 | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-JC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-JC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 65 | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-JC6*175 | 200 | 3 | 65 | 175 | --- | 200 | 3 | 22 | 120 | 40 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 5 | 120 | 40
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 200 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-JC6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 22 | 139 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 5 | 139 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 230 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-JC6*175 | 480 | 3 | 65 | 175 | --- | 480 | 3 | 22 | 124 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 5 | 124 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 480 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-JC6*175 | 600 | 3 | 65 | 175 | --- | 600 | 3 | 14 | 99 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 5 | 99 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 600 | 3 | 5 | 20-135 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-G3*100 | 200 | 3 | 100 | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-G3*100 | 230 | 3 | 100 | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-G3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-H3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J3*100 | 200 | 3 | 100 | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J3*100 | 230 | 3 | 100 | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..I3...200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I3*100 | 200 | 3 | 100 | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..I3...230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I3*100 | 230 | 3 | 100 | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..I2...200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I2*100 | 200 | 3 | 100 | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..I2...230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I2*100 | 230 | 3 | 100 | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..I3...480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J3*175 | 200 | 3 | 100 | 175 | --- | 200 | 3 | 22 | 120 | 40 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 5 | 120 | 40
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 200 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J3*175 | 230 | 3 | 100 | 175 | --- | 230 | 3 | 22 | 139 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 5 | 139 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 230 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..I3...200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I3*175 | 200 | 3 | 100 | 175 | --- | 200 | 3 | 22 | 120 | 40 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 5 | 120 | 40
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 200 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..I3...230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I3*175 | 230 | 3 | 100 | 175 | --- | 230 | 3 | 22 | 139 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 5 | 139 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 230 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..I2...200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I2*175 | 200 | 3 | 100 | 175 | --- | 200 | 3 | 22 | 120 | 40 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 5 | 120 | 40
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 200 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..I2...230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I2*175 | 230 | 3 | 100 | 175 | --- | 230 | 3 | 22 | 139 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 5 | 139 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 230 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J3*175 | 480 | 3 | 35 | 175 | --- | 480 | 3 | 22 | 124 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 5 | 124 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 480 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..I3...480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I3*175 | 480 | 3 | 35 | 175 | --- | 480 | 3 | 22 | 124 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 5 | 124 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 480 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J3*175 | 600 | 3 | 18 | 175 | --- | 600 | 3 | 14 | 99 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 5 | 99 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 600 | 3 | 5 | 20-135 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-G2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-G2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-G2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-H2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J2*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..I3...200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..I2...230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J2*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..I2...480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I2*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J2*175 | 200 | 3 | 65 | 175 | --- | 200 | 3 | 22 | 120 | 40 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 5 | 120 | 40
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 200 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J2*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 22 | 139 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 5 | 139 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 230 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J2*175 | 480 | 3 | 25 | 175 | --- | 480 | 3 | 22 | 124 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 5 | 124 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 480 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..I2...480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I2*175 | 480 | 3 | 25 | 175 | --- | 480 | 3 | 22 | 124 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 5 | 124 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 480 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J2*175 | 600 | 3 | 14 | 175 | --- | 600 | 3 | 14 | 99 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 5 | 99 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 600 | 3 | 5 | 20-135 | ---
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(7) = See Table 7 for minimum internal power wiring.
Table 7 - Minimum Internal Power Wiring
1/32in. thick thermoplastic insulation, rated 105C
Wire Code |  | Wire Size
7a |  | 10 AWG
7b |  | 10 AWG
7c |  | 8 AWG
7d |  | 4 AWG
7e |  | 1AWG
7f |  | 250 MCM

## 500F D EUT
[16 empty] | Issued: | 2015-12-31
[16 empty] | Last Revised: | 2017-10-10
ID Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage | Number of Phases | SCCR, kA | Full Load Current, A | HP rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP Rating | Enclosure Volume, CU Ft
AB500F-A…-EUTB42_01-..200V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 200 | 3 | --- | 3 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..230V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 230 | 3 | --- | 3 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..480V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..600V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..200V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..230V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..480V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..600V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..200V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..230V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..480V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..600V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..200V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..200V (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1-1/2HP-..200V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..230V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..230V (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1-1/2HP-..230V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..480V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..480V (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1-1/2HP-..480V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..600V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..200V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..200V (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_2HP-..200V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..230V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..230V (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_2HP-..230V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..480V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..480V (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_2HP-..480V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..600V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*7 | 600 | 3 | --- | 7 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..200V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..200V (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3HP-..200V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..480V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..480V (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3HP-..480V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..600V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*7 | 600 | 3 | --- | 7 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_07-..480V_C (AB500DAB007) | D | ICB | Allen Bradley | 140MG-G8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..480V (AB500DAB007) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_5HP-..480V (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_07-..600V_C (AB500DAB007) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..200V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..200V (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_5HP-..200V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..230V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..230V (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_5HP-..230V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..480V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..480V (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_5HP-..480V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..600V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..230V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..230V (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_7-1/2HP-..230V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..480V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..480V (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_7-1/2HP-..480V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..600V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_10-..480V_C (AB500DAB010) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..480V (AB500DAB010) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_10HP-..480V (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_10-..600V_C (AB500DAB010) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-C…-EUTC42_11-..200V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..230V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..480V (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_10HP-..480V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..600V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..480V_C (AB500DAB012) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..480V (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_15HP-..480V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..600V_C (AB500DAB012) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_13-..480V_C (AB500DAB013) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..480V (AB500DAB013) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_20HP-..480V (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_13-..600V_C (AB500DAB013) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_14-..480V_C (AB500DAB014) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..480V (AB500DAB014) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_25HP-..480V (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_14-..600V_C (AB500DAB014) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB500F-D…-EUTD42_15-..200V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-G8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..230V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-G8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..480V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..480V (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_15HP-..480V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..600V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 17 | 15 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..200V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-G8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..230V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-G8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..480V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..600V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-J8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 22 | 20 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..200V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..230V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..480V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..480V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_25HP-..480V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..600V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-J8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 27 | 25 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..480V_C (AB500DAB018) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..600V_C (AB500DAB018) | D | ICB | Allen Bradley | 140MG-J8*80 | 600 | 3 | --- | 80 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..600V (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_30HP-..600V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_19-..480V_C (AB500DAB019) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_19-..600V_C (AB500DAB019) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 41 | 40 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_20-..480V_C (AB500DAB020) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42G_20-..480V_C (AB500DAB020) | D | ICB | Allen Bradley | 140MG-G8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_20-..600V_C (AB500DAB020) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB500F-E…-EUTE42_21-..200V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*150 | 200 | 3 | --- | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..230V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*125 | 230 | 3 | --- | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..480V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42I_21-..480V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..600V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*80 | 600 | 3 | --- | 80 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..480V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42I_22-..480V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..600V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..480V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42I_23-..480V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..600V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 62 | 60 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_24-..480V_C (AB500DAB024) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42I_24-..480V_C (AB500DAB024) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_24-..600V_C (AB500DAB024) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 77 | 75 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_25-..600V_C (AB500DAB025) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 99 | 100 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_100HP-..600V (AB500DAB025) |  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_100HP-..600V (AB500DAB025) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB500F-F…-EUTF42_26-..200V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-K8*400 | 200 | 3 | --- | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 200 | 3 | 10 | 221 | 75
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 200 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_26-..230V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-K8*400 | 230 | 3 | --- | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_26-..480V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-K8*175 | 480 | 3 | --- | 175 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_26-..600V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 125 | ---
AB500F-F…-EUTF42_27-..230V_C (AB500DAB027) | D | ICB | Allen Bradley | 140MG-K8*400 | 230 | 3 | --- | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_27-..480V_C (AB500DAB027) | D | ICB | Allen Bradley | 140MG-K8*400 | 480 | 3 | --- | 400 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_27-..600V_C (AB500DAB027) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_28-..600V_C (AB500DAB028) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-A…-EUTB42_01-..200V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 200 | 3 | --- | 3 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..230V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 230 | 3 | --- | 3 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_01-..480V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..200V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..230V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_02-..480V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..200V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..230V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_03-..480V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..200V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..230V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_04-04/2HP-..480V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..200V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..230V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_05-..480V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..200V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..230V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_06-..480V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_07-..480V_C_2 (AB500DAB007) | D | ICB | Allen Bradley | 140MG-H8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..200V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..230V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_08-..480V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..230V_C_2 (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..230V_2 (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_7-1/2HP-..230V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_09-1/2HP-..480V_C_2 (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-B…-EUTB42_10-..480V_C_2 (AB500DAB010) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-C…-EUTC42_11-..200V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..230V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42I_11-..200V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42I_11-..230V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_11-..480V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_12-..480V_C_2 (AB500DAB012) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_13-..480V_C_2 (AB500DAB013) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-C…-EUTC42_14-..480V_C_2 (AB500DAB014) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB500F-D…-EUTD42_15-..200V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42I_15-..200V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_15-..480V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..200V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..230V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42I_16-..200V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42I_16-..230V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_16-..480V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..480V_2 (AB500DAB016) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_20HP-..480V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..200V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..230V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42I_17-..200V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42I_17-..230V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_17-..480V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..480V_2 (AB500DAB017) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_25HP-..480V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..230V_C_2 (AB500DAB018) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42I_18-..230V_C_2 (AB500DAB018) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_18-..480V_C_2 (AB500DAB018) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_19-..480V_C_2 (AB500DAB019) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-D…-EUTD42_20-..480V_C_2 (AB500DAB020) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB500F-E…-EUTE42_21-..200V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*150 | 200 | 3 | --- | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..230V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*125 | 230 | 3 | --- | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42I_21-..200V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*150 | 200 | 3 | --- | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42I_21-..230V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*125 | 230 | 3 | --- | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_21-..480V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42I_21-..480V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_22-..480V_C_2 (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42I_22-..480V_C_2 (AB500DAB022) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42_23-..480V_C_2 (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-E…-EUTE42I_23-..480V_C_2 (AB500DAB023) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB500F-F…-EUTF42_26-..600V_C_2 (AB500DAB026) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_27-..600V_C_2 (AB500DAB027) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-F…-EUTF42_29-..600V_C_2 (AB500DAB029) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB500F-A…-EUTB42_32-..480V_D (AB500DAB032) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_32-..600V_D (AB500DAB032) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_33-..480V_D (AB500DAB033) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB500F-A…-EUTB42_34-..600V_D (AB500DAB034) | D | ICB | Allen Bradley | 140MG-H8*7 | 600 | 3 | --- | 7 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
Size 0-4; use Table 152 for W elements and Table 163 for J elements; Size 5 use Table 347 for W elements and Table 547 for J elements
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(7) = See Table 7 for minimum internal power wiring.
Table 7 - Minimum Internal Power Wiring
1/32in. thick thermoplastic insulation, rated 105C
Wire Code |  | Wire Size
7a |  | 10 AWG
7b |  | 10 AWG
7c |  | 8 AWG
7d |  | 4 AWG
7e |  | 1AWG
7f |  | 250 MCM

## 500F D E1+
[16 empty] | Issued: | 2015-12-31
[16 empty] | Last Revised: | 2017-10-10
ID Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage | Number of Phases | SCCR, kA | Full Load Current, A | HP rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP Rating | Enclosure Volume, CU Ft
AB500F-A…-E1+EEEC_01-..200V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 200 | 3 | --- | 3 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_01-..230V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 230 | 3 | --- | 3 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_01-..480V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_01-..600V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEBC | 600 | 3 | 5 | 0.2-1 | ---
AB500F-A…-E1+EEEC_02-..200V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_02-..230V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_02-..480V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_02-..600V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_03-..200V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_03-..230V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_03-..480V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_03-..600V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..200V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..230V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..480V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..600V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_05-..200V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_05-..230V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_05-..480V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_05-..600V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*7 | 600 | 3 | --- | 7 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_06-..200V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_06-..480V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_06-..600V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*7 | 600 | 3 | --- | 7 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB500F-A…-E1+EEEC_07-..480V_C (AB500DAB007) | D | ICB | Allen Bradley | 140MG-G8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_07-..600V_C (AB500DAB007) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | 5
AB500F-B…-E1+EEEC_08-..200V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 200 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_08-..230V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_08-..480V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_08-..600V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..200V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..480V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..600V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_10-..480V_C (AB500DAB010) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_10-..600V_C (AB500DAB010) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | 10
AB500F-C…-E1+EEFC_11-..200V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..230V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-C…-E1+EEFC_11-..600V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-C…-E1+EEFC_12-..480V_C (AB500DAB012) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_12-..600V_C (AB500DAB012) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_13-..480V_C (AB500DAB013) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_13-..600V_C (AB500DAB013) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_14-..480V_C (AB500DAB014) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEFC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_14-..600V_C (AB500DAB014) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-2.7 | ---
AB500F-D…-E1+EEGD_15-..200V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-G8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..230V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-G8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..480V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_15-..600V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 17 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_16-..200V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-G8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..230V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-G8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..480V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_16-..600V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-J8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 22 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_17-..200V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-G8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..230V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-G8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..480V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_17-..600V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-J8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 27 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_18-..230V_C (AB500DAB018) | D | ICB | Allen Bradley | 140MG-G8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_18-..480V_C (AB500DAB018) | D | ICB | Allen Bradley | 140MG-G8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_18-..600V_C (AB500DAB018) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_19-..480V_C (AB500DAB019) | D | ICB | Allen Bradley | 140MG-G8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_19-..600V_C (AB500DAB019) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 41 | 40 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_20-..480V_C (AB500DAB020) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_20-..G480V_C (AB500DAB020) | D | ICB | Allen Bradley | 140MG-G8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_20-..600V_C (AB500DAB020) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEGD | 600 | 3 | 5 | 18-90 | ---
AB500F-E…-E1+EEHE_21-..200V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*150 | 200 | 3 | --- | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..230V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*125 | 230 | 3 | --- | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..480V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..I480V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..600V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..230V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*150 | 230 | 3 | --- | 150 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..480V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..I480V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..600V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..480V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..I480V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..600V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 62 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..480V_C (AB500DAB024) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..I480V_C (AB500DAB024) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..600V_C (AB500DAB024) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 77 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_25-..600V_C (AB500DAB025) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 99 | 100 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB500F-F…-E1+EEKF_26-..200V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-K8*400 | 200 | 3 | --- | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EEKF | 200 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..230V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-K8*400 | 230 | 3 | --- | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EEKF | 230 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..480V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-K8*400 | 480 | 3 | --- | 400 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_26-..600V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..480V_C (AB500DAB027) | D | ICB | Allen Bradley | 140MG-J8*175 | 480 | 3 | --- | 175 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..I480V_C (AB500DAB027) | D | ICB | Allen Bradley | 140MG-I8*175 | 480 | 3 | --- | 175 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..600V_C (AB500DAB027) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_28-..600V_C (AB500DAB028) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-A…-E1+EEEC_01-..200V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 200 | 3 | --- | 3 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_01-..230V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 230 | 3 | --- | 3 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_01-..480V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_02-..200V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_02-..230V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_02-..480V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_03-..200V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_03-..230V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_03-..480V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..200V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..230V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E04+EEEC_04-04/2HP-..480V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_05-..200V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_05-..230V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_05-..480V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_06-..200V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-E1+EEEC_06-..480V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E1+EEEC_07-..480V_C_2 (AB500DAB007) | D | ICB | Allen Bradley | 140MG-H8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_08-..200V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 200 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_08-..230V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_08-..480V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..200V_C_2 (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-E1+EEEC_09-1/2HP-..480V_C_2 (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-E1+EEEC_10-..480V_C_2 (AB500DAB010) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_11-..200V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..230V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..I200V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..I230V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E1+EEFC_11-..480V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_12-..480V_C_2 (AB500DAB012) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_13-..480V_C_2 (AB500DAB013) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-E1+EEFC_14-..480V_C_2 (AB500DAB014) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEFC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_15-..200V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..230V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..I200V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..I230V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_15-..480V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_16-..200V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..230V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..I200V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..I230V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_16-..480V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_17-..200V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..230V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..I200V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..I230V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_17-..480V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_18-..480V_C_2 (AB500DAB018) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E1+EEGD_19-..480V_C_2 (AB500DAB019) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E1+EEGD_20-..480V_C_2 (AB500DAB020) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB500F-E…-E1+EEHE_21-..200V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*150 | 200 | 3 | --- | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..230V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*125 | 230 | 3 | --- | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..I200V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*150 | 200 | 3 | --- | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..I230V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*125 | 230 | 3 | --- | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..480V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_21-..I480V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..480V_C_2 (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_22-..I480V_C_2 (AB500DAB022) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..480V_C_2 (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_23-..I480V_C_2 (AB500DAB023) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..480V_C_2 (AB500DAB024) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_24-..480V_C_2 (AB500DAB024) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB500F-F…-E1+EEKF_26-..600V_C_2 (AB500DAB026) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_27-..600V_C_2 (AB500DAB027) | D | ICB | Allen Bradley | 140MG-J8*200 | 600 | 3 | --- | 200 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-F…-E1+EEKF_28-..600V_C_2 (AB500DAB028) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB500F-E…-E1+EEHE_31-..I230V_C_2 (AB500DAB031) | D | ICB | Allen Bradley | 140MG-I8*150 | 230 | 3 | --- | 150 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB500F-E…-E1+EEHE_31-..230V_C_2 (AB500DAB031) | D | ICB | Allen Bradley | 140MG-J8*150 | 230 | 3 | --- | 150 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-A…-E1+EEEC_32-..480V_D (AB500DAB032) | D | ICB | Allen Bradley | 140MG-G8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | 0 | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_32-..600V_D (AB500DAB032) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
Size 0-4; use Table 152 for W elements and Table 163 for J elements; Size 5 use Table 347 for W elements and Table 547 for J elements
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(7) = See Table 7 for minimum internal power wiring.
Table 7 - Minimum Internal Power Wiring
1/32in. thick thermoplastic insulation, rated 105C
Wire Code |  | Wire Size
7a |  | 10 AWG
7b |  | 10 AWG
7c |  | 8 AWG
7d |  | 4 AWG
7e |  | 1AWG
7f |  | 250 MCM

## 500F D E3
[16 empty] | Issued: | 2015-12-31
[16 empty] | Last Revised: | 2017-10-10
ID Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage | Number of Phases | SCCR, kA | Full Load Current, A | HP rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP Rating | Enclosure Volume, CU Ft
AB500F-A…-E3EC*D_01-..200V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 200 | 3 | --- | 3 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..230V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 230 | 3 | --- | 3 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..480V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..600V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*PC | 600 | 3 | 5 | 0.4-2 | ---
AB500F-A…-E3EC*D_02-..200V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..230V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..480V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..600V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..200V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..230V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*7 | 230 | 3 | --- | 7 | 3 | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..480V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..600V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_04-04/2HP-..200V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_04-04/2HP-..230V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_04-04/2HP-..480V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_04-04/2HP-..600V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_05-..200V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_05-..230V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_05-..480V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_05-..600V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*7 | 600 | 3 | --- | 7 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_06-..200V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_06-..230V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_06-..480V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_06-..600V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*7 | 600 | 3 | --- | 7 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_07-..480V_C (AB500DAB007) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_07-..600V_C (AB500DAB007) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_08-..200V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 200 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_08-..230V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_08-..480V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_08-..600V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_09-1/2HP-..200V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-B…-E3EC*D_09-1/2HP-..480V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_09-1/2HP-..600V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_10-..480V_C (AB500DAB010) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-B…-E3EC*D_10-..600V_C (AB500DAB010) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-C…-E3EC*D_11-..200V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..230V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-C…-E3EC*D_11-..600V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB500F-C…-E3EC*D_12-..480V_C (AB500DAB012) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 480 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_12-..600V_C (AB500DAB012) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_13-..480V_C (AB500DAB013) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_13-..600V_C (AB500DAB013) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_14-..480V_C (AB500DAB014) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_14-..600V_C (AB500DAB014) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_15-..200V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-G8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..230V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-G8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..480V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_15-..600V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 17 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_16-..200V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..230V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..480V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_16-..600V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-J8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 22 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_17-..200V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..230V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..480V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_17-..600V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-J8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 27 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_18-..230V_C (AB500DAB018) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_18-..480V_C (AB500DAB018) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_18-..600V_C (AB500DAB018) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_19-..480V_C (AB500DAB019) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_19-..600V_C (AB500DAB019) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 41 | 40 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_20-..480V_C (AB500DAB020) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_20-..G480V_C (AB500DAB020) | D | ICB | Allen Bradley | 140MG-G8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_20-..600V_C (AB500DAB020) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 600 | 3 | 5 | 18-90 | ---
AB500F-E…-E3EC*F_21-..200V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*150 | 200 | 3 | --- | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..230V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*125 | 230 | 3 | --- | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..480V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..I480V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..600V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..480V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..I480V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..600V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..480V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..I480V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..480V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..600V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 62 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..480V_C (AB500DAB024) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..I480V_C (AB500DAB024) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..600V_C (AB500DAB024) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 77 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_25-..600V_C (AB500DAB025) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 99 | 100 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB500F-F…-E3EC*H_26-..200V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-K8*400 | 200 | 3 | --- | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EC*HF | 200 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..230V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-K8*400 | 230 | 3 | --- | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EC*HF | 230 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..480V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-J8*175 | 480 | 3 | --- | 175 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..I480V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-I8*175 | 480 | 3 | --- | 175 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_26-..600V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..480V_C (AB500DAB027) | D | ICB | Allen Bradley | 140MG-J8*250 | 480 | 3 | --- | 250 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..600V_C (AB500DAB027) | D | ICB | Allen Bradley | 140MG-J8*200 | 600 | 3 | --- | 200 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_28-..480V_C (AB500DAB028) | D | ICB | Allen Bradley | 140MG-K8*400 | 480 | 3 | --- | 400 | --- | 480 | 3 | 65 | 240 | 200 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_28-..600V_C (AB500DAB028) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-A…-E3EC*D_01-..200V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 200 | 3 | --- | 3 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..230V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 230 | 3 | --- | 3 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_01-..480V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..200V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..230V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_02-..480V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..200V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..230V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_03-..480V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_04-04/2HP-..200V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_04-04/2HP-..230V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_04-04/2HP-..480V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_05-..200V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_05-..230V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_05-..480V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_06-..200V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB500F-A…-E3EC*D_06-..480V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB500F-A…-E3EC*D_07-..480V_C_2 (AB500DAB007) | D | ICB | Allen Bradley | 140MG-H8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_08-..200V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 200 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_08-..230V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_08-..480V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_09-1/2HP-..230V_C_2 (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB500F-B…-E3EC*D_09-1/2HP-..480V_C_2 (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-B…-E3EC*D_10-..480V_C_2 (AB500DAB010) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..200V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 200 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..230V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_11-..480V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB500F-C…-E3EC*D_12-..480V_C_2 (AB500DAB012) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 480 | 3 | 5 | 5.0-25 | ---
AB500F-C…-E3EC*D_13-..480V_C_2 (AB500DAB013) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 65 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-C…-E3EC*D_14-..480V_C_2 (AB500DAB014) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_15-..200V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..230V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..I200V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..I230V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_15-..480V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_16-..200V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..230V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..I200V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..I230V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_16-..480V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_17-..200V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..230V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..I200V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..I230V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_17-..480V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_18-..480V_C_2 (AB500DAB018) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB500F-D…-E3EC*E_19-..480V_C_2 (AB500DAB019) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-D…-E3EC*E_20-..480V_C_2 (AB500DAB020) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB500F-E…-E3EC*F_21-..200V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*150 | 200 | 3 | --- | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..230V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*125 | 230 | 3 | --- | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..I200V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*150 | 200 | 3 | --- | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..I230V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*125 | 230 | 3 | --- | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..480V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_21-..I480V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..480V_C_2 (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_22-..I480V_C_2 (AB500DAB022) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..480V_C_2 (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_23-..I480V_C_2 (AB500DAB023) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..480V_C_2 (AB500DAB024) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-E…-E3EC*F_24-..I480V_C_2 (AB500DAB024) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB500F-F…-E3EC*H_26-..600V_C_2 (AB500DAB026) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB500F-F…-E3EC*H_27-..600V_C_2 (AB500DAB027) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_28-..600V_C_2 (AB500DAB028) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-A…-E3EC*D_32-..480V_D (AB500DAB032) | D | ICB | Allen Bradley | 140MG-G8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_32-..600V_D (AB500DAB032) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(7) = See Table 7 for minimum internal power wiring.
Table 7 - Minimum Internal Power Wiring
1/32in. thick thermoplastic insulation, rated 105C
Wire Code |  | Wire Size
7a |  | 10 AWG
7b |  | 10 AWG
7c |  | 8 AWG
7d |  | 4 AWG
7e |  | 1AWG
7f |  | 250 MCM

## 500F D E300
[16 empty] | Issued: | 2015-12-31
[16 empty] | Last Revised: | 2017-10-10
ID Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage | Number of Phases | SCCR, kA | Full Load Current, A | HP rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP Rating | Enclosure Volume, Cu Ft
AB500F-A…-E300ESM-*-30A-S2_01-..200V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 200 | 3 | --- | 3 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..230V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 230 | 3 | --- | 3 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..480V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..600V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..200V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..230V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..480V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..600V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..200V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..230V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..480V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..600V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..200V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..230V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..480V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..600V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..200V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..230V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..480V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..600V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*7 | 600 | 3 | --- | 7 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..200V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..230V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..480V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..600V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*7 | 600 | 3 | --- | 7 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_07-..480V_C (AB500DAB007) | D | ICB | Allen Bradley | 140MG-G8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_07-..600V_C (AB500DAB007) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..200V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..230V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..480V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..600V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..230V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..480V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..600V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_10-..480V_C (AB500DAB010) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_10-..600V_C (AB500DAB010) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..200V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 200 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..230V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..600V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_12-..480V_C (AB500DAB012) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_12-..600V_C (AB500DAB012) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_13-..480V_C (AB500DAB013) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_13-..600V_C (AB500DAB013) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_14-..480V_C (AB500DAB014) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_14-..600V_C (AB500DAB014) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..200V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 200 | 3 | --- | 3 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..230V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 230 | 3 | --- | 3 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_01-..480V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..200V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..230V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_02-..480V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..200V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..230V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_03-..480V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..200V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..230V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_04-04/2HP-..480V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..200V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..230V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_05-..480V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..200V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..230V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_06-..480V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_07-..480V_C_2 (AB500DAB007) | D | ICB | Allen Bradley | 140MG-H8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..200V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..230V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_08-..480V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..200V_C_2 (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 25.3 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..230V_C_2 (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_09-1/2HP-..480V_C_2 (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-B…-E300ESM-*-30A-S2_10-..480V_C_2 (AB500DAB010) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..200V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 200 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..230V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_11-..480V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_12-..480V_C_2 (AB500DAB012) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_13-..480V_C_2 (AB500DAB013) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-C…-E300ESM-*-60A-S2_14-..480V_C_2 (AB500DAB014) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB500F-A…-E300ESM-*-30A-S2_28-..480V_D (AB500DAB028) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB500F-A…-E300ESM-*-30A-S2_28-..600V_D (AB500DAB028) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..I200V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..I230V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..I480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-J8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-J8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..I200V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..I230V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..I480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB500F-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..200V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-J8*175 | 200 | 3 | --- | 175 | --- | 200 | 3 | 22 | 120 | 40 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 200 | 3 | 5 | 120 | 40
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 200 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..230V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-J8*175 | 230 | 3 | --- | 175 | --- | 230 | 3 | 22 | 139 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 230 | 3 | 5 | 139 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 230 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-J8*175 | 480 | 3 | --- | 175 | --- | 480 | 3 | 22 | 124 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 5 | 124 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 480 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..I480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*175 | 480 | 3 | --- | 175 | --- | 480 | 3 | 22 | 124 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 480 | 3 | 5 | 124 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 480 | 3 | 5 | 20-135 | ---
AB500F-E…-E300ESM-*-200A-S4_11-..600V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-J8*175 | 600 | 3 | --- | 175 | --- | 600 | 3 | 14 | 99 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 500F-E | 600 | 3 | 5 | 99 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 600 | 3 | 5 | 20-135 | ---
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(7) = See Table 7 for minimum internal power wiring.
Table 7 - Minimum Internal Power Wiring
1/32in. thick thermoplastic insulation, rated 105C
Wire Code |  | Wire Size
7a |  | 10 AWG
7b |  | 10 AWG
7c |  | 8 AWG
7d |  | 4 AWG
7e |  | 1AWG
7f |  | 250 MCM

## 509 C EUT
[16 empty] | Issued: | 2015-12-31
[16 empty] | Last Revised: | 2017-10-10
ID Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage | Number of Phases | SCCR, kA | Full Load Current, A | HP rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP Rating | Enclosure Volume, Cu Ft
AB509-A…-EUTB42_01-..200V_C_140G-G6*_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..200V_C_140G-G3*_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..200V_C_50kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 2.5 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..230V_C_140G-G6*_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..230V_C_140G-G3*_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..230V_C _50kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 2.2 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..480V_C_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..480V_C_35kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.1 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..480V_C_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.1 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..600V_C_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..600V_C_18kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 0.9 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..600V_C_14kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 0.9 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..200V_C_140G-G6*_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..200V_C_140G-G3*_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..200V_C _50kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 3.7 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..230V_C_140G-G6*_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..230V_C_140G-G3*_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..230V_C_50kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 3.2 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..480V_C_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..480V_C_35kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.6 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..480V_C_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.6 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..600V_C_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..600V_C_18kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 1.3 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..600V_C_14kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 1.3 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..200V_C_140G-G6*_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..200V_C_140G-G3*_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..200V_C_50kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 4.8 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..230V_C_140G-G6*_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..230V_C_140G-G3*_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..230V_C_50kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 4.2 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..480V_C_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..480V_C_35kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 2.1 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..480V_C_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 2.1 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..600V_C_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..600V_C_18kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 1.7 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..600V_C_14kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 1.7 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..200V_C_140G-G6*_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..200V (AB500DAB004) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1-1/2HP-..200V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..200V_C_140G-G3*_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..200V (AB500DAB004) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1-1/2HP-..200V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..200V_C_50kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 6.9 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..200V (AB500DAB004) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1-1/2HP-..200V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..230V_C_140G-G6*_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..230V (AB500DAB004) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1-1/2HP-..230V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..230V_C_140G-G3*_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..230V (AB500DAB004) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1-1/2HP-..230V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..230V_C_50kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..230V (AB500DAB004) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1-1/2HP-..230V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..480V_C_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..480V (AB500DAB004) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1-1/2HP-..480V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..480V_C_35kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..480V (AB500DAB004) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1-1/2HP-..480V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..480V_C_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..480V (AB500DAB004) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1-1/2HP-..480V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..600V_C _25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..600V_C_18kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 2.4 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..600V_C_14kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 2.4 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..200V_C_140G-G6*_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..200V (AB500DAB005) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_2HP-..200V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..200V_C_140G-G3*_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..200V (AB500DAB005) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_2HP-..200V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..200V_C_50kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 7.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..200V (AB500DAB005) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_2HP-..200V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..230V_C_140G-G6*_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..230V (AB500DAB005) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_2HP-..230V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..230V_C_140G-G3*_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..230V (AB500DAB005) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_2HP-..230V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..230V_C_50kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..230V (AB500DAB005) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_2HP-..230V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..480V_C_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..480V (AB500DAB005) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_2HP-..480V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..480V_C_35kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3.4 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..480V (AB500DAB005) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_2HP-..480V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..480V_C_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3.4 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..480V (AB500DAB005) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_2HP-..480V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..600V_C_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..600V_C_18kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 2.7 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..600V_C_14kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 2.7 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..200V_C_140G-G6*_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..200V (AB500DAB006) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3HP-..200V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..200V_C_140G-G3*_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..200V (AB500DAB006) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3HP-..200V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..200V_C_50kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 11 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..200V (AB500DAB006) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3HP-..200V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..230V_C_140G-G6*_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..230V (AB500DAB006) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3HP-..230V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..230V_C_140G-G3*_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..230V (AB500DAB006) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3HP-..230V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..230V_C_50kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 9.6 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..230V (AB500DAB006) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3HP-..230V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..480V_C_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..480V (AB500DAB006) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3HP-..480V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..480V_C_35kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 4.8 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..480V (AB500DAB006) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3HP-..480V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..480V_C_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 4.8 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..480V (AB500DAB006) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3HP-..480V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..600V_C_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..600V_C_18kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 3.9 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..600V_C_14kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 3.9 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_07-..480V_C_65kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..480V (AB500DAB007) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_5HP-..480V (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_07-..480V_C_35kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..480V (AB500DAB007) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_5HP-..480V (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_07-..480V_C_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..480V (AB500DAB007) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_5HP-..480V (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_07-..600V_C_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_07-..600V_C_18kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 6.1 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_07-..600V_C_14kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 6.1 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..200V_C_140G-G6*_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..200V (AB500DAB008) |  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_5HP-..200V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..200V_C_140G-G3*_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..200V (AB500DAB008) |  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_5HP-..200V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..200V_C_50kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 17.5 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..200V (AB500DAB008) |  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_5HP-..200V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..230V_C_140G-G6*_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..230V (AB500DAB008) |  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_5HP-..230V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..230V_C_140G-G63*_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..230V (AB500DAB008) |  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_5HP-..230V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..230V_C_50kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 15.2 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..230V (AB500DAB008) |  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_5HP-..230V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..480V_C_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..480V (AB500DAB008) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_5HP-..480V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..480V_C_35kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..480V (AB500DAB008) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_5HP-..480V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..480V_C_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..480V (AB500DAB008) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_5HP-..480V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..600V_C_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..600V_C_18kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 6.1 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..600V_C _14kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 6.1 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..230V_C_140G-G6*_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..200V (AB500DAB009) |  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_7-1/2HP-..200V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..230V_C_140G-G3*_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..200V (AB500DAB009) |  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_7-1/2HP-..200V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..230V_C_50kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 22 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..200V (AB500DAB009) |  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_7-1/2HP-..200V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..480V_C_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..480V (AB500DAB009) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_7-1/2HP-..480V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..480V_C_35kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 11 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..480V (AB500DAB009) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_7-1/2HP-..480V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..480V_C_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 11 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..480V (AB500DAB009) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_7-1/2HP-..480V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..600V_C_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..600V_C_18kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 9 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..600V_C_14kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 9 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_10-..480V_C_65kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..480V (AB500DAB010) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_10HP-..480V (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_10-..480V_C_35kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..480V (AB500DAB010) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_10HP-..480V (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_10-..480V_C_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..480V (AB500DAB010) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_10HP-..480V (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_10-..600V_C_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_10-..600V_C_18kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 11 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_10-..600V_C_14kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 11 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-C…-EUTC42_11-..200V_C_140G-G6* _65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V (AB500DAB011) |  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..200V_C_140G-G3*_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V (AB500DAB011) |  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..200V_C_50kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*50 | 200 | 3 | 50 | 50 | --- | 200 | 3 | 50 | 32.2 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V (AB500DAB011) |  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..230V_C_140G-G6*_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V (AB500DAB011) |  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..230V_C_140G-G3*_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V (AB500DAB011) |  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..230V_C_50kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*50 | 230 | 3 | 50 | 50 | --- | 230 | 3 | 50 | 28 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V (AB500DAB011) |  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..480V_C_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..480V (AB500DAB011) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_10HP-..480V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..480V_C _35kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..480V (AB500DAB011) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_10HP-..480V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..480V_C_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..480V (AB500DAB011) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_10HP-..480V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..600V_C_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..600V_C_18kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 11 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..600V_C14kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 11 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..230V_C_140G-G6_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..230V (AB500DAB012) |  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_15HP-..230V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..230V_C_140G-G3_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..230V (AB500DAB012) |  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_15HP-..230V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..230V_C_50kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 42 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..230V (AB500DAB012) |  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_15HP-..230V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..480V_C_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..480V (AB500DAB012) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_15HP-..480V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..480V_C_35kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..480V (AB500DAB012) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_15HP-..480V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..480V_C_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..480V (AB500DAB012) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_15HP-..480V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..600V_C_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..600V_C_18kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 18 | 17 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..600V_C_14kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 17 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_13-..480V_C_65kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..480V (AB500DAB013) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_20HP-..480V (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_13-..480V_C_35kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..480V (AB500DAB013) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_20HP-..480V (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_13-..480V_C_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..480V (AB500DAB013) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_20HP-..480V (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_13-..600V_C_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_13-..600V_C_18kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 22 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_13-..600V_C_14kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 22 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_14-..480V_C_65kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..480V (AB500DAB014) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_25HP-..480V (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_14-..480V_C_35kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..480V (AB500DAB014) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_25HP-..480V (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_14-..480V_C_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..480V (AB500DAB014) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_25HP-..480V (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_14-..600V_C_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_14-..600V_C_18kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 27 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_14-..600V_C_14kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 27 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-D…-EUTD42_15-..200V_C_140G-G6*_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V (AB500DAB015) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..200V_C_140G-G3*_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V (AB500DAB015) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..200V_C_50kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 48.3 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V (AB500DAB015) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..230V_C_140G-G6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V (AB500DAB015) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..230V_C_140G-G3_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V (AB500DAB015) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..230V_C_50kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 42 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V (AB500DAB015) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..480V_C_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..480V (AB500DAB015) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_15HP-..480V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..480V_C_35kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..480V (AB500DAB015) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_15HP-..480V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..480V_C_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..480V (AB500DAB015) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_15HP-..480V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..600V_C_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..600V_C_18kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 17 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..600V_C_14kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 17 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..200V_C_140G-H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..200V_C_140G-H3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..200V_C_140G-H2_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..230V_C_140G-H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..230V_C_140G-H3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..230V_C_140G-H2_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..480V_C _65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..480V_C_35kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..480V_C_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..600V_C_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-J6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..600V_C_18kA (AB500DAB016) | C | CB | Allen Bradley | 140G-J3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 22 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..600V_C_14kA (AB500DAB016) | C | CB | Allen Bradley | 140G-J6*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 22 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..200V_C_140G-H6-65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..200V_C_140G-H3-65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..200V_C_140G-H2-65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..230V_C_140G-H6-65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..230V_C_140G-H3-65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..230V_C_140G-H2-65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..480V_C_140G-H6-65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..480V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_25HP-..480V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..480V_C_140G-H3-35kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..480V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_25HP-..480V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..480V_C_140G-H2-25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..480V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_25HP-..480V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..600V_C_140G-J6-25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-J6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..600V_C_140G-J3-18kA (AB500DAB017) | C | CB | Allen Bradley | 140G-J3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 27 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..600V_C_140G-J2-14kA (AB500DAB017) | C | CB | Allen Bradley | 140G-J2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 27 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..230V_C_140G-H6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V (AB500DAB018) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..230V_C_140G-H3_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V (AB500DAB018) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..230V_C_140G-H2_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V (AB500DAB018) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..480V_C_140G-H6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..480V_C_140G-H3_35kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..480V_C_140G-H2_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..600V_C_140G-J6_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..600V_C_140G-J3_18kA (AB500DAB018) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 32 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..600V_C_140G-J2_14kA (AB500DAB018) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 32 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_19-..480V_C_140G-H6_65kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_19-..480V_C_140G-H3_35kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 52 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_19-..480V_C_140G-H2_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 52 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_19-..600V_C_140G-J6_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 41 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_19-..600V_C_140G-J3_18kA (AB500DAB019) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 41 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_19-..600V_C_140G-J2_14kA (AB500DAB019) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 41 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_20-..480V_C_140G-H6_65kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_20-..480V_C_140M-H3_35kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_20-..480V_C_140M-H2_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_20-..600V_C_140M-J6_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_20-..600V_C_140M-J3_18kA (AB500DAB020) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 52 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_20-..600V_C_140M-J2_14kA (AB500DAB020) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 52 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-E…-EUTE42_21-..200V_C_140G-J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..200V_C_140G-J3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..200V_C_140G-J2_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..230V_C_140G-J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..230V_C_140G-J3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..230V_C_140G-J2_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..480V_C_140G-J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..480V_C_140G-J3_35kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..480V_C_140G-I3_35kA (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..480V_C_140G-J2_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..480V_C_140G-I2_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..600V_C_140G-J6_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..600V_C_140G-J3_18kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 32 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..600V_C_140G-J2_14kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 32 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..230V_C_140G-J6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V (AB500DAB022) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..230V_C_140G-J3_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V (AB500DAB022) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..230V_C_140G-J2_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V (AB500DAB022) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..480V_C_140G-J6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..480V_C_140G-J3_35kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..480V_C_140G-I3_35kA (AB500DAB022) | C | CB | Allen Bradley | 140G-I3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..480V_C_140G-J2_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..480V_C_140G-I2_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-I2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..600V_C_140G-J6_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..600V_C_140G-J3_18kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 52 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..600V_C_140G-J2_14kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 52 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..480V_C_140G-J6_65kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..480V_C_140G-J3_35kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..480V_C_140G-I3_35kA (AB500DAB023) | C | CB | Allen Bradley | 140G-I3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..480V_C_140G-J2_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..480V_C_140G-I2_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-I2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..600V_C_140G-J6_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 62 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..600V_C_140G-J3_18kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 62 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..600V_C_140G-J2_14kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 62 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_24-..480V_C_140G-J6-65kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_24-..480V_C_140G-J3-35kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_24-..480V_C_140G-I3-35kA (AB500DAB024) | C | CB | Allen Bradley | 140G-I3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_24-..480V_C_140G-J2-25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_24-..480V_C_140G-I2-25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-I2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_24-..600V_C_140G-J6-25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_24-..600V_C_140G-J3-18kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 77 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_24-..600V_C_140G-J2-14kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 77 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_25-..600V_C_140G-J6_25kA (AB500DAB025) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 99 | 100 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_25-..600V_C_140G-J3_18kA (AB500DAB025) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 99 | 100 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_25-..600V_C_140G-J2_14kA (AB500DAB025) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 99 | 100 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-F…-EUTF42_26-..200V_C_140G-K6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K6*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 200 | 3 | 10 | 221 | 75
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 200 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_26-..200V_C_140G-K3_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K3*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 200 | 3 | 10 | 221 | 75
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 200 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_26-..200V_C_140G-K2_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K2*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 200 | 3 | 10 | 221 | 75
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 200 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_26-..230V_C_140G-K6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_26-..230V_C_140G-K3_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K3*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_26-..230V_C_140G-K2_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K2*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_26-..480V_C_140G-K6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_26-..480V_C_140G-K3_35kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K3*300 | 480 | 3 | 35 | 300 | --- | 480 | 3 | 35 | 96 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_26-..480V_C_140G-K2_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K2*300 | 480 | 3 | 25 | 300 | --- | 480 | 3 | 25 | 96 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_26-..600V_C_140G-J6_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 125 | ---
AB509-F…-EUTF42_26-..600V_C_140G-J3_18kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 77 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 125 | ---
AB509-F…-EUTF42_26-..600V_C_140G-J2_14kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 77 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 125 | ---
AB509-F…-EUTF42_27-..230V_C_140G-K6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_27-..230V_C_140G-K3_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K3*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_27-..230V_C_140G-K2_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K2*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_27-..480V_C_140G-K6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_27-..480V_C_140G-K3_35kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K3*300 | 480 | 3 | 35 | 300 | --- | 480 | 3 | 35 | 124 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_27-..480V_C_140G-K2_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K2*300 | 480 | 3 | 25 | 300 | --- | 480 | 3 | 25 | 124 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_27-..600V_C_140G-J6_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_27-..600V_C_140G-J3_18kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 99 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_27-..600V_C_140G-J2_14kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 99 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_28-..600V_C_140G-J6_25kA (AB500DAB028) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_28-..600V_C_140G-J3_18kA (AB500DAB028) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 192 | 200 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_28-..600V_C_140G-J2_14kA (AB500DAB028) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 192 | 200 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-A…-EUTB42_01-..200V_C_2_140G-H6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..200V_C_2_140G-H3_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..200V_C_2_140G-H2_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..230V_C_2_140G-H6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..230V_C_2_140G-H3_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..230V_C_2_140G-H2_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..480V_C_2_140G-H6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..480V_C_2_140G-H3_35kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.1 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..480V_C_2_140G-H2_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.1 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..200V_C_2_140G-H6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..200V_C_2_140G-H3_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..200V_C_2_140G-H2_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..230V_C_2_140G-H6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..230V_C_2_140G-H3_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..230V_C_2_140G-H2_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..480V_C_2_140G-H6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..480V_C_2_140G-H3_35kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.6 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..480V_C_2_140G-H2_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.6 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..200V_C_2_140G-H6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..200V_C_2_140G-H3_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..200V_C_2_140G-H2_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..230V_C_2_140G-H6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..230V_C_2_140G-H3_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..230V_C_2_140G-H2_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..480V_C_2_140G-H6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..480V_C_2_140G-H3_35kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 2.1 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..480V_C_2_140G-H2_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 2.1 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..200V_C_2_140G-H6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..200V_C_2_140G-H3_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..200V_C_2_140G-H2_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..230V_C_2_140G-H6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..230V_C_2_140G-H3_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..230V_C_2_140G-H2_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..480V_C_2_140G-H6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..480V_C_2_140G-H3_35kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..480V_C_2_140G-H2_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..200V_C_2_140G-H6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..200V_C_2_140G-H3_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..200V_C_2_140G-H2_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..230V_C_2_140G-H6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..230V_C_2_140G-H3_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..230V_C_2_140G-H2_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..480V_C_2_140G-H6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..480V_C_2_140G-H3_35kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3.4 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..480V_C_2_140G-H2_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3.4 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..200V_C_2_140G-H6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..200V_C_2_140G-H3_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..200V_C_2_140G-H2_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..230V_C_2_140G-H6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..230V_C_2_140G-H4_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..230V_C_2_140G-H2_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..480V_C_2_140G-H6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..480V_C_2_140G-H3_35kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 4.8 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..480V_C_2_140G-H2_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 4.8 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_07-..480V_C_2_140G-H6_65kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_07-..480V_C_2_140G-H3_35kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H36*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_07-..480V_C_2_140G-H2_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..200V_C_2_140G-H6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..200V_C_2_140G-H3_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..200V_C_2_140G-H2_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..230V_C_2_140G-H6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..230V_C_2_140G-H3_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..230V_C_2_140G-H2_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..480V_C_2_140G-H6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..480V_C_2_140G-H3_35kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..480V_C_2_140G-H2_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..200V_C_2_140G-H6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 25.3 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..200V_2 (AB500DAB009) |  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_7-1/2HP-..200V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..200V_C_2_140G-H3_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 25.3 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..200V_2 (AB500DAB009) |  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_7-1/2HP-..200V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..200V_C_2_140G-H2_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 25.3 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..200V_2 (AB500DAB009) |  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_7-1/2HP-..200V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..480V_C_2_140G-H6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..480V_C_2_140G-H3_35kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 11 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..480V_C_2_140G-H2_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 11 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_10-..480V_C_2_140G-H6_65kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_10-..480V_C_2_140G-H3_35kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_10-..480V_C_2_140G-H2_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-C…-EUTC42_11-..200V_C_2_140G-H6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..200V_C_2_140G-H3_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..200V_C_2_140G-H2_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..230V_C_2_140G-H6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..230V_C_2_140G-H3_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..230V_C_2_140G-H2_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..480V_C_2_140G-H6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..480V_C_2_140G-H3_35kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..480V_C_2_140G-H2_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..230V_C_2_140G-H6_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..230V_2 (AB500DAB012) |  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_15HP-..230V_2 (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..230V_C_2_140G-H3_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..230V_2 (AB500DAB012) |  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_15HP-..230V_2 (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..230V_C_2_140G-H2_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..230V_2 (AB500DAB012) |  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_15HP-..230V_2 (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..480V_C_2_140G-H6_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..480V_C_2_140G-H3_35kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..480V_C_2_140G-H2_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_13-..480V_C_2_140G-H6_65k (AB500DAB013) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_13-..480V_C_2_140G-H3_35k (AB500DAB013) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_13-..480V_C_2_140G-H2_25k (AB500DAB013) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_14-..480V_C_2_140G-H6_65k (AB500DAB014) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_14-..480V_C_2_140G-H3_35k (AB500DAB014) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_14-..480V_C_2_140G-H2_25k (AB500DAB014) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-D…-EUTD42_15-..200V_C_2_140G-H6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..200V_C_2_140G-H3_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..200V_C_2_140G-H2_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..200V_C_2_140G-I3_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..200V_C_2_140G-I2_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-I2*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..230V_C_2_140G-H6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..230V_C_2_140G-H3_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..230V_C_2_140G-H2_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..230V_C_2_140G-I3_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..230V_C_2_140G-I2_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..480V_C_2_140G-H6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..480V_C_2_140G-H3_35kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 35 | 50
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..480V_C_2_140G-H2_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 25 | 50
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..200V_C_2_140G-H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..200V_C_2_140G-H3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..200V_C_2_140G-H2_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..200V_C_2_140G-I3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..200V_C_2_140G-I2_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-I2*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..230V_C_2_140G-H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..230V_C_2_140G-H3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..230V_C_2_140G-H2_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..230V_C_2_140G-I3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..230V_C_2_140G-I2_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..480V_C_2_140G-H2_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..480V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_20HP-..480V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..200V_C_2_140G-H6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..200V_C_2_140G-H3_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..200V_C_2_140G-H2_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..200V_C_2_140G-I3_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..200V_C_2_140G-I2_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-I2*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..230V_C_2_140G-H6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..230V_C_2_140G-H3_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..230V_C_2_140G-H2_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..230V_C_2_140G-I3_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..230V_C_2_140G-I2_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..480V_C_2_140G-H2_25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..480V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_25HP-..480V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..230V_C_2_140G-H6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..230V_C_2_140G-H3_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..230V_C_2_140G-H2_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..230V_C_2_140G-I3_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..230V_C_2_140G-I2_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..480V_C_2_140G-H6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..480V_C_2_140G-H3_35kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..480V_C_2_140G-H2_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_19-..480V_C_2_140G-H6_65kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_19-..480V_C_2_140G-H3_35kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 52 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_19-..480V_C_2_140G-H2_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 52 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_20-..480V_C_2_140G-H6_65kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_20-..480V_C_2_140G-H3_35kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_20-..480V_C_2_140G-H2_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-E…-EUTE42_21-..200V_C_2_140G-J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..200V_C_2_140G-J3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..200V_C_2_140G-J2_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..200V_C_2_140G-I3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..200V_C_2_140G-I2_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*150 | 200 | 3 | 50 | 150 | --- | 200 | 3 | 50 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..230V_C_2_140G-J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..230V_C_2_140G-J3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..230V_C_2_140G-J2_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..230V_C_2_140G-I3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..230V_C_2_140G-I2_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*125 | 230 | 3 | 50 | 125 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..480V_C_2_140G-J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..480V_C_2_140G-J3_35kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..480V_C_2_140G-I3_35kA (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..480V_C_2_140G-J2_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..480V_C_2_140G-I2_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..230V_C_2_140G-J6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*150 | 230 | 3 | 65 | 150 | --- | 230 | 3 | 65 | 143 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..230V_C_2_140G-J3_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*150 | 230 | 3 | 65 | 150 | --- | 230 | 3 | 65 | 143 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..230V_C_2_140G-J2_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*150 | 230 | 3 | 65 | 150 | --- | 230 | 3 | 65 | 143 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..230V_C_2_140G-I3_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-I3*150 | 230 | 3 | 65 | 150 | --- | 230 | 3 | 65 | 143 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..230V_C_2_140G-I2_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-I2*150 | 230 | 3 | 50 | 150 | --- | 230 | 3 | 50 | 143 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..480V_C_2_140G-J6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..480V_C_2_140G-J3_35kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..480V_C_2_140G-I3_35kA (AB500DAB022) | C | CB | Allen Bradley | 140G-I3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..480V_C_2_140G-J2_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..480V_C_2_140G-I2_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-I2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..480V_C_2_140G-J6_65kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..480V_C_2_140G-J3_35kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..480V_C_2_140G-I3_35kA (AB500DAB023) | C | CB | Allen Bradley | 140G-I3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..480V_C_2_140G-J2_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..480V_C_2_140G-I2_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-I2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_24-..480V_C_2_140G-J6_65kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_24-..480V_C_2_140G-J3_35kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_24-..480V_C_2_140G-I3_35kA (AB500DAB024) | C | CB | Allen Bradley | 140G-I3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_24-..480V_C_2_140G-J2_25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_24-..480V_C_2_140G-I2_25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-I2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-F…-EUTF42_26-..600V_C_2_140G-J6_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_26-..600V_C_2_140G-J3_18kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 77 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_26-..600V_C_2_140G-J2_14kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 77 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_27-..600V_C_2_140G-J6_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_27-..600V_C_2_140G-J3_18kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 99 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_27-..600V_C_2_140G-J2_14kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 99 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_29-..600V_C_2_140G-J6_25kA (AB500DAB029) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_29-..600V_C_2_140G-J3_18kA (AB500DAB029) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 192 | 200 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_29-..600V_C_2_140G-J2_14kA (AB500DAB029) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 192 | 200 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-D…-EUTD42_30-..230V_C_2_140G-J6_65kA (AB500DAB030) | C | CB | Allen Bradley | 140G-J6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_30-..230V_C_2_140G-J3_65kA (AB500DAB030) | C | CB | Allen Bradley | 140G-J3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_30-..230V_C_2_140G-J3_65kA (AB500DAB030) | C | CB | Allen Bradley | 140G-J2*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_30-..230V_C_2_140G-I3_65kA (AB500DAB030) | C | CB | Allen Bradley | 140G-I3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_30-..230V_C_2_140G-I3_65kA (AB500DAB030) | C | CB | Allen Bradley | 140G-I2*125 | 230 | 3 | 50 | 125 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-E…-EUTE42_31-..230V_C_2_140G-J6_65kA (AB500DAB031) | C | CB | Allen Bradley | 140G-J6*-175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB031) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB031) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_31-..230V_C_2_140G-J3_65kA (AB500DAB031) | C | CB | Allen Bradley | 140G-J3*-175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB031) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB031) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_31-..230V_C_2_140G-J2_65kA (AB500DAB031) | C | CB | Allen Bradley | 140G-J2*-175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB031) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB031) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-A…-EUTB42_01-..600V_C_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..600V_C_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..600V_C_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..600V_C _25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..600V_C_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..600V_C_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_07-..600V_C_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..600V_C_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..600V_C_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_10-..600V_C_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-C…-EUTC42_11-..600V_C_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..600V_C_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_13-..600V_C_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_14-..600V_C_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-D…-EUTD42_15-..600V_C_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..200V_C_140G-HC6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..230V_C_140G-HC6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..230V_C_140G-_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..230V_C_140G-_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..480V_C _65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..600V_C_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-JC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..200V_C_140G-HC6-65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..230V_C_140G-HC6-65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..600V_C_140G-JC6-25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-JC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..230V_C_140G-HC6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V (AB500DAB018) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..480V_C_140G-HC6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..600V_C_140G-JC6_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_19-..480V_C_140G-HC6_65kA (AB500DAB019) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_19-..600V_C_140G-JC6_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 41 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_20-..480V_C_140G-HC6_65kA (AB500DAB020) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_20-..600V_C_140M-JC6_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-E…-EUTE42_21-..200V_C_140G-JC6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..230V_C_140G-JC6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..480V_C_140G-JC6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..600V_C_140G-JC6_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..230V_C_140G-JC6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V (AB500DAB022) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..480V_C_140G-JC6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..600V_C_140G-JC6_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..480V_C_140G-JC6_65kA (AB500DAB023) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..600V_C_140G-JC6_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 62 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_24-..480V_C_140G-JC6-65kA (AB500DAB024) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_24-..600V_C_140G-JC6-25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_25-..600V_C_140G-JC6_25kA (AB500DAB025) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 99 | 100 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-F…-EUTF42_26-..200V_C_140G-KC6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-KC6*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 200 | 3 | 10 | 221 | 75
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 200 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_26-..230V_C_140G-KC6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-KC6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_26-..480V_C_140G-KC6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-KC6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_26-..600V_C_140G-JC6_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 125 | ---
AB509-F…-EUTF42_27-..230V_C_140G-KC6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-KC6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_27-..480V_C_140G-KC6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-KC6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_27-..600V_C_140G-JC6_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_28-..600V_C_140G-JC6_25kA (AB500DAB028) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-A…-EUTB42_01-..200V_C_2_140G-HC6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..230V_C_2_140G-HC6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..480V_C_2_140G-HC6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..200V_C_2_140G-HC6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..230V_C_2_140G-HC6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..480V_C_2_140G-HC6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..200V_C_2_140G-HC6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..230V_C_2_140G-HC6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..480V_C_2_140G-HC6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..200V_C_2_140G-HC6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..230V_C_2_140G-HC6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..480V_C_2_140G-HC6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..200V_C_2_140G-HC6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..230V_C_2_140G-HC6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..480V_C_2_140G-HC6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..200V_C_2_140G-HC6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..230V_C_2_140G-HC6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..480V_C_2_140G-HC6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_07-..480V_C_2_140G-HC6_65kA (AB500DAB007) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..200V_C_2_140G-HC6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..230V_C_2_140G-HC6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..480V_C_2_140G-HC6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..200V_C_2_140G-HC6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 25.3 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..200V_2 (AB500DAB009) |  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_7-1/2HP-..200V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..480V_C_2_140G-HC6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_10-..480V_C_2_140G-HC6_65kA (AB500DAB010) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-C…-EUTC42_11-..200V_C_2_140G-HC6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..230V_C_2_140G-HC6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..480V_C_2_140G-HC6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..230V_C_2_140G-HC6_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..230V_2 (AB500DAB012) |  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_15HP-..230V_2 (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..480V_C_2_140G-HC6_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_13-..480V_C_2_140G-HC6_65k (AB500DAB013) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_14-..480V_C_2_140G-HC6_65k (AB500DAB014) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 3, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-D…-EUTD42_15-..200V_C_2_140G-HC6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..230V_C_2_140G-HC6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..480V_C_2_140G-HC6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..200V_C_2_140G-HC6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..230V_C_2_140G-HC6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..480V_C_2_140G-HC6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..480V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_20HP-..480V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..200V_C_2_140G-HC6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..230V_C_2_140G-HC6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..480V_C_2_140G-HC6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..480V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_25HP-..480V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..230V_C_2_140G-HC6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..480V_C_2_140G-HC6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_19-..480V_C_2_140G-HC6_65kA (AB500DAB019) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_20-..480V_C_2_140G-HC6_65kA (AB500DAB020) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-E…-EUTE42_21-..200V_C_2_140G-JC6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..230V_C_2_140G-JC6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..480V_C_2_140G-JC6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..230V_C_2_140G-JC6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*150 | 230 | 3 | 65 | 150 | --- | 230 | 3 | 65 | 143 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..480V_C_2_140G-JC6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..480V_C_2_140G-JC6_65kA (AB500DAB023) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_24-..480V_C_2_140G-JC6_65kA (AB500DAB024) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V_2 (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-F…-EUTF42_26-..600V_C_2_140G-JC6_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_27-..600V_C_2_140G-JC6_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_29-..600V_C_2_140G-JC6_25kA (AB500DAB029) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 3, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-D…-EUTD42_30-..230V_C_2_140G-JC6_65kA (AB500DAB030) | C | CB | Allen Bradley | 140G-JC6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB030) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-E…-EUTE42_31-..230V_C_2_140G-JC6_65kA (AB500DAB031) | C | CB | Allen Bradley | 140G-JC6*-175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 3, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB031) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_50HP-..230V_2 (AB500DAB031) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
Size 0-4; use Table 152 for W elements and Table 163 for J elements; Size 5 use Table 347 for W elements and Table 547 for J elements
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(7) = See Table 7 for minimum internal power wiring.
Table 7 - Minimum Internal Power Wiring
1/32in. thick thermoplastic insulation, rated 105C
Wire Code |  | Wire Size
7a |  | 10 AWG
7b |  | 10 AWG
7c |  | 8 AWG
7d |  | 4 AWG
7e |  | 1AWG
7f |  | 250 MCM

## 509 C E1+
[16 empty] | Issued: | 2015-12-31
[16 empty] | Last Revised: | 2017-10-10
ID Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage | Number of Phases | SCCR, kA | Full Load Current, A | HP rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP Rating | Enclosure Volume, Cu Ft
AB509-A…-E1+EEEC_01-..200V_C_140G_G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_01-..200V_C_140G_G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_01-..200V_C_140G-G2_50kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 2.5 | 0.5 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_01-..230V_C_140G_G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_01-..230V_C_140G-G3_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_01-..230V_C_140-G2_50kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 2.2 | 0.5 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_01-..480V_C_140G_G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_01-..480V_C_140G-G3_35kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_01-..480V_C_140-G2_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.1 | 0.5 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_01-..600V_C_140G_H6_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEBC | 600 | 3 | 5 | 0.2-1 | ---
AB509-A…-E1+EEEC_01-..600V_C_140G-H3_18kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEBC | 600 | 3 | 5 | 0.2-1 | ---
AB509-A…-E1+EEEC_01-..600V_C_140G-H2_14kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEBC | 600 | 3 | 5 | 0.2-1 | ---
AB509-A…-E1+EEEC_02-..200V_C_140G_G6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_02-..200V_C_140G-G3_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_02-..200V_C_140-G2_50kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 3.7 | 0.75 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_02-..230V_C_140G_G6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_02-..230V_C_140G-G3_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_02-..230V_C_140-G2_50kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 3.2 | 0.75 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_02-..480V_C_140G_G6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_02-..480V_C_140G-G3_35kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_02-..480V_C_140-G2_25kA (AB500DAB002) | C | x | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.6 | 0.75 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_02-..600V_C_140G_H6_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_02-..600V_C_140G-H3_18kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_02-..600V_C_140G-H2_14kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_03-..200V_C_140G_G6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_03-..200V_C_140G-G3_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_03-..200V_C_140-G2_50kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 4.8 | 1 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_03-..230V_C_140G_G6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_03-..230V_C_140G-G3_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_03-..230V_C_140-G2_50kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 4.2 | 1 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_03-..480V_C_140G_G6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_03-..480V_C_140G-G3_35kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_03-..480V_C_140-G2_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 2.1 | 1 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_03-..600V_C_140G_H6_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_03-..600V_C_140G-H3_18kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_03-..600V_C_140G-H2_14kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E04+EEEC_04-04/2HP-..200V_C_140G_G6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E04+EEEC_04-04/2HP-..200V_C_140G-G3_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E04+EEEC_04-04/2HP-..200V_C_140-G2_50kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 6.9 | 1.5 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E04+EEEC_04-04/2HP-..230V_C_140G_G6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E04+EEEC_04-04/2HP-..230V_C_140G-G3_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E04+EEEC_04-04/2HP-..230V_C_140-G2_50kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6 | 1.5 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E04+EEEC_04-04/2HP-..480V_C_140G_G6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E04+EEEC_04-04/2HP-..480V_C_140G-G3_35kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E04+EEEC_04-04/2HP-..480V_C_140-G2_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3 | 1.5 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E04+EEEC_04-04/2HP-..600V_C_140G_H6_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E04+EEEC_04-04/2HP-..600V_C_140G-H3_18kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E04+EEEC_04-04/2HP-..600V_C_140G-H2_14kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_05-..200V_C_140G_G6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_05-..200V_C_140G-G3_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_05-..200V_C_140-G2_50kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 7.8 | 2 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_05-..230V_C_140G_G6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_05-..230V_C_140G-G3_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_05-..230V_C_140-G2_50kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6.8 | 2 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_05-..480V_C_140G_G6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_05-..480V_C_140G-G3_35kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_05-..480V_C_140-G2_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3.4 | 2 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_05-..600V_C_140G_H6_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_05-..600V_C_140G-H3_18kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_05-..600V_C_140G-H2_14kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_06-..200V_C_140G_G6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_06-..200V_C_140G-G3_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_06-..200V_C_140-G2_50kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 11 | 3 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_06-..230V_C_140G_G6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_06-..230V_C_140G-G3_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_06-..230V_C_140-G2_50kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 9.6 | 3 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_06-..480V_C_140G_G6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_06-..480V_C_140G-G3_35kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_06-..480V_C_140-G2_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 4.8 | 3 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_06-..600V_C_140G_H6_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_06-..600V_C_140G-H3_18kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_06-..600V_C_140G-H2_14kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_07-..480V_C_140G_G6_65kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_07-..480V_C_140G-G3_35kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_07-..480V_C_140-G2_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.14 | 1, 7a | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_07-..600V_C_140G_H6_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_07-..600V_C_140G-H3_18kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_07-..600V_C_140G-H2_14kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_08-..200V_C_140G_G6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 200 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_08-..200V_C_140G-G3_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 200 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_08-..200V_C_140-G2_50kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 17.5 | 5 | 1.14 | 1, 7b | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 14.3 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 200 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_08-..230V_C_140G_G6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_08-..230V_C_140G-G3_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_08-..230V_C_140-G2_50kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 15.2 | 5 | 1.14 | 1, 7b | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_08-..480V_C_140G_G6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_08-..480V_C_140G-G3_35kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_08-..480V_C_140-G2_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.14 | 1, 7b | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_08-..600V_C_140G_H6_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_08-..600V_C_140G-H3_18kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_08-..600V_C_140G-H2_14kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_09-1/2HP-..230V_C_140G_G6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_09-1/2HP-..230V_C_140G-G3_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_09-1/2HP-..230V_C_140-G2_50kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 22 | 7.5 | 1.14 | 1, 7b | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_09-1/2HP-..480V_C_140G_G6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_09-1/2HP-..480V_C_140G-G3_35kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_09-1/2HP-..480V_C_140-G2_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 11 | 7.5 | 1.14 | 1, 7b | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_09-1/2HP-..600V_C_140G_H6_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_09-1/2HP-..600V_C_140G-H3_18kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_09-1/2HP-..600V_C_140G-H2_14kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_10-..480V_C_140G_G6_65kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_10-..480V_C_140G-G3_35kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_10-..480V_C_140-G2_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.14 | 1, 7b | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_10-..600V_C_140G_H6_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_10-..600V_C_140G-H3_18kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_10-..600V_C_140G-H2_14kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-C…-E1+EEFC_11-..200V_C_140G_G6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..200V_C_140G-G3_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..200V_C_140-G2_50kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*50 | 200 | 3 | 50 | 50 | --- | 200 | 3 | 50 | 32.2 | 10 | 1.14 | 1, 7c | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..230V_C_140G_G6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..230V_C_140G-G3_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..230V_C_140-G2_50kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*50 | 230 | 3 | 50 | 50 | --- | 230 | 3 | 50 | 28 | 10 | 1.14 | 1, 7c | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..480V_C_140G_G6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-C…-E1+EEFC_11-..480V_C_140G-G3_35kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-C…-E1+EEFC_11-..480V_C_140-G2_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.14 | 1, 7c | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 14
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-C…-E1+EEFC_11-..600V_C_140G_H6_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-C…-E1+EEFC_11-..600V_C_140G-H3_18kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-C…-E1+EEFC_11-..600V_C_140G-H2_14kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-C…-E1+EEFC_12-..480V_C_140G_G6_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_12-..480V_C_140G-G3_35kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_12-..480V_C_140-G2_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 1.14 | 1, 7c | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 14
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_12-..600V_C_140G_H6_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_12-..600V_C_140G-H3_18kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_12-..600V_C_140G-H2_14kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_13-..480V_C_140G_G6_65kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_13-..480V_C_140G-G3_35kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_13-..480V_C_140-G2_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 1.14 | 1, 7c | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 14
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_13-..600V_C_140G_H6_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_13-..600V_C_140G-H3_18kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_13-..600V_C_140G-H2_14kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_14-..480V_C_140G_G6_65kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEFC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_14-..480V_C_140G-G3_35kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEFC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_14-..480V_C_140-G2_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 14 | 1.14 | 1, 7c | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 14
|  | OLR | Allen Bradley | 592-EEFC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_14-..600V_C_140G_H6_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_14-..600V_C_140G-H3_18kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_14-..600V_C_140G-H2_14kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB509-D…-E1+EEGD_15-..200V_C_140G_G6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..200V_C_140G-G3_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..200V_C_140-G2_50kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 48.3 | 15 | 3.47 | 1, 7d | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 14
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..230V_C_140G_G6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..230V_C_140G-G3_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..230V_C_140-G2_50kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 42 | 15 | 3.47 | 1, 7d | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..480V_C_140G_G6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_15-..480V_C_140G-G3_35kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_15-..480V_C_140-G2_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 3.47 | 1, 7d | E114316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_15-..600V_C_140G_H6_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_15-..600V_C_140G-H3_18kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 17 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_15-..600V_C_140G-H2_14kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 17 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_16-..200V_C_140G_H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..200V_C_140G-H3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..200V_C_140G-H2_50kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..230V_C_140G_H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..230V_C_140G-H3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..230V_C_140G-H2_50kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..480V_C_140G_H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_16-..480V_C_140G-H3_35kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_16-..480V_C_140G-H2_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_16-..600V_C_140G_J6_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-J6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_16-..600V_C_140G-J3_18kA (AB500DAB016) | C | CB | Allen Bradley | 140G-J3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 22 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_16-..600V_C_140G-J2_14kA (AB500DAB016) | C | CB | Allen Bradley | 140G-J2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 22 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_17-..200V_C_140G_H6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..200V_C_140G-H3_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..200V_C_140G-H2_50kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..230V_C_140G_H6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..230V_C_140G-H3_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..230V_C_140G-H2_50kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..480V_C_140G_H6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_17-..480V_C_140G-H3_35kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_17-..480V_C_140G-H2_25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_17-..600V_C_140G_J6_25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-J6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_17-..600V_C_140G-J3_18kA (AB500DAB017) | C | CB | Allen Bradley | 140G-J3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 27 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_17-..600V_C_140G-J2_14kA (AB500DAB017) | C | CB | Allen Bradley | 140G-J2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 27 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_18-..230V_C_140G_H6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_18-..230V_C_140G-H3_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_18-..230V_C_140G-H2_50kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_18-..480V_C_140G_H6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_18-..480V_C_140G-H3_35kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_18-..480V_C_140G-H2_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_18-..600V_C_140G_J6_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_18-..600V_C_140G-J3_18kA (AB500DAB018) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 32 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_18-..600V_C_140G-J2_14kA (AB500DAB018) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 32 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_19-..480V_C_140G_H6_65kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_19-..480V_C_140G-H3_35kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_19-..480V_C_140G-H2_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_19-..600V_C_140G_J6_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 41 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_19-..600V_C_140G-J3_18kA (AB500DAB019) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 41 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_19-..600V_C_140G-J2_14kA (AB500DAB019) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 41 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_20-..480V_C_140G_H6_65kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_20-..480V_C_140G-H3_35kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_20-..480V_C_140G-H2_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_20-..600V_C_140G_J6_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEGD | 600 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_20-..600V_C_140G-J3_18kA (AB500DAB020) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 52 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEGD | 600 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_20-..600V_C_140G-J2_14kA (AB500DAB020) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 52 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEGD | 600 | 3 | 5 | 18-90 | ---
AB509-E…-E1+EEHE_21-..200V_C_140G_J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..200V_C_140G-J3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..200V_C_140G-J2_50kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*150 | 200 | 3 | 50 | 150 | --- | 200 | 3 | 50 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..230V_C_140G_J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..230V_C_140G-J3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..230V_C_140G-J2_50kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*125 | 230 | 3 | 50 | 125 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..480V_C_140G_J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..480V_C_140G-J3_35kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..480V_C_140G-J2_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..600V_C_140G_J6_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..600V_C_140G-J3_18kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 32 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..600V_C_140G-J2_14kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 32 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..230V_C_140G_J6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..230V_C_140G-J3_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..230V_C_140G-J2_50kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*175 | 230 | 3 | 50 | 175 | --- | 230 | 3 | 50 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..480V_C_140G_J6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..480V_C_140G-J3_35kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..480V_C_140G-J2_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..600V_C_140G_J6_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..600V_C_140G-J3_18kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 52 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..600V_C_140G-J2_14kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 52 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..480V_C_140G_J6_65kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..480V_C_140G-J3_35kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..480V_C_140G-J2_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..600V_C_140G_J6_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 62 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..600V_C_140G-J3_18kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 62 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..600V_C_140G-J2_14kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 62 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..480V_C_140G_J6_65kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..480V_C_140G-J3_35kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..480V_C_140G-J2_25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..600V_C_140G_J6_25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..600V_C_140G-J3_18kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 77 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..600V_C_140G-J2_14kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 77 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_25-..600V_C_140G_J6_25kA (AB500DAB025) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 99 | 100 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_25-..600V_C_140G-J3_18kA (AB500DAB025) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 99 | 100 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_25-..600V_C_140G-J2_14kA (AB500DAB025) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 99 | 100 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-F…-E1+EEKF_26-..200V_C_140G_G6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K6*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EEKF | 200 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..200V_C_140G-K3_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K3*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EEKF | 200 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..200V_C_140G-K2_50kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K2*400 | 200 | 3 | 50 | 400 | --- | 200 | 3 | 50 | 221 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EEKF | 200 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..230V_C_140G_G6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EEKF | 230 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..230V_C_140G-K3_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K3*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EEKF | 230 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..230V_C_140G-K2_50kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K2*400 | 230 | 3 | 50 | 400 | --- | 230 | 3 | 50 | 192 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EEKF | 230 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..480V_C_140G_G6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..480V_C_140G-K3_35kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K3*300 | 480 | 3 | 35 | 300 | --- | 480 | 3 | 35 | 96 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..480V_C_140G-K2_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K2*300 | 480 | 3 | 25 | 300 | --- | 480 | 3 | 25 | 96 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..600V_C_140G_J6_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..600V_C_140G-J3_18kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..600V_C_140G-J2_14kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..230V_C_140G_G6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EEKF | 230 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..230V_C_140G-K3_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K3*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EEKF | 230 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..230V_C_140G-K2_50kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K2*400 | 230 | 3 | 50 | 400 | --- | 230 | 3 | 50 | 248 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EEKF | 230 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..480V_C_140G_G6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..480V_C_140G-K3_35kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K3*300 | 480 | 3 | 35 | 300 | --- | 480 | 3 | 35 | 124 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..480V_C_140G-K2_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K2*300 | 480 | 3 | 25 | 300 | --- | 480 | 3 | 25 | 124 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..600V_C_140G_J6_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..600V_C_140G-J3_18kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..600V_C_140G-J2_14kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_28-..600V_C_140G_J6_25kA (AB500DAB028) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_28-..600V_C_140G-J3_18kA (AB500DAB028) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_28-..600V_C_140G-J2_14kA (AB500DAB028) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-A…-E1+EEEC_01-..200V_C_140G_H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_01-..200V_C_140G-H3_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_01-..200V_C_140G-H2_50kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_01-..230V_C_140G_H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_01-..230V_C_140G-H3_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_01-..230V_C_140G-H2_50kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_01-..480V_C_140G_H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_01-..480V_C_140G-H3_35kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_01-..480V_C_140G-H2_25kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_02-..200V_C_140G_H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_02-..200V_C_140G-H3_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_02-..200V_C_140G-H2_50kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_02-..230V_C_140G_H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_02-..230V_C_140G-H3_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_02-..230V_C_140G-H2_50kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_02-..480V_C_140G_H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_02-..480V_C_140G-H3_35kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_02-..480V_C_140G-H2_25kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_03-..200V_C_140G_H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_03-..200V_C_140G-H3_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_03-..200V_C_140G-H2_50kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_03-..230V_C_140G_H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_03-..230V_C_140G-H3_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_03-..230V_C_140G-H2_50kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_03-..480V_C_140G_H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_03-..480V_C_140G-H3_35kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_03-..480V_C_140G-H2_25kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E04+EEEC_04-04/2HP-..200V_C_140G_H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E04+EEEC_04-04/2HP-..200V_C_140G-H3_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E04+EEEC_04-04/2HP-..200V_C_140G-H2_50kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E04+EEEC_04-04/2HP-..230V_C_140G_H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E04+EEEC_04-04/2HP-..230V_C_140G-H3_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E04+EEEC_04-04/2HP-..230V_C_140G-H2_50kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E04+EEEC_04-04/2HP-..480V_C_140G_H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E04+EEEC_04-04/2HP-..480V_C_140G-H3_35kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E04+EEEC_04-04/2HP-..480V_C_140G-H2_25kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_05-..200V_C_140G_H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_05-..200V_C_140G-H3_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_05-..200V_C_140G-H2_50kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_05-..230V_C_140G_H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_05-..230V_C_140G-H3_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_05-..230V_C_140G-H2_50kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_05-..480V_C_140G_H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_05-..480V_C_140G-H3_35kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_05-..480V_C_140G-H2_25kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_06-..200V_C_140G_H6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_06-..200V_C_140G-H3_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_06-..200V_C_140G-H2_50kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_06-..230V_C_140G_H6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_06-..230V_C_140G-H3_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_06-..230V_C_140G-H2_50kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_06-..480V_C_140G_H6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_06-..480V_C_140G-H3_35kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_06-..480V_C_140G-H2_25kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_07-..480V_C_140G_H6_65kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_07-..480V_C_140G-H3_35kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_07-..480V_C_140G-H2_25kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_08-..200V_C_140G_H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 200 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_08-..200V_C_140G-H3_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 200 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_08-..200V_C_140G-H2_50kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 200 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_08-..230V_C_140G_H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_08-..230V_C_140G-H3_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_08-..230V_C_140G-H2_50kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_08-..480V_C_140G_H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_08-..480V_C_140G-H3_35kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_08-..480V_C_140G-H2_25kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_09-1/2HP-..230V_C_140G_H6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_09-1/2HP-..230V_C_140G-H3_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_09-1/2HP-..230V_C_140G-H2_50kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_09-1/2HP-..480V_C_140G_H6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_09-1/2HP-..480V_C_140G-H3_35kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_09-1/2HP-..480V_C_140G-H2_25kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_10-..480V_C_140G_H6_65kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_10-..480V_C_140G-H3_35kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_10-..480V_C_140G-H2_25kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_11-..200V_C_140G_H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..200V_C_140G-H3_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..200V_C_140G-H2_50kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*50 | 200 | 3 | 50 | 50 | --- | 200 | 3 | 50 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..230V_C_140G_H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..230V_C_140G-H3_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..230V_C_140G-H2_50kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*50 | 230 | 3 | 50 | 50 | --- | 230 | 3 | 50 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..480V_C_140G_H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_11-..480V_C_140G-H3_35kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_11-..480V_C_140G-H2_25kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_12-..480V_C_140G_H6_65kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_12-..480V_C_140G-H3_35kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_12-..480V_C_140G-H2_25kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_13-..480V_C_140G_H6_65kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_13-..480V_C_140G-H3_35kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_13-..480V_C_140G-H2_25kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_14-..480V_C_140G_H6_65kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEFC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_14-..480V_C_140G-H3_35kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEFC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_14-..480V_C_140G-H2_25kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEFC | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_15-..200V_C_140G_H6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..200V_C_140G-H3_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..200V_C_140G-H2_50kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..200V_C_140G-I3_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..200V_C_140G-I2_50kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-I2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..230V_C_140G_H6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..230V_C_140G-H3_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..230V_C_140G-H2_50kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..230V_C_140G-I3_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..230V_C_140G-I2_50kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..480V_C_140G_H6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_15-..480V_C_140G-H3_35kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_15-..480V_C_140G-H2_25kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_16-..200V_C_140G_H6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..200V_C_140G-H3_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..200V_C_140G-H2_50kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..200V_C_140G-I3_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..200V_C_140G-I2_50kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-I2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..230V_C_140G_H6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..230V_C_140G-H3_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..230V_C_140G-H2_50kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..230V_C_140G-I3_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..230V_C_140G-I2_50kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..480V_C_140G_H6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_16-..480V_C_140G-H3_35kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_16-..480V_C_140G-H2_25kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_17-..200V_C_140G_H6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..200V_C_140G-H3_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..200V_C_140G-H2_50kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..200V_C_140G-I3_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..200V_C_140G-I2_50kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-I2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..230V_C_140G_H6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..230V_C_140G-H3_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..230V_C_140G-H2_50kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..230V_C_140G-I3_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..230V_C_140G-I2_50kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..480V_C_140G_H6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_17-..480V_C_140G-H3_35kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_17-..480V_C_140G-H2_25kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_18-..230V_C_140G_H6_65kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_18-..230V_C_140G-H3_65kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_18-..230V_C_140G-H2_50kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_18-..230V_C_140G-I3_65kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_18-..230V_C_140G-I2_50kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_18-..480V_C_140G_H6_65kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_18-..480V_C_140G-H3_35kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_18-..480V_C_140G-H2_25kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_19-..480V_C_140G_H6_65kA_2 (AB500DAB019) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_19-..480V_C_140G-H3_35kA_2 (AB500DAB019) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_19-..480V_C_140G-H2_25kA_2 (AB500DAB019) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_20-..480V_C_140G_H6_65kA_2 (AB500DAB020) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_20-..480V_C_140G-H3_35kA_2 (AB500DAB020) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_20-..480V_C_140G-H2_25kA_2 (AB500DAB020) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-E…-E1+EEHE_21-..200V_C_140G_J6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..200V_C_140G-J3_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..200V_C_140G-J2_50kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*150 | 200 | 3 | 50 | 150 | --- | 200 | 3 | 50 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..200V_C_140G-I3_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..200V_C_140G-I2_50kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*150 | 200 | 3 | 50 | 150 | --- | 200 | 3 | 50 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..230V_C_140G_J6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..230V_C_140G-J3_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..230V_C_140G-J2_50kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*125 | 230 | 3 | 50 | 125 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..230V_C_140G-I3_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..230V_C_140G-I2_50kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*125 | 230 | 3 | 50 | 125 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..480V_C_140G_J6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..480V_C_140G-J3_35kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..480V_C_140G-J2_25kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..480V_C_140G-I3_35kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..480V_C_140G-I2_25kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..230V_C_140G_J6_65kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..230V_C_140G-J3_65kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..230V_C_140G-J2_50kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*175 | 230 | 3 | 50 | 175 | --- | 230 | 3 | 50 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..480V_C_140G_J6_65kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..480V_C_140G-J3_35kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..480V_C_140G-J2_25kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..480V_C_140G-I3_35kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-I3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..480V_C_140G-I2_25kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-I2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..480V_C_140G_J6_65kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..480V_C_140G-J3_35kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..480V_C_140G-J2_25kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..480V_C_140G-I3_35kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-I3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..480V_C_140G-I2_25kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-I2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..480V_C_140G_J6_65kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..480V_C_140G-J3_35kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..480V_C_140G-J2_25kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..480V_C_140G-I3_35kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-I3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..480V_C_140G-I2_25kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-I2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-F…-E1+EEKF_26-..600V_C_140G_J6_25kA_2 (AB500DAB026) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..600V_C_140G-J3_18kA_2 (AB500DAB026) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..600V_C_140G-J2_14kA_2 (AB500DAB026) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..600V_C_140G_J6_25kA_2 (AB500DAB027) | C | CB | Allen Bradley | 140G-J6*200 | 600 | 3 | 25 | 200 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..600V_C_140G-J3_18kA_2 (AB500DAB027) | C | CB | Allen Bradley | 140G-J3*200 | 600 | 3 | 18 | 200 | --- | 600 | 3 | 18 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..600V_C_140G-J2_14kA_2 (AB500DAB027) | C | CB | Allen Bradley | 140G-J2*200 | 600 | 3 | 14 | 200 | --- | 600 | 3 | 14 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_28-..600V_C_140G_J6_25kA_2 (AB500DAB028) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_28-..600V_C_140G-J3_18kA_2 (AB500DAB028) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_28-..600V_C_140G-J2_14kA_2 (AB500DAB028) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-D…-E1+EEGD_30-..230V_C_140G_J6_65kA_2 (AB500DAB030) | C | CB | Allen Bradley | 140G-J6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_30-..230V_C_140G-J3_65kA_2 (AB500DAB030) | C | CB | Allen Bradley | 140G-J3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_30-..230V_C_140G-J2_50kA_2 (AB500DAB030) | C | CB | Allen Bradley | 140G-J2*125 | 230 | 3 | 50 | 125 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-E…-E1+EEHE_31-..230V_C_140G_J6_65kA_2 (AB500DAB031) | C | CB | Allen Bradley | 140G-J6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_31-..230V_C_140G-J3_65kA_2 (AB500DAB031) | C | CB | Allen Bradley | 140G-J3*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_31-..230V_C_140G-J2_50kA_2 (AB500DAB031) | C | CB | Allen Bradley | 140G-J2*175 | 230 | 3 | 50 | 175 | --- | 230 | 3 | 50 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-A…-E1+EEEC_01-..600V_C_140G_6_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEBC | 600 | 3 | 5 | 0.2-1 | ---
AB509-A…-E1+EEEC_02-..600V_C_140G_6_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_03-..600V_C_140G_6_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E04+EEEC_04-04/2HP-..600V_C_140G_6_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_05-..600V_C_140G_6_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_06-..600V_C_140G_6_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_07-..600V_C_140G_6_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_08-..600V_C_140G_6_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_09-1/2HP-..600V_C_140G_6_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_10-..600V_C_140G_6_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-C…-E1+EEFC_11-..600V_C_140G_6_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-C…-E1+EEFC_12-..480V_C_140G_G6_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_12-..600V_C_140G_6_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_13-..600V_C_140G_6_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_14-..600V_C_140G_6_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB509-D…-E1+EEGD_15-..600V_C_140G_6_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_16-..200V_C_140G_6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..230V_C_140G_6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..480V_C_140G_6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_16-..600V_C_140G_6_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-JC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_17-..200V_C_140G_6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..230V_C_140G_6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..480V_C_140G_6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_17-..600V_C_140G_6_25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-JC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_18-..230V_C_140G_6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_18-..480V_C_140G_6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_18-..600V_C_140G_6_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_19-..480V_C_140G_6_65kA (AB500DAB019) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_19-..600V_C_140G_6_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 41 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_20-..480V_C_140G_6_65kA (AB500DAB020) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_20-..600V_C_140G_6_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEGD | 600 | 3 | 5 | 18-90 | ---
AB509-E…-E1+EEHE_21-..200V_C_140G_6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..230V_C_140G_6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..480V_C_140G_6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..600V_C_140G_6_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..230V_C_140G_6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..480V_C_140G_6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..600V_C_140G_6_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..480V_C_140G_6_65kA (AB500DAB023) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..600V_C_140G_6_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 62 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..480V_C_140G_6_65kA (AB500DAB024) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..600V_C_140G_6_25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_25-..600V_C_140G_6_25kA (AB500DAB025) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 99 | 100 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-F…-E1+EEKF_26-..200V_C_140G_G6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-KC6*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EEKF | 200 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..230V_C_140G_G6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-KC6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EEKF | 230 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..480V_C_140G_G6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-KC6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..600V_C_140G_6_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..230V_C_140G_G6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-KC6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EEKF | 230 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..480V_C_140G_G6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-KC6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..600V_C_140G_6_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_28-..600V_C_140G_6_25kA (AB500DAB028) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-A…-E1+EEEC_01-..200V_C_140G_6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_01-..230V_C_140G_6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_01-..480V_C_140G_6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_02-..200V_C_140G_6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_02-..230V_C_140G_6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_02-..480V_C_140G_6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_03-..200V_C_140G_6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_03-..230V_C_140G_6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_03-..480V_C_140G_6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E04+EEEC_04-04/2HP-..200V_C_140G_6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E04+EEEC_04-04/2HP-..230V_C_140G_6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E04+EEEC_04-04/2HP-..480V_C_140G_6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_05-..200V_C_140G_6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_05-..230V_C_140G_6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_05-..480V_C_140G_6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_06-..200V_C_140G_6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_06-..230V_C_140G_6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_06-..480V_C_140G_6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_07-..480V_C_140G_6_65kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_08-..200V_C_140G_6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 200 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_08-..230V_C_140G_6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_08-..480V_C_140G_6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_09-1/2HP-..230V_C_140G_6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_09-1/2HP-..480V_C_140G_6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_10-..480V_C_140G_6_65kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_11-..200V_C_140G_6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..230V_C_140G_6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..480V_C_140G_6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_12-..480V_C_140G_6_65kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_13-..480V_C_140G_6_65kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_14-..480V_C_140G_6_65kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEFC | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_15-..200V_C_140G_6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..230V_C_140G_6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..480V_C_140G_6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_16-..200V_C_140G_6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..230V_C_140G_6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..480V_C_140G_6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_17-..200V_C_140G_6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..230V_C_140G_6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..480V_C_140G_6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_18-..230V_C_140G_6_65kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_18-..480V_C_140G_6_65kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_19-..480V_C_140G_6_65kA_2 (AB500DAB019) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_20-..480V_C_140G_6_65kA_2 (AB500DAB020) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-E…-E1+EEHE_21-..200V_C_140G_6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..230V_C_140G_6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..480V_C_140G_6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..230V_C_140G_6_65kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..480V_C_140G_6_65kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..480V_C_140G_6_65kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..480V_C_140G_6_65kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-F…-E1+EEKF_26-..600V_C_140G_6_25kA_2 (AB500DAB026) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..600V_C_140G_6_25kA_2 (AB500DAB027) | C | CB | Allen Bradley | 140G-JC6*200 | 600 | 3 | 25 | 200 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_28-..600V_C_140G_6_25kA_2 (AB500DAB028) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-D…-E1+EEGD_30-..230V_C_140G_6_65kA_2 (AB500DAB030) | C | CB | Allen Bradley | 140G-JC6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-E…-E1+EEHE_31-..230V_C_140G_6_65kA_2 (AB500DAB031) | C | CB | Allen Bradley | 140G-JC6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
Size 0-4; use Table 150 for W elements and Table 162 for J elements; Size 5 use Table 347 for W elements and Table 547 for J elements
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(7) = See Table 7 for minimum internal power wiring.
Table 7 - Minimum Internal Power Wiring
1/32in. thick thermoplastic insulation, rated 105C
Wire Code |  | Wire Size
7a |  | 10 AWG
7b |  | 10 AWG
7c |  | 8 AWG
7d |  | 4 AWG
7e |  | 1AWG
7f |  | 250 MCM

## 509 C E3
[16 empty] | Issued: | 2015-12-31
[16 empty] | Last Revised: | 2017-10-10
ID Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number [1] | Voltage | Number of Phases | SCCR, kA | Full Load Current, A | HP rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP Rating | Enclosure Volume, Cu Ft
AB509-A…-E3EC*D_01-..200V_C_140G-G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..200V_C_140G-G3_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..200V_C_140G-G2_50kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..230V_C_140G-G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..230V_C_140G-G3_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..230V_C_140G-G2_50kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..480V_C_140G-G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..480V_C_140G-G3_35kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..480V_C_140G-G2_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..600V_C_140G-H6_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*PC | 600 | 3 | 5 | 0.4-2 | ---
AB509-A…-E3EC*D_01-..600V_C_140G-H3_18kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*PC | 600 | 3 | 5 | 0.4-2 | ---
AB509-A…-E3EC*D_01-..600V_C_140G-H2_14kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*PC | 600 | 3 | 5 | 0.4-2 | ---
AB509-A…-E3EC*D_02-..200V_C_140G-G6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..200V_C_140G-G3_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..200V_C_140G-G2_50kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..230V_C_140G-G6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..230V_C_140G-G3_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..230V_C_140G-G2_50kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..480V_C_140G-G6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..480V_C_140G-G3_35kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..480V_C_140G-G2_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 35 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..600V_C_140G-H6_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..600V_C_140G-H3_18kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..600V_C_140G-H2_14kA (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..200V_C_140G-G6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..200V_C_140G-G3_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..200V_C_140G-G2_50kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..230V_C_140G-G6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | 3 | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..230V_C_140G-G3_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | 3 | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..230V_C_140G-G2_50kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | 3 | 230 | 3 | 50 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..480V_C_140G-G6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..480V_C_140G-G3_35kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..480V_C_140G-G2_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..600V_C_140G-H6_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..600V_C_140G-H3_18kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..600V_C_140G-H2_14kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_04-04/2HP-..200V_C_140G-G6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_04-04/2HP-..200V_C_140G-G3_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_04-04/2HP-..200V_C_140G-G2_50kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_04-04/2HP-..230V_C_140G-G6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_04-04/2HP-..230V_C_140G-G3_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_04-04/2HP-..230V_C_140G-G2_50kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_04-04/2HP-..480V_C_140G-G6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_04-04/2HP-..480V_C_140G-G3_35kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_04-04/2HP-..480V_C_140G-G2_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_04-04/2HP-..600V_C_140G-H6_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_04-04/2HP-..600V_C_140G-H3_18kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_04-04/2HP-..600V_C_140G-H2_14kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_05-..200V_C_140G-G6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_05-..200V_C_140G-G3_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_05-..200V_C_140G-G2_50kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_05-..230V_C_140G-G6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_05-..230V_C_140G-G3_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_05-..230V_C_140G-G2_50kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_05-..480V_C_140G-G6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_05-..480V_C_140G-G3_35kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_05-..480V_C_140G-G2_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_05-..600V_C_140G-H6_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_05-..600V_C_140G-H3_18kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_05-..600V_C_140G-H2_14kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_06-..200V_C_140G-G6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_06-..200V_C_140G-G3_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_06-..200V_C_140G-G2_50kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_06-..480V_C_140G-G6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_06-..480V_C_140G-G3_35kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_06-..480V_C_140G-G2_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_06-..600V_C_140G-H6_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_06-..600V_C_140G-H3_18kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_06-..600V_C_140G-H2_14kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_07-..480V_C_140G-G6_65kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_07-..480V_C_140G-G3_35kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_07-..480V_C_140G-G2_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_07-..600V_C_140G-H6_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_07-..600V_C_140G-H3_18kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_07-..600V_C_140G-H2_14kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_08-..200V_C_140G-G6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 200 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_08-..200V_C_140G-G3_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 200 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_08-..200V_C_140G-G2_50kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 200 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_08-..230V_C_140G-G6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_08-..230V_C_140G-G3_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_08-..230V_C_140G-G2_50kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_08-..480V_C_140G-G6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_08-..480V_C_140G-G3_35kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_08-..480V_C_140G-G2_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_08-..600V_C_140G-H6_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_08-..600V_C_140G-H3_18kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_08-..600V_C_140G-H2_14kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_09-1/2HP-..200V_C_140G-G6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB509-B…-E3EC*D_09-1/2HP-..200V_C_140G-G3_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB509-B…-E3EC*D_09-1/2HP-..200V_C_140G-G2_50kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB509-B…-E3EC*D_09-1/2HP-..480V_C_140G-G6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_09-1/2HP-..480V_C_140G-G3_35kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_09-1/2HP-..480V_C_140G-G2_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_09-1/2HP-..600V_C_140G-H6_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_09-1/2HP-..600V_C_140G-H3_18kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_09-1/2HP-..600V_C_140G-H2_14kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_10-..480V_C_140G-G6_65kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*D | 480 | 3 | 5 | 9.0-45 | ---
AB509-B…-E3EC*D_10-..480V_C_140G-G3_35kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*D | 480 | 3 | 5 | 9.0-45 | ---
AB509-B…-E3EC*D_10-..480V_C_140G-G2_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*D | 480 | 3 | 5 | 9.0-45 | ---
AB509-B…-E3EC*D_10-..600V_C_140G-H6_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_10-..600V_C_140G-H3_18kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_10-..600V_C_140G-H2_14kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-C…-E3EC*D_11-..200V_C_140G-G6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..200V_C_140G-G3_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..200V_C_140G-G2_50kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*50 | 200 | 3 | 50 | 50 | --- | 200 | 3 | 50 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..230V_C_140G-G6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..230V_C_140G-G3_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..230V_C_140G-G2_50kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*50 | 230 | 3 | 50 | 50 | --- | 230 | 3 | 50 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..480V_C_140G-G6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-C…-E3EC*D_11-..480V_C_140G-G3_35kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-C…-E3EC*D_11-..480V_C_140G-G2_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-C…-E3EC*D_11-..600V_C_140G-H6_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-C…-E3EC*D_11-..600V_C_140G-H3_18kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-C…-E3EC*D_11-..600V_C_140G-H2_14kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-C…-E3EC*D_12-..480V_C_140G-G6_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 480 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_12-..480V_C_140G-G3_35kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 480 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_12-..480V_C_140G-G2_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 480 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_12-..600V_C_140G-H6_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_12-..600V_C_140G-H3_18kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_12-..600V_C_140G-H2_14kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_13-..480V_C_140G-G6_65kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_13-..480V_C_140G-G3_35kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_13-..480V_C_140G-G2_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_13-..600V_C_140G-H6_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_13-..600V_C_140G-H3_18kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_13-..600V_C_140G-H2_14kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_14-..480V_C_140G-G6_65kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_14-..480V_C_140G-G3_35kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_14-..480V_C_140G-G2_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_14-..600V_C_140G-H6_25kA_140G-H6_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 600 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_14-..600V_C_140G-H3_18kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 600 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_14-..600V_C_140G-H2_14kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_15-..200V_C_140G-G6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..200V_C_140G-G3_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..200V_C_140G-G2_50kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..230V_C_140G-G6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..230V_C_140G-G3_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..230V_C_140G-G2_50kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..480V_C_140G-G6_65kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_15-..480V_C_140G-G3_35kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_15-..480V_C_140G-G2_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_15-..600V_C_140G-H6_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_15-..600V_C_140G-H3_18kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 17 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_15-..600V_C_140G-H2_14kA (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 17 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_16-..200V_C_140G-H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..200V_C_140G-H3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..200V_C_140G-H2_50kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..230V_C_140G-H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..230V_C_140G-H3_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..230V_C_140G-H2_50kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..480V_C_140G-H6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_16-..480V_C_140G-H3_35kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_16-..480V_C_140G-H2_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_16-..600V_C_140G-J6_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-J6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_16-..600V_C_140G-J3_18kA (AB500DAB016) | C | CB | Allen Bradley | 140G-J3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 22 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_16-..600V_C_140G-J2_14kA (AB500DAB016) | C | CB | Allen Bradley | 140G-J2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 22 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_17-..200V_C_140G-H6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..200V_C_140G-H3_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..200V_C_140G-H2_50kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..230V_C_140G-H6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..230V_C_140G-H3_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..230V_C_140G-H2_50kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..480V_C_140G-H6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_17-..480V_C_140G-H3_35kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_17-..480V_C_140G-H2_25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_17-..600V_C_140G-J6_25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-J6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_17-..600V_C_140G-J3_18kA (AB500DAB017) | C | CB | Allen Bradley | 140G-J3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 27 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_17-..600V_C_140G-J2_14kA (AB500DAB017) | C | CB | Allen Bradley | 140G-J2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 27 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_18-..480V_C_140G-H6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_18-..480V_C_140G-H3_35kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_18-..480V_C_140G-H2_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_18-..600V_C_140G-J6_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_18-..600V_C_140G-J3_18kA (AB500DAB018) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 32 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_18-..600V_C_140G-J2_14kA (AB500DAB018) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 32 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_19-..480V_C_140G-H6_65kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_19-..480V_C_140G-H3_35kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_19-..480V_C_140G-H2_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_19-..600V_C_140G-J6_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 41 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_19-..600V_C_140G-J3_18kA (AB500DAB019) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 41 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_19-..600V_C_140G-J2_14kA (AB500DAB019) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 41 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_20-..480V_C_140G-H6_65kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_20-..480V_C_140G-H3_35kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_20-..480V_C_140G-H2_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_20-..600V_C_140G-J6_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 600 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_20-..600V_C_140G-J3_18kA (AB500DAB020) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 52 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 600 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_20-..600V_C_140G-J2_14kA (AB500DAB020) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 52 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 600 | 3 | 5 | 18-90 | ---
AB509-E…-E3EC*F_21-..200V_C_140G-J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..200V_C_140G-J3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..200V_C_140G-J2_50kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*150 | 200 | 3 | 50 | 150 | --- | 200 | 3 | 50 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..230V_C_140G-J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..230V_C_140G-J3_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..230V_C_140G-J2_50kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*125 | 230 | 3 | 50 | 125 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..480V_C_140G-J6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..480V_C_140G-J3_35kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..480V_C_140G-J2_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..600V_C_140G-J6_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..600V_C_140G-J3_18kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 32 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..600V_C_140G-J2_14kA (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 32 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..480V_C_140G-J6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..480V_C_140G-J3_35kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..480V_C_140G-J2_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..600V_C_140G-J6_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..600V_C_140G-J3_18kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 18 | 52 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..600V_C_140G-J2_14kA (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 14 | 52 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..480V_C_140G-J6_65kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..480V_C_140G-J3_35kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..480V_C_140G-J2_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..600V_C_140G-J6_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 62 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..600V_C_140G-J3_18kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 62 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..600V_C_140G-J2_14kA (AB500DAB023) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 62 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..480V_C_140G-J6_65kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..480V_C_140G-J3_35kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..480V_C_140G-J2_25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..600V_C_140G-J6_25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..600V_C_140G-J3_18kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 77 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..600V_C_140G-J2_14kA (AB500DAB024) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 77 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_25-..600V_C_140G-J6_25kA (AB500DAB025) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 99 | 100 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_25-..600V_C_140G-J3_18kA (AB500DAB025) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 99 | 100 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_25-..600V_C_140G-J2_14kA (AB500DAB025) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 99 | 100 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-F…-E3EC*H_26-..200V_C_140G-K6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K6*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EC*HF | 200 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..200V_C_140G-K3_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K3*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EC*HF | 200 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..200V_C_140G-K2_50kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K2*400 | 200 | 3 | 50 | 400 | --- | 200 | 3 | 50 | 221 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EC*HF | 200 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..230V_C_140G-K6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EC*HF | 230 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..230V_C_140G-K3_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K3*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EC*HF | 230 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..230V_C_140G-K2_50kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K2*400 | 230 | 3 | 50 | 400 | --- | 230 | 3 | 50 | 192 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EC*HF | 230 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..480V_C_140G-K6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..480V_C_140G-K3_35kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K3*300 | 480 | 3 | 35 | 300 | --- | 480 | 3 | 35 | 96 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..480V_C_140G-K2_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-K2*300 | 480 | 3 | 25 | 300 | --- | 480 | 3 | 25 | 96 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..600V_C_140G-J6_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..600V_C_140G-J3_18kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..600V_C_140G-J2_14kA (AB500DAB026) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..230V_C_140G-K6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EC*HF | 230 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..230V_C_140G-K3_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K3*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EC*HF | 230 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..230V_C_140G-K2_50kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K2*400 | 230 | 3 | 50 | 400 | --- | 230 | 3 | 50 | 248 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EC*HF | 230 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..480V_C_140G-K6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..480V_C_140G-K3_35kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K3*300 | 480 | 3 | 35 | 300 | --- | 480 | 3 | 35 | 124 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..480V_C_140G-K2_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-K2*300 | 480 | 3 | 25 | 300 | --- | 480 | 3 | 25 | 124 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..600V_C_140G-J6_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J6*200 | 600 | 3 | 25 | 200 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..600V_C_140G-J3_18kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J3*200 | 600 | 3 | 18 | 200 | --- | 600 | 3 | 18 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..600V_C_140G-J2_14kA (AB500DAB027) | C | CB | Allen Bradley | 140G-J2*200 | 600 | 3 | 14 | 200 | --- | 600 | 3 | 14 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_28-..600V_C_140G-J6_25kA (AB500DAB028) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_28-..600V_C_140G-J3_18kA (AB500DAB028) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_28-..600V_C_140G-J2_14kA (AB500DAB028) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-A…-E3EC*D_01-..200V_C_140G-H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..200V_C_140G-H3_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..200V_C_140G-H2_50kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..230V_C_140G-H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..230V_C_140G-H3_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..230V_C_140G-H2_50kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..480V_C_140G-H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..480V_C_140G-H3_35kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..480V_C_140G-H2_25kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..200V_C_140G-H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..200V_C_140G-H3_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..200V_C_140G-H2_50kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..230V_C_140G-H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..230V_C_140G-H3_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..230V_C_140G-H2_50kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..480V_C_140G-H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..480V_C_140G-H3_35kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..480V_C_140G-H2_25kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..200V_C_140G-H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..200V_C_140G-H3_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..200V_C_140G-H2_50kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..230V_C_140G-H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..230V_C_140G-H3_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..230V_C_140G-H2_50kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..480V_C_140G-H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..480V_C_140G-H3_35kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..480V_C_140G-H2_25kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_04-04/2HP-..200V_C_140G-H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_04-04/2HP-..200V_C_140G-H3_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_04-04/2HP-..200V_C_140G-H2_50kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_04-04/2HP-..230V_C_140G-H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_04-04/2HP-..230V_C_140G-H3_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_04-04/2HP-..230V_C_140G-H2_50kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_04-04/2HP-..480V_C_140G-H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_04-04/2HP-..480V_C_140G-H3_35kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_04-04/2HP-..480V_C_140G-H2_25kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_05-..200V_C_140G-H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_05-..200V_C_140G-H3_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_05-..200V_C_140G-H2_50kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_05-..230V_C_140G-H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_05-..230V_C_140G-H3_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_05-..230V_C_140G-H2_50kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_05-..480V_C_140G-H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_05-..480V_C_140G-H3_35kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_05-..480V_C_140G-H2_25kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_06-..200V_C_140G-H6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_06-..200V_C_140G-H3_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_06-..200V_C_140G-H2_50kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_06-..480V_C_140G-H6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_06-..480V_C_140G-H3_35kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_06-..480V_C_140G-H2_25kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_07-..480V_C_140G-H6_65kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_07-..480V_C_140G-H3_35kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_07-..480V_C_140G-H2_25kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_08-..200V_C_140G-H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 200 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_08-..200V_C_140G-H3_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 200 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_08-..200V_C_140G-H2_50kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 200 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_08-..230V_C_140G-H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_08-..230V_C_140G-H3_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_08-..230V_C_140G-H2_50kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_08-..480V_C_140G-H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_08-..480V_C_140G-H3_35kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_08-..480V_C_140G-H2_25kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_09-1/2HP-..200V_C_140G-H6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB509-B…-E3EC*D_09-1/2HP-..200V_C_140G-H3_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB509-B…-E3EC*D_09-1/2HP-..200V_C_140G-H2_50kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB509-B…-E3EC*D_09-1/2HP-..480V_C_140G-H6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_09-1/2HP-..480V_C_140G-H3_35kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_09-1/2HP-..480V_C_140G-H2_25kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_10-..480V_C_140G-H6_65kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-B…-E3EC*D_10-..480V_C_140G-H3_35kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-B…-E3EC*D_10-..480V_C_140G-H2_25kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..200V_C_140G-H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..200V_C_140G-H3_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..200V_C_140G-H2_50kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*50 | 200 | 3 | 50 | 50 | --- | 200 | 3 | 50 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..230V_C_140G-H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..230V_C_140G-H3_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..230V_C_140G-H2_50kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*50 | 230 | 3 | 50 | 50 | --- | 230 | 3 | 50 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..480V_C_140G-H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-C…-E3EC*D_11-..480V_C_140G-H3_35kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-C…-E3EC*D_11-..480V_C_140G-H2_25kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-C…-E3EC*D_12-..480V_C_140G-H6_65kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 480 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_12-..480V_C_140G-H3_35kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 480 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_12-..480V_C_140G-H2_25kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 480 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_13-..480V_C_140G-H6_65kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 65 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_13-..480V_C_140G-H3_35kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 65 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_13-..480V_C_140G-H2_25kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 65 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_14-..480V_C_140G-H6_65kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_14-..480V_C_140G-H3_35kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_14-..480V_C_140G-H2_25kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_15-..200V_C_140G-H6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..200V_C_140G-H3_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..200V_C_140G-H2_50kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..200V_C_140G-I3_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..200V_C_140G-I2_50kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-I2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..230V_C_140G-H6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..230V_C_140G-H3_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..230V_C_140G-H2_50kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..230V_C_140G-I3_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..230V_C_140G-I2_50kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..480V_C_140G-H6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_15-..480V_C_140G-H3_35kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_15-..480V_C_140G-H2_25kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_16-..200V_C_140G-H6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..200V_C_140G-H3_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..200V_C_140G-H2_50kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..200V_C_140G-I3_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..200V_C_140G-I2_50kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-I2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..230V_C_140G-H6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..230V_C_140G-H3_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..230V_C_140G-H2_50kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..230V_C_140G-I3_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..230V_C_140G-I2_50kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..480V_C_140G-H6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_16-..480V_C_140G-H3_35kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_16-..480V_C_140G-H2_25kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_17-..200V_C_140G-H6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..200V_C_140G-H3_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..200V_C_140G-H2_50kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..200V_C_140G-I3_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..200V_C_140G-I2_50kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-I2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 50 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..230V_C_140G-H6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..230V_C_140G-H3_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..230V_C_140G-H2_50kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..230V_C_140G-I3_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-I3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..230V_C_140G-I2_50kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-I2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..480V_C_140G-H6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_17-..480V_C_140G-H3_35kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_17-..480V_C_140G-H2_25kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_18-..480V_C_140G-H6_65kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_18-..480V_C_140G-H3_35kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_18-..480V_C_140G-H2_25kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_19-..480V_C_140G-H6_65kA_2 (AB500DAB019) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_19-..480V_C_140G-H3_35kA_2 (AB500DAB019) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_19-..480V_C_140G-H2_25kA_2 (AB500DAB019) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_20-..480V_C_140G-H6_65kA_2 (AB500DAB020) | C | CB | Allen Bradley | 140G-H6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_20-..480V_C_140G-H3_35kA_2 (AB500DAB020) | C | CB | Allen Bradley | 140G-H3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_20-..480V_C_140G-H2_25kA_2 (AB500DAB020) | C | CB | Allen Bradley | 140G-H2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-E…-E3EC*F_21-..200V_C_140G-J6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..200V_C_140G-J3_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..200V_C_140G-J2_50kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*150 | 200 | 3 | 50 | 150 | --- | 200 | 3 | 50 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..200V_C_140G-I3_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..200V_C_140G-I2_50kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*150 | 200 | 3 | 50 | 150 | --- | 200 | 3 | 50 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..230V_C_140G-J6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..230V_C_140G-J3_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..230V_C_140G-J2_50kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*125 | 230 | 3 | 50 | 125 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..230V_C_140G-I3_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..230V_C_140G-I2_50kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*125 | 230 | 3 | 50 | 125 | --- | 230 | 3 | 50 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..480V_C_140G-J6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..480V_C_140G-J3_35kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..480V_C_140G-J2_25kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..480V_C_140G-I3_35kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..480V_C_140G-I2_25kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-I2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..480V_C_140G-J6_65kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..480V_C_140G-J3_35kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..480V_C_140G-J2_25kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-J2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..480V_C_140G-I3_35kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-I3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 35 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..480V_C_140G-I2_25kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-I2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 25 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..480V_C_140G-J6_65kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..480V_C_140G-J3_35kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..480V_C_140G-J2_25kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..480V_C_140G-I3_35kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-I3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..480V_C_140G-I2_25kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-I2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..480V_C_140G-J6_65kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-J6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..480V_C_140G-J3_35kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-J3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..480V_C_140G-J2_25kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-J2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..480V_C_140G-I3_35kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-I3*150 | 480 | 3 | 35 | 150 | --- | 480 | 3 | 35 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..480V_C_140G-I2_25kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-I2*150 | 480 | 3 | 25 | 150 | --- | 480 | 3 | 25 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-F…-E3EC*H_26-..600V_C_140G-J6_25kA_2 (AB500DAB026) | C | CB | Allen Bradley | 140G-J6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..600V_C_140G-J3_18kA_2 (AB500DAB026) | C | CB | Allen Bradley | 140G-J3*150 | 600 | 3 | 18 | 150 | --- | 600 | 3 | 18 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..600V_C_140G-J2_14kA_2 (AB500DAB026) | C | CB | Allen Bradley | 140G-J2*150 | 600 | 3 | 14 | 150 | --- | 600 | 3 | 14 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..600V_C_140G-J6_25kA_2 (AB500DAB027) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..600V_C_140G-J3_18kA_2 (AB500DAB027) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..600V_C_140G-J2_14kA_2 (AB500DAB027) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_28-..600V_C_140G-J6_25kA_2 (AB500DAB028) | C | CB | Allen Bradley | 140G-J6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_28-..600V_C_140G-J3_18kA_2 (AB500DAB028) | C | CB | Allen Bradley | 140G-J3*250 | 600 | 3 | 18 | 250 | --- | 600 | 3 | 18 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_28-..600V_C_140G-J2_14kA_2 (AB500DAB028) | C | CB | Allen Bradley | 140G-J2*250 | 600 | 3 | 14 | 250 | --- | 600 | 3 | 14 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-A…-E3EC*D_01-..600V_C_140G-6_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*PC | 600 | 3 | 5 | 0.4-2 | ---
AB509-A…-E3EC*D_02-..600V_C_140G-6_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..600V_C_140G-6_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_04-04/2HP-..600V_C_140G-6_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_05-..600V_C_140G-6_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_06-..600V_C_140G-6_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_07-..600V_C_140G-6_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_08-..600V_C_140G-6_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_09-1/2HP-..600V_C_140G-6_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_10-..600V_C_140G-6_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-C…-E3EC*D_11-..600V_C_140G-6_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-C…-E3EC*D_12-..600V_C_140G-6_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_13-..600V_C_140G-6_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_14-..600V_C_140G-6_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_15-..600V_C_140G-6_25kA (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_16-..200V_C_140G-6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..230V_C_140G-6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..480V_C_140G-6_65kA (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_16-..600V_C_140G-6_25kA (AB500DAB016) | C | CB | Allen Bradley | 140G-JC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_17-..200V_C_140G-6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..230V_C_140G-6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..480V_C_140G-6_65kA (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_17-..600V_C_140G-6_25kA (AB500DAB017) | C | CB | Allen Bradley | 140G-JC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_18-..480V_C_140G-6_65kA (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_18-..600V_C_140G-6_25kA (AB500DAB018) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_19-..480V_C_140G-6_65kA (AB500DAB019) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_19-..600V_C_140G-6_25kA (AB500DAB019) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 41 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_20-..480V_C_140G-6_65kA (AB500DAB020) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_20-..600V_C_140G-6_25kA (AB500DAB020) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 600 | 3 | 5 | 18-90 | ---
AB509-E…-E3EC*F_21-..200V_C_140G-6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..230V_C_140G-6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..480V_C_140G-6_65kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..600V_C_140G-6_25kA (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..480V_C_140G-6_65kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..600V_C_140G-6_25kA (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 25 | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..480V_C_140G-6_65kA (AB500DAB023) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..600V_C_140G-6_25kA (AB500DAB023) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 62 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..480V_C_140G-6_65kA (AB500DAB024) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..600V_C_140G-6_25kA (AB500DAB024) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_25-..600V_C_140G-6_25kA (AB500DAB025) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 99 | 100 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-F…-E3EC*H_26-..200V_C_140G-KC6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-KC6*400 | 200 | 3 | 65 | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EC*HF | 200 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..230V_C_140G-KC6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-KC6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EC*HF | 230 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..480V_C_140G-KC6_65kA (AB500DAB026) | C | CB | Allen Bradley | 140G-KC6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..600V_C_140G-6_25kA (AB500DAB026) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..230V_C_140G-KC6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-KC6*400 | 230 | 3 | 65 | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EC*HF | 230 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..480V_C_140G-KC6_65kA (AB500DAB027) | C | CB | Allen Bradley | 140G-KC6*300 | 480 | 3 | 65 | 300 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..600V_C_140G-6_25kA (AB500DAB027) | C | CB | Allen Bradley | 140G-JC6*200 | 600 | 3 | 25 | 200 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_28-..600V_C_140G-6_25kA (AB500DAB028) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-A…-E3EC*D_01-..200V_C_140G-6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..230V_C_140G-6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..480V_C_140G-6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..200V_C_140G-6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..230V_C_140G-6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..480V_C_140G-6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..200V_C_140G-6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..230V_C_140G-6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..480V_C_140G-6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_04-04/2HP-..200V_C_140G-6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_04-04/2HP-..230V_C_140G-6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_04-04/2HP-..480V_C_140G-6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_05-..200V_C_140G-6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_05-..230V_C_140G-6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_05-..480V_C_140G-6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_06-..200V_C_140G-6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_06-..480V_C_140G-6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_07-..480V_C_140G-6_65kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_08-..200V_C_140G-6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 200 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_08-..230V_C_140G-6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_08-..480V_C_140G-6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_09-1/2HP-..200V_C_140G-6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB509-B…-E3EC*D_09-1/2HP-..480V_C_140G-6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_10-..480V_C_140G-6_65kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..200V_C_140G-6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..230V_C_140G-6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..480V_C_140G-6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-C…-E3EC*D_12-..480V_C_140G-6_65kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 480 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_13-..480V_C_140G-6_65kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 65 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_14-..480V_C_140G-6_65kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_15-..200V_C_140G-6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..230V_C_140G-6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..480V_C_140G-6_65kA_2 (AB500DAB015) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_16-..200V_C_140G-6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..230V_C_140G-6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..480V_C_140G-6_65kA_2 (AB500DAB016) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_17-..200V_C_140G-6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..230V_C_140G-6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..480V_C_140G-6_65kA_2 (AB500DAB017) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_18-..480V_C_140G-6_65kA_2 (AB500DAB018) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_19-..480V_C_140G-6_65kA_2 (AB500DAB019) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_20-..480V_C_140G-6_65kA_2 (AB500DAB020) | C | CB | Allen Bradley | 140G-HC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-E…-E3EC*F_21-..200V_C_140G-6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*150 | 200 | 3 | 65 | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..230V_C_140G-6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*125 | 230 | 3 | 65 | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..480V_C_140G-6_65kA_2 (AB500DAB021) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..480V_C_140G-6_65kA_2 (AB500DAB022) | C | CB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..480V_C_140G-6_65kA_2 (AB500DAB023) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..480V_C_140G-6_65kA_2 (AB500DAB024) | C | CB | Allen Bradley | 140G-JC6*150 | 480 | 3 | 65 | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-F…-E3EC*H_26-..600V_C_140G-6_25kA_2 (AB500DAB026) | C | CB | Allen Bradley | 140G-JC6*150 | 600 | 3 | 25 | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..600V_C_140G-6_25kA_2 (AB500DAB027) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_28-..600V_C_140G-6_25kA_2 (AB500DAB028) | C | CB | Allen Bradley | 140G-JC6*250 | 600 | 3 | 25 | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
Size 0-4; use Table 150 for W elements and Table 162 for J elements; Size 5 use Table 347 for W elements and Table 547 for J elements
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(7) = See Table 7 for minimum internal power wiring.
Table 7 - Minimum Internal Power Wiring
1/32in. thick thermoplastic insulation, rated 105C
Wire Code |  | Wire Size
7a |  | 10 AWG
7b |  | 10 AWG
7c |  | 8 AWG
7d |  | 4 AWG
7e |  | 1AWG
7f |  | 250 MCM

## 509 C E300
[16 empty] | Issued: | 2015-12-31
[16 empty] | Last Revised: | 2017-10-10
ID Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage | Number of Phases | SCCR, kA | Full Load Current, A | HP rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP Rating | Enclosure Volume, CU Ft
AB509-A…-E300ESM-*-30A-S2_01-..200V_C_140G-G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..200V_C_140G-G3_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..200V_C_140G-G2_50kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..230V_C_140G-G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..230V_C_140G-G3_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..230V_C_140G-G2_50kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..480V_C_140G-G6_65kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..480V_C_140G-G3_35kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..480V_C_140G-G2_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..600V_C_140G-H6_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..600V_C_140G-H3_18kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..600V_C_140G-H2_14kA (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..200V_C_140G-G6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..200V_C_140G-G3_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..200V_C_140G-G2_50kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..230V_C_140G-G6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..230V_C_140G-G3_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..230V_C_140G-G2_50kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..480V_C_140G-G6_65kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..480V_C_140G-G3_35kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..480V_C_140G-G2_25kA (AB500DAB002) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..600V_C (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..600V_C (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..600V_C (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..200V_C_140G-G6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..200V_C_140G-G3_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..200V_C_140G-G2_50kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..230V_C_140G-G6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..230V_C_140G-G3_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..230V_C_140G-G2_50kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..480V_C_140G-G6_65kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..480V_C_140G-G3_35kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..480V_C_140G-G2_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..600V_C_140G-H6_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..600V_C_140G-H3_18kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..600V_C_140G-H2_14kA (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..200V_C_140G-G6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..200V_C_140G-G3_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..200V_C_140G-G2_50kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..230V_C_140G-G6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..230V_C_140G-G3_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..230V_C_140G-G2_50kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..480V_C_140G-G6_65kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..480V_C_140G-G3_35kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..480V_C_140G-G2_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..600V_C_140G-H6_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..600V_C_140G-H3_18kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..600V_C_140G-H2_14kA (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..200V_C_140G-G6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..200V_C_140G-G3_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..200V_C_140G-G2_50kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..230V_C_140G-G6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..230V_C_140G-G3_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..230V_C_140G-G2_50kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..480V_C_140G-G6_65kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..480V_C_140G-G3_35kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..480V_C_140G-G2_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..600V_C_140G-H6_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..600V_C_140G-H3_18kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..600V_C_140G-H2_14kA (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..200V_C_140G-G6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..200V_C_140G-G3_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..200V_C_140G-G2_50kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..480V_C_140G-G6_65kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..480V_C_140G-G3_35kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..480V_C_140G-G2_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..600V_C_140G-H6_25kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | 600 | 3 | 5 | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | 600 | 3 | 5 | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..600V_C_140G-H3_18kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | 600 | 3 | 5 | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | 600 | 3 | 5 | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..600V_C_140G-H2_14kA (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 3.9 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | 600 | 3 | 5 | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | 600 | 3 | 5 | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_07-..480V_C_140G-G6_65kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_07-..480V_C_140G-G3_35kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_07-..480V_C_140G-G2_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_07-..600V_C_140G-H6_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_07-..600V_C_140G-H3_18kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_07-..600V_C_140G-H2_14kA (AB500DAB007) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..200V_C_140G-G6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..200V_C_140G-G3_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..200V_C_140G-G2_50kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..230V_C_140G-G6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..230V_C_140G-G3_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..230V_C_140G-G2_50kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..480V_C_140G-G6_65kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..480V_C_140G-G3_35kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..480V_C_140G-G2_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-G2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..600V_C_140G-H6_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..600V_C_140G-H3_18kA (AB500DAB008) | C | x | Allen Bradley | 140G-H3*15 | 600 | 3 | 18 | 15 | --- | 600 | 3 | 18 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..600V_C_140G-H2_14kA (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*15 | 600 | 3 | 14 | 15 | --- | 600 | 3 | 14 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..200V_C_140G-G6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..200V_C_140G-G3_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..200V_C_140G-G2_50kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..480V_C_140G-G6_65kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..480V_C_140G-G3_35kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..480V_C_140G-G2_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..600V_C_140G-H6_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..600V_C_140G-H3_18kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..600V_C_140G-H2_14kA (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_10-..480V_C_140G-G6_65kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_10-..480V_C_140G-G3_35kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_10-..480V_C_140G-G2_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_10-..600V_C_140G-H6_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_10-..600V_C_140G-H3_18kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_10-..600V_C_140G-H2_14kA (AB500DAB010) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-C…-E300ESM-*-60A-S2_11-..200V_C_140G-G6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 200 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..200V_C_140G-G3_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 200 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..200V_C_140G-G2_50kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*50 | 200 | 3 | 50 | 50 | --- | 200 | 3 | 50 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 200 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..230V_C_140G-G6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..230V_C_140G-G3_65kA (AB500DAB011) | C | xv | Allen Bradley | 140G-G3*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..230V_C_140G-G2_50kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*50 | 230 | 3 | 50 | 50 | --- | 230 | 3 | 50 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..480V_C_140G-G6_65kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..480V_C_140G-G3_35kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..480V_C_140G-G2_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-G2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..600V_C_140G-H6_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..600V_C_140G-H3_18kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*30 | 600 | 3 | 18 | 30 | --- | 600 | 3 | 18 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..600V_C_140G-H2_14kA (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*30 | 600 | 3 | 14 | 30 | --- | 600 | 3 | 14 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_12-..480V_C_140G-G6_65kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_12-..480V_C_140G-G3_35kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_12-..480V_C_140G-G2_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_12-..600V_C_140G-H6_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_12-..600V_C_140G-H3_18kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_12-..600V_C_140G-H2_14kA (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_13-..480V_C_140G-G6_65kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_13-..480V_C_140G-G3_35kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_13-..480V_C_140G-G2_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_13-..600V_C_140G-H6_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_13-..600V_C_140G-H3_18kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_13-..600V_C_140G-H2_14kA (AB500DAB013) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_14-..480V_C_140G-G6_65kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_14-..480V_C_140G-G3_35kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_14-..480V_C_140G-G2_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-G2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_14-..600V_C_140G-H6_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_14-..600V_C_140G-H3_18kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H3*50 | 600 | 3 | 18 | 50 | --- | 600 | 3 | 18 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_14-..600V_C_140G-H2_14kA (AB500DAB014) | C | CB | Allen Bradley | 140G-H2*50 | 600 | 3 | 14 | 50 | --- | 600 | 3 | 14 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-A…-E300ESM-*-30A-S2_01-..200V_C_140G-H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..200V_C_140G-H3_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..200V_C_140G-H2_50kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..230V_C_140G-H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..230V_C_140G-H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..230V_C_140G-H2_50kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..480V_C_140G-H6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..480V_C_140G-H3_35kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..480V_C_140G-H2_25kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..200V_C_140G-H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..200V_C_140G-H3_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..200V_C_140G-H2_50kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..230V_C_140G-H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..230V_C_140G-H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..230V_C_140G-H2_50kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..480V_C_140G-H6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | 480 | 3 | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | 480 | 3 | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..480V_C_140G-H3_35kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | 480 | 3 | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | 480 | 3 | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..480V_C_140G-H2_25kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | 480 | 3 | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | 480 | 3 | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..200V_C_140G-H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..200V_C_140G-H3_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..200V_C_140G-H2_50kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..230V_C_140G-H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..230V_C_140G-H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..230V_C_140G-H2_50kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..480V_C_140G-H6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..480V_C_140G-H3_35kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..480V_C_140G-H2_25kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..200V_C_140G-H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..200V_C_140G-H3_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..200V_C_140G-H2_50kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..230V_C_140G-H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..230V_C_140G-H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..230V_C_140G-H2_50kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..480V_C_140G-H6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..480V_C_140G-H3_35kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..480V_C_140G-H2_25kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..200V_C_140G-H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..200V_C_140G-H3_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..200V_C_140G-H2_50kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 200 | 3 | 50 | 15 | --- | 200 | 3 | 50 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..230V_C_140G-H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..230V_C_140G-H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..230V_C_140G-H2_50kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 230 | 3 | 50 | 15 | --- | 230 | 3 | 50 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..480V_C_140G-H6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..480V_C_140G-H3_35kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..480V_C_140G-H2_25kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..200V_C_140G-H6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..200V_C_140G-H3_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..200V_C_140G-H2_50kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..230V_C_140G-H6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..230V_C_140G-H6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..230V_C_140G-H2_50kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..480V_C_140G-H6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..480V_C_140G-H3_35kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..480V_C_140G-H2_25kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_07-..480V_C_140G-H6_65kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_07-..480V_C_140G-H3_35kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_07-..480V_C_140G-H2_25kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..200V_C_140G-H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..200V_C_140G-H3_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..200V_C_140G-H2_50kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*30 | 200 | 3 | 50 | 30 | --- | 200 | 3 | 50 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..230V_C_140G-H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..230V_C_140G-H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..230V_C_140G-H2_50kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..480V_C_140G-H6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..480V_C_140G-H3_35kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H3*15 | 480 | 3 | 35 | 15 | --- | 480 | 3 | 35 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..480V_C_140G-H2_25kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-H2*15 | 480 | 3 | 25 | 15 | --- | 480 | 3 | 25 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..200V_C_140G-H6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..200V_C_140G-H3_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..200V_C_140G-H2_50kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 230 | 3 | 50 | 30 | --- | 230 | 3 | 50 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..480V_C_140G-H6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..480V_C_140G-H3_35kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..480V_C_140G-H2_25kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_10-..480V_C_140G-H6_65kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_10-..480V_C_140G-H3_35kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_10-..480V_C_140G-H2_25kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-C…-E300ESM-*-60A-S2_11-..200V_C_140G-H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 200 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..200V_C_140G-H3_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 200 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..200V_C_140G-H2_50kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*50 | 200 | 3 | 50 | 50 | --- | 200 | 3 | 50 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 200 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..230V_C_140G-H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..230V_C_140G-H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..230V_C_140G-H2_50kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*50 | 230 | 3 | 50 | 50 | --- | 230 | 3 | 50 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..480V_C_140G-H6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..480V_C_140G-H3_35kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H3*30 | 480 | 3 | 35 | 30 | --- | 480 | 3 | 35 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..480V_C_140G-H2_25kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-H2*30 | 480 | 3 | 25 | 30 | --- | 480 | 3 | 25 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_12-..230V_C_140G-H6_65kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_12-..230V_C_140G-H6_65kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_12-..230V_C_140G-H2_50kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 50 | 42 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_12-..480V_C_140G-H6_65kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_12-..480V_C_140G-H3_35kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_12-..480V_C_140G-H2_25kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_13-..480V_C_140G-H6_65kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_13-..480V_C_140G-H3_35kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_13-..480V_C_140G-H2_25kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_14-..480V_C_140G-H6_65kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-H6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_14-..480V_C_140G-H3_35kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-H3*50 | 480 | 3 | 35 | 50 | --- | 480 | 3 | 35 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_14-..480V_C_140G-H2_25kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-H2*50 | 480 | 3 | 25 | 50 | --- | 480 | 3 | 25 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-A…-E300ESM-*-30A-S2_01-..600V_C_140G-6_25kA (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..600V_C (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..600V_C_140G-6_25kA (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..600V_C_140G-6_25kA (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..600V_C_140G-6_25kA (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_07-..480V_C_140G-G6_65kA (AB500DAB007) | C | CB | Allen Bradley | 140G-G6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_07-..600V_C_140G-6_25kA (AB500DAB007) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..600V_C_140G-6_25kA (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*15 | 600 | 3 | 25 | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..600V_C_140G-6_25kA (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_10-..600V_C_140G-6_25kA (AB500DAB010) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-C…-E300ESM-*-60A-S2_11-..600V_C_140G-6_25kA (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*30 | 600 | 3 | 25 | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_12-..600V_C_140G-6_25kA (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_13-..600V_C_140G-6_25kA (AB500DAB013) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_14-..600V_C_140G-6_25kA (AB500DAB014) | C | CB | Allen Bradley | 140G-HC6*50 | 600 | 3 | 25 | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-A…-E300ESM-*-30A-S2_01-..200V_C_140G-6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..230V_C_140G-6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..480V_C_140G-6_65kA_2 (AB500DAB001) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..200V_C_140G-6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..230V_C_140G-6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..480V_C_140G-6_65kA_2 (AB500DAB002) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | 480 | 3 | 5 | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | 480 | 3 | 5 | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..200V_C_140G-6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..230V_C_140G-6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..480V_C_140G-6_65kA_2 (AB500DAB003) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..200V_C_140G-6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..230V_C_140G-6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..480V_C_140G-6_65kA_2 (AB500DAB004) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..200V_C_140G-6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 200 | 3 | 65 | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..230V_C_140G-6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 230 | 3 | 65 | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..480V_C_140G-6_65kA_2 (AB500DAB005) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..200V_C_140G-6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..230V_C_140G-6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..480V_C_140G-6_65kA_2 (AB500DAB006) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_07-..480V_C_140G-6_65kA_2 (AB500DAB007) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..200V_C_140G-6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*30 | 200 | 3 | 65 | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..230V_C_140G-6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..480V_C_140G-6_65kA_2 (AB500DAB008) | C | CB | Allen Bradley | 140G-HC6*15 | 480 | 3 | 65 | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..200V_C_140G-6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 230 | 3 | 65 | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..480V_C_140G-6_65kA_2 (AB500DAB009) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_10-..480V_C_140G-6_65kA_2 (AB500DAB010) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-C…-E300ESM-*-60A-S2_11-..200V_C_140G-6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*50 | 200 | 3 | 65 | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 200 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..230V_C_140G-6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*50 | 230 | 3 | 65 | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..480V_C_140G-6_65kA_2 (AB500DAB011) | C | CB | Allen Bradley | 140G-HC6*30 | 480 | 3 | 65 | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_12-..230V_C_140G-6_65kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 65 | 42 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_12-..480V_C_140G-6_65kA_2 (AB500DAB012) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_13-..480V_C_140G-6_65kA_2 (AB500DAB013) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_14-..480V_C_140G-6_65kA_2 (AB500DAB014) | C | CB | Allen Bradley | 140G-HC6*50 | 480 | 3 | 65 | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-G6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-G6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-G6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-H6*100 | 600 | 3 | 65 | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J6*100 | 600 | 3 | 65 | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB509-E…-E300ESM-*-200A-S4_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J6*175 | 200 | 3 | 65 | 175 | --- | 200 | 3 | 22 | 120 | 40 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 5 | 120 | 40
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 200 | 3 | 5 | 20-135 | ---
AB509-E…-E300ESM-*-200A-S4_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 22 | 139 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 5 | 139 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 230 | 3 | 5 | 20-135 | ---
AB509-E…-E300ESM-*-200A-S4_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J6*175 | 480 | 3 | 65 | 175 | --- | 480 | 3 | 22 | 124 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 5 | 124 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 480 | 3 | 5 | 20-135 | ---
AB509-E…-E300ESM-*-200A-S4_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J6*175 | 600 | 3 | 65 | 175 | --- | 600 | 3 | 14 | 99 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 5 | 99 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 600 | 3 | 5 | 20-135 | ---
AB509-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-HC6*100 | 600 | 3 | 65 | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-JC6*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-JC6*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-JC6*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-JC6*100 | 600 | 3 | 65 | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB509-E…-E300ESM-*-200A-S4_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-JC6*175 | 200 | 3 | 65 | 175 | --- | 200 | 3 | 22 | 120 | 40 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 5 | 120 | 40
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 200 | 3 | 5 | 20-135 | ---
AB509-E…-E300ESM-*-200A-S4_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-JC6*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 22 | 139 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 5 | 139 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 230 | 3 | 5 | 20-135 | ---
AB509-E…-E300ESM-*-200A-S4_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-JC6*175 | 480 | 3 | 65 | 175 | --- | 480 | 3 | 22 | 124 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 5 | 124 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 480 | 3 | 5 | 20-135 | ---
AB509-E…-E300ESM-*-200A-S4_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-JC6*175 | 600 | 3 | 65 | 175 | --- | 600 | 3 | 14 | 99 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 5 | 99 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 600 | 3 | 5 | 20-135 | ---
AB509-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-G3*100 | 200 | 3 | 100 | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-G3*100 | 230 | 3 | 100 | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-G3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-H3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J3*100 | 200 | 3 | 100 | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J3*100 | 230 | 3 | 100 | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I3*100 | 480 | 3 | 35 | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J3*100 | 600 | 3 | 18 | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB509-E…-E300ESM-*-200A-S4_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J3*175 | 200 | 3 | 100 | 175 | --- | 200 | 3 | 22 | 120 | 40 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 5 | 120 | 40
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 200 | 3 | 5 | 20-135 | ---
AB509-E…-E300ESM-*-200A-S4_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J3*175 | 230 | 3 | 100 | 175 | --- | 230 | 3 | 22 | 139 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 5 | 139 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 230 | 3 | 5 | 20-135 | ---
AB509-E…-E300ESM-*-200A-S4_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J3*175 | 480 | 3 | 35 | 175 | --- | 480 | 3 | 22 | 124 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 5 | 124 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 480 | 3 | 5 | 20-135 | ---
AB509-E…-E300ESM-*-200A-S4_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I3*175 | 480 | 3 | 35 | 175 | --- | 480 | 3 | 22 | 124 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 5 | 124 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 480 | 3 | 5 | 20-135 | ---
AB509-E…-E300ESM-*-200A-S4_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J3*175 | 600 | 3 | 18 | 175 | --- | 600 | 3 | 14 | 99 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 5 | 99 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 600 | 3 | 5 | 20-135 | ---
AB509-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-G2*100 | 200 | 3 | 50 | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-G2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-G2*100 | 480 | 3 | 25 | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-H2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J2*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J2*100 | 230 | 3 | 65 | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I3*100 | 200 | 3 | 65 | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I2*100 | 230 | 3 | 50 | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J2*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I2*100 | 480 | 3 | 65 | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J2*100 | 600 | 3 | 14 | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB509-E…-E300ESM-*-200A-S4_11-..200V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J2*175 | 200 | 3 | 65 | 175 | --- | 200 | 3 | 22 | 120 | 40 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 5 | 120 | 40
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 200 | 3 | 5 | 20-135 | ---
AB509-E…-E300ESM-*-200A-S4_11-..230V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J2*175 | 230 | 3 | 65 | 175 | --- | 230 | 3 | 22 | 139 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 5 | 139 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 230 | 3 | 5 | 20-135 | ---
AB509-E…-E300ESM-*-200A-S4_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J2*175 | 480 | 3 | 25 | 175 | --- | 480 | 3 | 22 | 124 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 5 | 124 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 480 | 3 | 5 | 20-135 | ---
AB509-E…-E300ESM-*-200A-S4_11-..480V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-I2*175 | 480 | 3 | 25 | 175 | --- | 480 | 3 | 22 | 124 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 5 | 124 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 480 | 3 | 5 | 20-135 | ---
AB509-E…-E300ESM-*-200A-S4_11-..600V_C (AB500DAB011) | C | ICB | Allen Bradley | 140G-J2*175 | 600 | 3 | 14 | 175 | --- | 600 | 3 | 14 | 99 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 5 | 99 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 600 | 3 | 5 | 20-135 | ---
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(7) = See Table 7 for minimum internal power wiring.
Table 7 - Minimum Internal Power Wiring
1/32in. thick thermoplastic insulation, rated 105C
Wire Code |  | Wire Size
7a |  | 10 AWG
7b |  | 10 AWG
7c |  | 8 AWG
7d |  | 4 AWG
7e |  | 1AWG
7f |  | 250 MCM

## 509 D EUT
[16 empty] | Issued: | 2015-12-31
[16 empty] | Last Revised: | 2017-10-10
ID Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage | Number of Phases | SCCR, kA | Full Load Current, A | HP rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP Rating | Enclosure Volume, CU Ft
AB509-A…-EUTB42_01-..200V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 200 | 3 | --- | 3 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..230V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 230 | 3 | --- | 3 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..480V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..600V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..200V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..230V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..480V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..600V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..200V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..230V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..480V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..600V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1HP-..600V (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..200V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..200V (AB500DAB004) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1-1/2HP-..200V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..230V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..230V (AB500DAB004) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1-1/2HP-..230V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..480V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..480V (AB500DAB004) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1-1/2HP-..480V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..600V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_1-1/2HP-..600V (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..200V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..200V (AB500DAB005) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_2HP-..200V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..230V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..230V (AB500DAB005) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_2HP-..230V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..480V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..480V (AB500DAB005) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_2HP-..480V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..600V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*7 | 600 | 3 | --- | 7 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_2HP-..600V (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..200V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..200V (AB500DAB006) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3HP-..200V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..480V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..480V (AB500DAB006) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3HP-..480V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..600V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*7 | 600 | 3 | --- | 7 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_3HP-..600V (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_07-..480V_C (AB500DAB007) | D | ICB | Allen Bradley | 140MG-G8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..480V (AB500DAB007) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_5HP-..480V (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_07-..600V_C (AB500DAB007) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
AB500F-A…-EUTB42_5HP-..600V (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..200V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..200V (AB500DAB008) |  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_5HP-..200V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..230V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..230V (AB500DAB008) |  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_5HP-..230V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..480V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..480V (AB500DAB008) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_5HP-..480V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..600V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_5HP-..600V (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..230V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..230V (AB500DAB009) |  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_7-1/2HP-..230V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..480V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..480V (AB500DAB009) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_7-1/2HP-..480V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..600V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_7-1/2HP-..600V (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_10-..480V_C (AB500DAB010) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..480V (AB500DAB010) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_10HP-..480V (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_10-..600V_C (AB500DAB010) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
AB500F-B…-EUTB42_10HP-..600V (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-C…-EUTC42_11-..200V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V (AB500DAB011) |  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..230V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V (AB500DAB011) |  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..480V (AB500DAB011) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_10HP-..480V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..600V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_10HP-..600V (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..480V_C (AB500DAB012) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..480V (AB500DAB012) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_15HP-..480V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..600V_C (AB500DAB012) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_15HP-..600V (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_13-..480V_C (AB500DAB013) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..480V (AB500DAB013) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_20HP-..480V (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_13-..600V_C (AB500DAB013) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_20HP-..600V (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_14-..480V_C (AB500DAB014) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..480V (AB500DAB014) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_25HP-..480V (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_14-..600V_C (AB500DAB014) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
AB500F-C…-EUTC42_25HP-..600V (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 600 | 3 | 5 | 68 | ---
AB509-D…-EUTD42_15-..200V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-G8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V (AB500DAB015) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..230V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-G8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..230V (AB500DAB015) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_15HP-..230V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..480V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..480V (AB500DAB015) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_15HP-..480V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..600V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 17 | 15 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_15HP-..600V (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..200V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-G8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..230V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-G8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..480V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_20HP-..480V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..600V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-J8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 22 | 20 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_20HP-..600V (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..200V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..230V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..480V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..480V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_25HP-..480V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..600V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-J8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 27 | 25 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_25HP-..600V (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..480V_C (AB500DAB018) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..600V_C (AB500DAB018) | D | ICB | Allen Bradley | 140MG-J8*80 | 600 | 3 | --- | 80 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..600V (AB500DAB018) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_30HP-..600V (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_19-..480V_C (AB500DAB019) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_19-..600V_C (AB500DAB019) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 41 | 40 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_40HP-..600V (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_20-..480V_C (AB500DAB020) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42G_20-..480V_C (AB500DAB020) | D | ICB | Allen Bradley | 140MG-G8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_20-..600V_C (AB500DAB020) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
AB500F-D…-EUTD42_50HP-..600V (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 600 | 3 | 5 | 125 | ---
AB509-E…-EUTE42_21-..200V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*150 | 200 | 3 | --- | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..230V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*125 | 230 | 3 | --- | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..480V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42I_21-..480V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..600V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*80 | 600 | 3 | --- | 80 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_30HP-..600V (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..480V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42I_22-..480V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..600V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_50HP-..600V (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..480V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42I_23-..480V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..600V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 62 | 60 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_60HP-..600V (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_24-..480V_C (AB500DAB024) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42I_24-..480V_C (AB500DAB024) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_75HP-..480V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_24-..600V_C (AB500DAB024) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 77 | 75 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_75HP-..600V (AB500DAB024) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_25-..600V_C (AB500DAB025) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 99 | 100 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_100HP-..600V (AB500DAB025) |  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
AB500F-E…-EUTE42_100HP-..600V (AB500DAB025) |  | OLR | Allen Bradley | 592-EUTE | 600 | 3 | 10 | 172 | ---
AB509-F…-EUTF42_26-..200V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-K8*400 | 200 | 3 | --- | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 200 | 3 | 10 | 221 | 75
AB500F-F…-EUTF42_75HP-..200V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 200 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_26-..230V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-K8*400 | 230 | 3 | --- | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_75HP-..230V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_26-..480V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-K8*175 | 480 | 3 | --- | 175 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_75HP-..480V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_26-..600V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 125 | ---
AB509-F…-EUTF42_27-..230V_C (AB500DAB027) | D | ICB | Allen Bradley | 140MG-K8*400 | 230 | 3 | --- | 400 | --- | 230 | 3 | 65 | 248 | 100 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
AB500F-F…-EUTF42_100HP-..230V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 230 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_27-..480V_C (AB500DAB027) | D | ICB | Allen Bradley | 140MG-K8*400 | 480 | 3 | --- | 400 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
AB500F-F…-EUTF42_100HP-..480V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 480 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_27-..600V_C (AB500DAB027) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_28-..600V_C (AB500DAB028) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V (AB500DAB028) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-A…-EUTB42_01-..200V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 200 | 3 | --- | 3 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1/2HP-..200V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..230V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 230 | 3 | --- | 3 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1/2HP-..230V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_01-..480V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1/2HP-..480V_2 (AB500DAB001) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..200V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3/4HP-..200V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..230V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3/4HP-..230V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_02-..480V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3/4HP-..480V_2 (AB500DAB002) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..200V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1HP-..200V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..230V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1HP-..230V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_03-..480V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1HP-..480V_2 (AB500DAB003) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..200V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_1-1/2HP-..200V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..230V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_1-1/2HP-..230V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_04-04/2HP-..480V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_1-1/2HP-..480V_2 (AB500DAB004) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..200V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_2HP-..200V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..230V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_2HP-..230V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_05-..480V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_2HP-..480V_2 (AB500DAB005) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..200V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
AB500F-A…-EUTB42_3HP-..200V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..230V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
AB500F-A…-EUTB42_3HP-..230V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_06-..480V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_3HP-..480V_2 (AB500DAB006) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_07-..480V_C_2 (AB500DAB007) | D | ICB | Allen Bradley | 140MG-H8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
AB500F-A…-EUTB42_5HP-..480V_2 (AB500DAB007) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..200V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
AB500F-B…-EUTB42_5HP-..200V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 200 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..230V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_5HP-..230V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_08-..480V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_5HP-..480V_2 (AB500DAB008) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..230V_C_2 (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..230V_2 (AB500DAB009) |  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-EUTB42_7-1/2HP-..230V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 230 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_09-1/2HP-..480V_C_2 (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_7-1/2HP-..480V_2 (AB500DAB009) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-B…-EUTB42_10-..480V_C_2 (AB500DAB010) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 5, 7b | E125316 dated 2001-09-12
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
AB500F-B…-EUTB42_10HP-..480V_2 (AB500DAB010) |  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-C…-EUTC42_11-..200V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..230V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB509-C…-EUTC42I_11-..200V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
AB500F-C…-EUTC42_10HP-..200V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 200 | 3 | 5 | 68 | ---
AB509-C…-EUTC42I_11-..230V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
AB500F-C…-EUTC42_10HP-..230V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 230 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_11-..480V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_10HP-..480V_2 (AB500DAB011) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_12-..480V_C_2 (AB500DAB012) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_15HP-..480V_2 (AB500DAB012) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_13-..480V_C_2 (AB500DAB013) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_20HP-..480V_2 (AB500DAB013) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-C…-EUTC42_14-..480V_C_2 (AB500DAB014) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 3, 5, 7c | E125316 dated 2001-09-12
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
AB500F-C…-EUTC42_25HP-..480V_2 (AB500DAB014) |  | OLR | Allen Bradley | 592-EUTC | 480 | 3 | 5 | 68 | ---
AB509-D…-EUTD42_15-..200V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42I_15-..200V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_15HP-..200V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_15-..480V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_15HP-..480V_2 (AB500DAB015) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..200V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..230V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42I_16-..200V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_20HP-..200V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42I_16-..230V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_20HP-..230V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_16-..480V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_20HP-..480V_2 (AB500DAB016) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_20HP-..480V_2 (AB500DAB016) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..200V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..230V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42I_17-..200V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
AB500F-D…-EUTD42_25HP-..200V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 200 | 3 | 5 | 125 | ---
AB509-D…-EUTD42I_17-..230V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_25HP-..230V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_17-..480V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_25HP-..480V_2 (AB500DAB017) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_25HP-..480V_2 (AB500DAB017) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..230V_C_2 (AB500DAB018) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42I_18-..230V_C_2 (AB500DAB018) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
AB500F-D…-EUTD42_30HP-..230V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 230 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_18-..480V_C_2 (AB500DAB018) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_30HP-..480V_2 (AB500DAB018) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_19-..480V_C_2 (AB500DAB019) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_40HP-..480V_2 (AB500DAB019) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-D…-EUTD42_20-..480V_C_2 (AB500DAB020) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 5, 7d | E125316 dated 2001-09-12
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
AB500F-D…-EUTD42_50HP-..480V_2 (AB500DAB020) |  | OLR | Allen Bradley | 592-EUTD | 480 | 3 | 5 | 125 | ---
AB509-E…-EUTE42_21-..200V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*150 | 200 | 3 | --- | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..230V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*125 | 230 | 3 | --- | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42I_21-..200V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*150 | 200 | 3 | --- | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
AB500F-E…-EUTE42_30HP-..200V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 200 | 3 | 10 | 172 | ---
AB509-E…-EUTE42I_21-..230V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*125 | 230 | 3 | --- | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
AB500F-E…-EUTE42_30HP-..230V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 230 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_21-..480V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42I_21-..480V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_30HP-..480V_2 (AB500DAB021) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_22-..480V_C_2 (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42I_22-..480V_C_2 (AB500DAB022) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_50HP-..480V_2 (AB500DAB022) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42_23-..480V_C_2 (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-E…-EUTE42I_23-..480V_C_2 (AB500DAB023) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 3, 5, 7e | E125316 dated 2001-09-12
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
AB500F-E…-EUTE42_60HP-..480V_2 (AB500DAB023) |  | OLR | Allen Bradley | 592-EUTE | 480 | 3 | 10 | 172 | ---
AB509-F…-EUTF42_26-..600V_C_2 (AB500DAB026) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_75HP-..600V_2 (AB500DAB026) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_27-..600V_C_2 (AB500DAB027) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_100HP-..600V_2 (AB500DAB027) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-F…-EUTF42_29-..600V_C_2 (AB500DAB029) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 3, 5, 7f | E125316 dated 2001-09-12
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
AB500F-F…-EUTF42_200HP-..600V_2 (AB500DAB029) |  | OLR | Allen Bradley | 592-FOW** | 600 | 3 | 10 | 279 | ---
AB509-A…-EUTB42_32-..480V_D (AB500DAB032) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_32-..600V_D (AB500DAB032) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_33-..480V_D (AB500DAB033) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EUTB | 480 | 3 | 5 | 42 | ---
AB509-A…-EUTB42_34-..600V_D (AB500DAB034) | D | ICB | Allen Bradley | 140MG-H8*7 | 600 | 3 | --- | 7 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 3, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EUTB | 600 | 3 | 5 | 42 | ---
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
Size 0-4; use Table 152 for W elements and Table 163 for J elements; Size 5 use Table 347 for W elements and Table 547 for J elements
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(7) = See Table 7 for minimum internal power wiring.
Table 7 - Minimum Internal Power Wiring
1/32in. thick thermoplastic insulation, rated 105C
Wire Code |  | Wire Size
7a |  | 10 AWG
7b |  | 10 AWG
7c |  | 8 AWG
7d |  | 4 AWG
7e |  | 1AWG
7f |  | 250 MCM

## 509 D E1+
[16 empty] | Issued: | 2015-12-31
[16 empty] | Last Revised: | 2017-10-10
ID Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage | Number of Phases | SCCR, kA | Full Load Current, A | HP rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP Rating | Enclosure Volume, CU Ft
AB509-A…-E1+EEEC_01-..200V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 200 | 3 | --- | 3 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_01-..230V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 230 | 3 | --- | 3 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_01-..480V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_01-..600V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEBC | 600 | 3 | 5 | 0.2-1 | ---
AB509-A…-E1+EEEC_02-..200V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_02-..230V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_02-..480V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_02-..600V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_03-..200V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_03-..230V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_03-..480V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_03-..600V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E04+EEEC_04-04/2HP-..200V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E04+EEEC_04-04/2HP-..230V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E04+EEEC_04-04/2HP-..480V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E04+EEEC_04-04/2HP-..600V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_05-..200V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_05-..230V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_05-..480V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_05-..600V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*7 | 600 | 3 | --- | 7 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_06-..200V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_06-..480V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_06-..600V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*7 | 600 | 3 | --- | 7 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EECC | 600 | 3 | 5 | 1.0-5.0 | ---
AB509-A…-E1+EEEC_07-..480V_C (AB500DAB007) | D | ICB | Allen Bradley | 140MG-G8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_07-..600V_C (AB500DAB007) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | 5
AB509-B…-E1+EEEC_08-..200V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 200 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_08-..230V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_08-..480V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_08-..600V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_09-1/2HP-..200V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_09-1/2HP-..480V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_09-1/2HP-..600V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_10-..480V_C (AB500DAB010) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_10-..600V_C (AB500DAB010) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | 10
AB509-C…-E1+EEFC_11-..200V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..230V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-C…-E1+EEFC_11-..600V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
AB509-C…-E1+EEFC_12-..480V_C (AB500DAB012) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_12-..600V_C (AB500DAB012) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_13-..480V_C (AB500DAB013) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_13-..600V_C (AB500DAB013) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_14-..480V_C (AB500DAB014) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEFC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_14-..600V_C (AB500DAB014) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EEEC | 600 | 3 | 5 | 5.4-2.7 | ---
AB509-D…-E1+EEGD_15-..200V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-G8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..230V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-G8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..480V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_15-..600V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 17 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_16-..200V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-G8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..230V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-G8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..480V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_16-..600V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-J8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 22 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_17-..200V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-G8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..230V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-G8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..480V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_17-..600V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-J8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 27 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_18-..230V_C (AB500DAB018) | D | ICB | Allen Bradley | 140MG-G8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_18-..480V_C (AB500DAB018) | D | ICB | Allen Bradley | 140MG-G8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_18-..600V_C (AB500DAB018) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_19-..480V_C (AB500DAB019) | D | ICB | Allen Bradley | 140MG-G8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_19-..600V_C (AB500DAB019) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 41 | 40 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEFD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_20-..480V_C (AB500DAB020) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_20-..G480V_C (AB500DAB020) | D | ICB | Allen Bradley | 140MG-G8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_20-..600V_C (AB500DAB020) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EEGD | 600 | 3 | 5 | 18-90 | ---
AB509-E…-E1+EEHE_21-..200V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*150 | 200 | 3 | --- | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..230V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*125 | 230 | 3 | --- | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..480V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..I480V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..600V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..230V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*150 | 230 | 3 | --- | 150 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..480V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..I480V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..600V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..480V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..I480V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..600V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 62 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..480V_C (AB500DAB024) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..I480V_C (AB500DAB024) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..600V_C (AB500DAB024) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 77 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_25-..600V_C (AB500DAB025) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 99 | 100 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EEHE | 600 | 3 | 10 | 30-150 | ---
AB509-F…-E1+EEKF_26-..200V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-K8*400 | 200 | 3 | --- | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EEKF | 200 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..230V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-K8*400 | 230 | 3 | --- | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EEKF | 230 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..480V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-K8*400 | 480 | 3 | --- | 400 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_26-..600V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..480V_C (AB500DAB027) | D | ICB | Allen Bradley | 140MG-J8*175 | 480 | 3 | --- | 175 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..I480V_C (AB500DAB027) | D | ICB | Allen Bradley | 140MG-I8*175 | 480 | 3 | --- | 175 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EEKF | 480 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..600V_C (AB500DAB027) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_28-..600V_C (AB500DAB028) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-A…-E1+EEEC_01-..200V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 200 | 3 | --- | 3 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_01-..230V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 230 | 3 | --- | 3 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_01-..480V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_02-..200V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_02-..230V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_02-..480V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_03-..200V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EECC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_03-..230V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EECC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_03-..480V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E04+EEEC_04-04/2HP-..200V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E04+EEEC_04-04/2HP-..230V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E04+EEEC_04-04/2HP-..480V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_05-..200V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_05-..230V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EEDC | 230 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_05-..480V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_06-..200V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EEDC | 200 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_06-..480V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EECC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E1+EEEC_07-..480V_C_2 (AB500DAB007) | D | ICB | Allen Bradley | 140MG-H8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_08-..200V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 200 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_08-..230V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_08-..480V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_09-1/2HP-..200V_C_2 (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EEEC | 230 | 3 | 5 | 5.4-27 | ---
AB509-B…-E1+EEEC_09-1/2HP-..480V_C_2 (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-B…-E1+EEEC_10-..480V_C_2 (AB500DAB010) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_11-..200V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..230V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..I200V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EEFC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..I230V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EEFC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E1+EEFC_11-..480V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_12-..480V_C_2 (AB500DAB012) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_13-..480V_C_2 (AB500DAB013) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEEC | 480 | 3 | 5 | 5.4-27 | ---
AB509-C…-E1+EEFC_14-..480V_C_2 (AB500DAB014) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EEFC | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_15-..200V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..230V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..I200V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..I230V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_15-..480V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_16-..200V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..230V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..I200V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..I230V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_16-..480V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_17-..200V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..230V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..I200V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EEGD | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..I230V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EEGD | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_17-..480V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_18-..480V_C_2 (AB500DAB018) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEFD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E1+EEGD_19-..480V_C_2 (AB500DAB019) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E1+EEGD_20-..480V_C_2 (AB500DAB020) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EEGD | 480 | 3 | 5 | 18-90 | ---
AB509-E…-E1+EEHE_21-..200V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*150 | 200 | 3 | --- | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..230V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*125 | 230 | 3 | --- | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..I200V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*150 | 200 | 3 | --- | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EEHE | 200 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..I230V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*125 | 230 | 3 | --- | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..480V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_21-..I480V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..480V_C_2 (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_22-..I480V_C_2 (AB500DAB022) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 75
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..480V_C_2 (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_23-..I480V_C_2 (AB500DAB023) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..480V_C_2 (AB500DAB024) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_24-..480V_C_2 (AB500DAB024) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EEHE | 480 | 3 | 10 | 30-150 | ---
AB509-F…-E1+EEKF_26-..600V_C_2 (AB500DAB026) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_27-..600V_C_2 (AB500DAB027) | D | ICB | Allen Bradley | 140MG-J8*200 | 600 | 3 | --- | 200 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-F…-E1+EEKF_28-..600V_C_2 (AB500DAB028) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EEKF | 600 | 3 | 10 | 60-300 | ---
AB509-E…-E1+EEHE_31-..I230V_C_2 (AB500DAB031) | D | ICB | Allen Bradley | 140MG-I8*150 | 230 | 3 | --- | 150 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-E…-E1+EEHE_31-..230V_C_2 (AB500DAB031) | D | ICB | Allen Bradley | 140MG-J8*150 | 230 | 3 | --- | 150 | --- | 230 | 3 | 65 | 130 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EEHE | 230 | 3 | 10 | 30-150 | ---
AB509-A…-E1+EEEC_32-..480V_D (AB500DAB032) | D | ICB | Allen Bradley | 140MG-G8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | 0 | Allen Bradley | 592-EEDC | 480 | 3 | 5 | 3.2-16 | ---
AB509-A…-E1+EEEC_32-..600V_D (AB500DAB032) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EEDC | 600 | 3 | 5 | 3.2-16 | ---
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
Size 0-4; use Table 152 for W elements and Table 163 for J elements; Size 5 use Table 347 for W elements and Table 547 for J elements
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(7) = See Table 7 for minimum internal power wiring.
Table 7 - Minimum Internal Power Wiring
1/32in. thick thermoplastic insulation, rated 105C
Wire Code |  | Wire Size
7a |  | 10 AWG
7b |  | 10 AWG
7c |  | 8 AWG
7d |  | 4 AWG
7e |  | 1AWG
7f |  | 250 MCM

## 509 D E3
[16 empty] | Issued: | 2015-12-31
[16 empty] | Last Revised: | 2017-10-10
ID Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage | Number of Phases | SCCR, kA | Full Load Current, A | HP rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP Rating | Enclosure Volume, CU Ft
AB509-A…-E3EC*D_01-..200V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 200 | 3 | --- | 3 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..230V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 230 | 3 | --- | 3 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..480V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..600V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*PC | 600 | 3 | 5 | 0.4-2 | ---
AB509-A…-E3EC*D_02-..200V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..230V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..480V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..600V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..200V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..230V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*7 | 230 | 3 | --- | 7 | 3 | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..480V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..600V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_04-04/2HP-..200V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_04-04/2HP-..230V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_04-04/2HP-..480V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_04-04/2HP-..600V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_05-..200V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_05-..230V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_05-..480V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_05-..600V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*7 | 600 | 3 | --- | 7 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_06-..200V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_06-..230V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_06-..480V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_06-..600V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*7 | 600 | 3 | --- | 7 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 600 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_07-..480V_C (AB500DAB007) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_07-..600V_C (AB500DAB007) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_08-..200V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 200 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_08-..230V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_08-..480V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_08-..600V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_09-1/2HP-..200V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB509-B…-E3EC*D_09-1/2HP-..480V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_09-1/2HP-..600V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_10-..480V_C (AB500DAB010) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-B…-E3EC*D_10-..600V_C (AB500DAB010) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-C…-E3EC*D_11-..200V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..230V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-C…-E3EC*D_11-..600V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
AB509-C…-E3EC*D_12-..480V_C (AB500DAB012) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 480 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_12-..600V_C (AB500DAB012) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_13-..480V_C (AB500DAB013) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_13-..600V_C (AB500DAB013) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 600 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_14-..480V_C (AB500DAB014) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_14-..600V_C (AB500DAB014) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_15-..200V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-G8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..230V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-G8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..480V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_15-..600V_C (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 17 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_16-..200V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..230V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..480V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_16-..600V_C (AB500DAB016) | D | ICB | Allen Bradley | 140MG-J8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 22 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_17-..200V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..230V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..480V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_17-..600V_C (AB500DAB017) | D | ICB | Allen Bradley | 140MG-J8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 27 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_18-..230V_C (AB500DAB018) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_18-..480V_C (AB500DAB018) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_18-..600V_C (AB500DAB018) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_19-..480V_C (AB500DAB019) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_19-..600V_C (AB500DAB019) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 41 | 40 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 600 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_20-..480V_C (AB500DAB020) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_20-..G480V_C (AB500DAB020) | D | ICB | Allen Bradley | 140MG-G8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_20-..600V_C (AB500DAB020) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 600 | 3 | 5 | 18-90 | ---
AB509-E…-E3EC*F_21-..200V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*150 | 200 | 3 | --- | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..230V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*125 | 230 | 3 | --- | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..480V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..I480V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..600V_C (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 32 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..480V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..I480V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..600V_C (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 25 | 52 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..480V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..I480V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..480V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..600V_C (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 62 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..480V_C (AB500DAB024) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..I480V_C (AB500DAB024) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..600V_C (AB500DAB024) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 77 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_25-..600V_C (AB500DAB025) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 99 | 100 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 600 | 3 | 10 | 28-140 | ---
AB509-F…-E3EC*H_26-..200V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-K8*400 | 200 | 3 | --- | 400 | --- | 200 | 3 | 65 | 221 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 200 | 3 | 10 | 221 | 75
|  | OLR | Allen Bradley | 592-EC*HF | 200 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..230V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-K8*400 | 230 | 3 | --- | 400 | --- | 230 | 3 | 65 | 192 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 230 | 3 | 10 | 248 | 100
|  | OLR | Allen Bradley | 592-EC*HF | 230 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..480V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-J8*175 | 480 | 3 | --- | 175 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..I480V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-I8*175 | 480 | 3 | --- | 175 | --- | 480 | 3 | 65 | 96 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_26-..600V_C (AB500DAB026) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..480V_C (AB500DAB027) | D | ICB | Allen Bradley | 140MG-J8*250 | 480 | 3 | --- | 250 | --- | 480 | 3 | 65 | 124 | 100 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..600V_C (AB500DAB027) | D | ICB | Allen Bradley | 140MG-J8*200 | 600 | 3 | --- | 200 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_28-..480V_C (AB500DAB028) | D | ICB | Allen Bradley | 140MG-K8*400 | 480 | 3 | --- | 400 | --- | 480 | 3 | 65 | 240 | 200 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 480 | 3 | 10 | 240 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 480 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_28-..600V_C (AB500DAB028) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-A…-E3EC*D_01-..200V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 200 | 3 | --- | 3 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..230V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 230 | 3 | --- | 3 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_01-..480V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..200V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..230V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_02-..480V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..200V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 200 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..230V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*AC | 230 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_03-..480V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_04-04/2HP-..200V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_04-04/2HP-..230V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_04-04/2HP-..480V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_05-..200V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_05-..230V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 230 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_05-..480V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_06-..200V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OLR | Allen Bradley | 592-EC*BC | 200 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_06-..480V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*AC | 480 | 3 | 5 | 1.0-5 | ---
AB509-A…-E3EC*D_07-..480V_C_2 (AB500DAB007) | D | ICB | Allen Bradley | 140MG-H8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_08-..200V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 200 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_08-..230V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_08-..480V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_09-1/2HP-..230V_C_2 (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Allen Bradley | 592-EC*CC | 230 | 3 | 5 | 5.0-25 | ---
AB509-B…-E3EC*D_09-1/2HP-..480V_C_2 (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-B…-E3EC*D_10-..480V_C_2 (AB500DAB010) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..200V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen Bradley | 592-EC*DC | 200 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..230V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen Bradley | 592-EC*DC | 230 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_11-..480V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-C…-E3EC*D_12-..480V_C_2 (AB500DAB012) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*CC | 480 | 3 | 5 | 5.0-25 | ---
AB509-C…-E3EC*D_13-..480V_C_2 (AB500DAB013) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 65 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-C…-E3EC*D_14-..480V_C_2 (AB500DAB014) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen Bradley | 592-EC*DC | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_15-..200V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..230V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..I200V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 48.3 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..I230V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 42 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_15-..480V_C_2 (AB500DAB015) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_16-..200V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..230V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..I200V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 62.1 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..I230V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 54 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_16-..480V_C_2 (AB500DAB016) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_17-..200V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..230V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..I200V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 65 | 78.2 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 78.2 | 25
|  | OLR | Allen Bradley | 592-EC*ED | 200 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..I230V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 65 | 68 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OLR | Allen Bradley | 592-EC*ED | 230 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_17-..480V_C_2 (AB500DAB017) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_18-..480V_C_2 (AB500DAB018) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 52 | 50
|  | OLR | Allen Bradley | 592-EC*DD | 480 | 3 | 5 | 9.0-45 | ---
AB509-D…-E3EC*E_19-..480V_C_2 (AB500DAB019) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 52 | 40 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-D…-E3EC*E_20-..480V_C_2 (AB500DAB020) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7d | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OLR | Allen Bradley | 592-EC*ED | 480 | 3 | 5 | 18-90 | ---
AB509-E…-E3EC*F_21-..200V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*150 | 200 | 3 | --- | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..230V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*125 | 230 | 3 | --- | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..I200V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*150 | 200 | 3 | --- | 150 | --- | 200 | 3 | 65 | 92 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen Bradley | 592-EC*FE | 200 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..I230V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*125 | 230 | 3 | --- | 125 | --- | 230 | 3 | 65 | 80 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen Bradley | 592-EC*FE | 230 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..480V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_21-..I480V_C_2 (AB500DAB021) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 40 | 30 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..480V_C_2 (AB500DAB022) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_22-..I480V_C_2 (AB500DAB022) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 65 | 65 | 50 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*F | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..480V_C_2 (AB500DAB023) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_23-..I480V_C_2 (AB500DAB023) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 77 | 60 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..480V_C_2 (AB500DAB024) | D | ICB | Allen Bradley | 140MG-J8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-E…-E3EC*F_24-..I480V_C_2 (AB500DAB024) | D | ICB | Allen Bradley | 140MG-I8*150 | 480 | 3 | --- | 150 | --- | 480 | 3 | 65 | 96 | 75 | 3.47 | 1, 5, 7e | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen Bradley | 592-EC*FE | 480 | 3 | 10 | 28-140 | ---
AB509-F…-E3EC*H_26-..600V_C_2 (AB500DAB026) | D | ICB | Allen Bradley | 140MG-J8*150 | 600 | 3 | --- | 150 | --- | 600 | 3 | 25 | 77 | 75 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_27-..600V_C_2 (AB500DAB027) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 99 | 100 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-F…-E3EC*H_28-..600V_C_2 (AB500DAB028) | D | ICB | Allen Bradley | 140MG-J8*250 | 600 | 3 | --- | 250 | --- | 600 | 3 | 25 | 192 | 200 | 6.37 | 1, 5, 7f | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-F | 600 | 3 | 10 | 192 | 200
|  | OLR | Allen Bradley | 592-EC*HF | 600 | 3 | 10 | 60-302 | ---
AB509-A…-E3EC*D_32-..480V_D (AB500DAB032) | D | ICB | Allen Bradley | 140MG-G8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 480 | 3 | 5 | 3.0-15 | ---
AB509-A…-E3EC*D_32-..600V_D (AB500DAB032) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OLR | Allen Bradley | 592-EC*BC | 600 | 3 | 5 | 3.0-15 | ---
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(7) = See Table 7 for minimum internal power wiring.
Table 7 - Minimum Internal Power Wiring
1/32in. thick thermoplastic insulation, rated 105C
Wire Code |  | Wire Size
7a |  | 10 AWG
7b |  | 10 AWG
7c |  | 8 AWG
7d |  | 4 AWG
7e |  | 1AWG
7f |  | 250 MCM

## 509 D E300
[16 empty] | Issued: | 2015-12-31
[16 empty] | Last Revised: | 2017-10-10
ID Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage | Number of Phases | SCCR, kA | Full Load Current, A | HP rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP Rating | Enclosure Volume, Cu Ft
AB509-A…-E300ESM-*-30A-S2_01-..200V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 200 | 3 | --- | 3 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..230V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 230 | 3 | --- | 3 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..480V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..600V_C (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..200V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..230V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..480V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..600V_C (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 1.3 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..200V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..230V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..480V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..600V_C (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 1.7 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..200V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..230V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..480V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..600V_C (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 2.4 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..200V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..230V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..480V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..600V_C (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*7 | 600 | 3 | --- | 7 | --- | 600 | 3 | 25 | 2.7 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..200V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..230V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..480V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-G8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..600V_C (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*7 | 600 | 3 | --- | 7 | --- | 600 | 3 | 25 | 3.9 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_07-..480V_C (AB500DAB007) | D | ICB | Allen Bradley | 140MG-G8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_07-..600V_C (AB500DAB007) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..200V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..230V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..480V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-G8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..600V_C (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*15 | 600 | 3 | --- | 15 | --- | 600 | 3 | 25 | 6.1 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..230V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-G8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..480V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..600V_C (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 9 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_10-..480V_C (AB500DAB010) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_10-..600V_C (AB500DAB010) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 600 | 3 | 5 | 11 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-C…-E300ESM-*-60A-S2_11-..200V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 200 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..230V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..600V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*30 | 600 | 3 | --- | 30 | --- | 600 | 3 | 25 | 11 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_12-..480V_C (AB500DAB012) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_12-..600V_C (AB500DAB012) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 17 | 15 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_13-..480V_C (AB500DAB013) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_13-..600V_C (AB500DAB013) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 22 | 20 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_14-..480V_C (AB500DAB014) | D | ICB | Allen Bradley | 140MG-G8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_14-..600V_C (AB500DAB014) | D | ICB | Allen Bradley | 140MG-H8*50 | 600 | 3 | --- | 50 | --- | 600 | 3 | 25 | 27 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 600 | 3 | 5 | 27 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 600 | 3 | 5 | 6.0-45 | ---
AB509-A…-E300ESM-*-30A-S2_01-..200V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 200 | 3 | --- | 3 | --- | 200 | 3 | 65 | 2.5 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..230V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 230 | 3 | --- | 3 | --- | 230 | 3 | 65 | 2.2 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_01-..480V_C_2 (AB500DAB001) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..200V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 3.7 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..230V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 3.2 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_02-..480V_C_2 (AB500DAB002) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.6 | 0.75 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..200V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*7 | 200 | 3 | --- | 7 | --- | 200 | 3 | 65 | 4.8 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..230V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*7 | 230 | 3 | --- | 7 | --- | 230 | 3 | 65 | 4.2 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_03-..480V_C_2 (AB500DAB003) | D | ICB | Allen Bradley | 140MG-H8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 2.1 | 1 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..200V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 6.9 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..230V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_04-04/2HP-..480V_C_2 (AB500DAB004) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3 | 1.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..200V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*15 | 200 | 3 | --- | 15 | --- | 200 | 3 | 65 | 7.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..230V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*15 | 230 | 3 | --- | 15 | --- | 230 | 3 | 65 | 6.8 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_05-..480V_C_2 (AB500DAB005) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 3.4 | 2 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..200V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 11 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 200 | 3 | 5 | 11 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..230V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 9.6 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 230 | 3 | 5 | 9.6 | 3
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_06-..480V_C_2 (AB500DAB006) | D | ICB | Allen Bradley | 140MG-H8*7 | 480 | 3 | --- | 7 | --- | 480 | 3 | 65 | 4.8 | 3 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_07-..480V_C_2 (AB500DAB007) | D | ICB | Allen Bradley | 140MG-H8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..200V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 17.5 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..230V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 15.2 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_08-..480V_C_2 (AB500DAB008) | D | ICB | Allen Bradley | 140MG-H8*15 | 480 | 3 | --- | 15 | --- | 480 | 3 | 65 | 7.6 | 5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..200V_C_2 (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 200 | 3 | --- | 30 | --- | 200 | 3 | 65 | 25.3 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 200 | 3 | 5 | 25.3 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 200 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..230V_C_2 (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 230 | 3 | --- | 30 | --- | 230 | 3 | 65 | 22 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 230 | 3 | 5 | 22 | 7.5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 230 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_09-1/2HP-..480V_C_2 (AB500DAB009) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 11 | 7.5 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-B…-E300ESM-*-30A-S2_10-..480V_C_2 (AB500DAB010) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7b | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-B | 480 | 3 | 5 | 14 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-C…-E300ESM-*-60A-S2_11-..200V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*50 | 200 | 3 | --- | 50 | --- | 200 | 3 | 65 | 32.2 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 200 | 3 | 5 | 32.2 | 10
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 200 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..230V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*50 | 230 | 3 | --- | 50 | --- | 230 | 3 | 65 | 28 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 230 | 3 | 5 | 42 | 15
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 230 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_11-..480V_C_2 (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*30 | 480 | 3 | --- | 30 | --- | 480 | 3 | 65 | 14 | 10 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_12-..480V_C_2 (AB500DAB012) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 21 | 15 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_13-..480V_C_2 (AB500DAB013) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 27 | 20 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-C…-E300ESM-*-60A-S2_14-..480V_C_2 (AB500DAB014) | D | ICB | Allen Bradley | 140MG-H8*50 | 480 | 3 | --- | 50 | --- | 480 | 3 | 65 | 34 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-C | 480 | 3 | 5 | 34 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-60A-S2 | 480 | 3 | 5 | 6.0-45 | ---
AB509-A…-E300ESM-*-30A-S2_28-..480V_D (AB500DAB028) | D | ICB | Allen Bradley | 140MG-G8*3 | 480 | 3 | --- | 3 | --- | 480 | 3 | 65 | 1.1 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 480 | 3 | 5 | 7.6 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 480 | 3 | 5 | 0.5-27 | ---
AB509-A…-E300ESM-*-30A-S2_28-..600V_D (AB500DAB028) | D | ICB | Allen Bradley | 140MG-H8*3 | 600 | 3 | --- | 3 | --- | 600 | 3 | 25 | 0.9 | 0.5 | 1.25 | 1, 5, 7a | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-A | 600 | 3 | 5 | 6.1 | 5
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-30A-S2 | 600 | 3 | 5 | 0.5-27 | ---
AB509-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..I200V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..I230V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..I480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-G8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-H8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..200V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-J8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..230V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-J8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..I200V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*100 | 200 | 3 | --- | 100 | --- | 200 | 3 | 5 | 62.1 | 25 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 200 | 3 | 5 | 62.1 | 25
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 200 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..I230V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*100 | 230 | 3 | --- | 100 | --- | 230 | 3 | 5 | 80 | 30 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 230 | 3 | 5 | 80 | 30
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 230 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-J8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..I480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*100 | 480 | 3 | --- | 100 | --- | 480 | 3 | 5 | 65 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 480 | 3 | 5 | 65 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 480 | 3 | 5 | 10.0-90.0 | ---
AB509-D…-E300ESM-*-100A-S3_11-..600V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-J8*100 | 600 | 3 | --- | 100 | --- | 600 | 3 | 5 | 52 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-D | 600 | 3 | 5 | 52 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-100A-S3 | 600 | 3 | 5 | 10.0-90.0 | ---
AB509-E…-E300ESM-*-200A-S4_11-..200V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-J8*175 | 200 | 3 | --- | 175 | --- | 200 | 3 | 22 | 120 | 40 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 200 | 3 | 5 | 120 | 40
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 200 | 3 | 5 | 20-135 | ---
AB509-E…-E300ESM-*-200A-S4_11-..230V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-J8*175 | 230 | 3 | --- | 175 | --- | 230 | 3 | 22 | 139 | 50 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 230 | 3 | 5 | 139 | 50
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 230 | 3 | 5 | 20-135 | ---
AB509-E…-E300ESM-*-200A-S4_11-..480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-J8*175 | 480 | 3 | --- | 175 | --- | 480 | 3 | 22 | 124 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 5 | 124 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 480 | 3 | 5 | 20-135 | ---
AB509-E…-E300ESM-*-200A-S4_11-..I480V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-I8*175 | 480 | 3 | --- | 175 | --- | 480 | 3 | 22 | 124 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 480 | 3 | 5 | 124 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 480 | 3 | 5 | 20-135 | ---
AB509-E…-E300ESM-*-200A-S4_11-..600V_C (AB500DAB011) | D | ICB | Allen Bradley | 140MG-J8*175 | 600 | 3 | --- | 175 | --- | 600 | 3 | 14 | 99 | 100 | 1.25 | 1, 5, 7c | E125316 dated 2001-09-12
|  | MC | Allen Bradley | 509-E | 600 | 3 | 5 | 99 | 100
|  | OL ACC (COMM) | Allen Bradley | 193-ECM* | --- | --- | --- | --- | ---
|  | OL ACC (CONT) | Allen Bradley | 193-EIO* | --- | --- | --- | --- | ---
|  | OLR | Allen Bradley | 592-ESM-*-200A-S4 | 600 | 3 | 5 | 20-135 | ---
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(7) = See Table 7 for minimum internal power wiring.
Table 7 - Minimum Internal Power Wiring
1/32in. thick thermoplastic insulation, rated 105C
Wire Code |  | Wire Size
7a |  | 10 AWG
7b |  | 10 AWG
7c |  | 8 AWG
7d |  | 4 AWG
7e |  | 1AWG
7f |  | 250 MCM

## Const. F w MPCB (303H-307H)
[15 empty] | Issued: | 2021-01-19
ID Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage | Number of Phases | SCCR, kA | Full Load Current, A | HP rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP Rating | Enclosure Volume, Cu. - In.
AB303H-CN***CA16-480… | F | MSP | Allen Bradley | 140M-C2E-A16 | 480Y/277V | 3 | 65 | 0.16 |  | 480Y/277 | 3 | 65 | 0.16 FLA/0.96 LRA | - | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***CA16-600… | F | MSP | Allen Bradley | 140M-C2E-A16 | 600Y/347V | 3 | 47 | 0.16 |  | 600Y/347 | 3 | 47 | 0.16 FLA/0.96 LRA | - | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***CA25-480… | F | MSP | Allen Bradley | 140M-C2E-A25 | 480Y/277V | 3 | 65 | 0.25 |  | 480Y/277 | 3 | 65 | 0.25 FLA/1.5 LRA | - | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***CA25-600… | F | MSP | Allen Bradley | 140M-C2E-A25 | 600Y/347V | 3 | 47 | 0.25 |  | 600Y/347 | 3 | 47 | 0.25 FLA/1.5 LRA | - | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***CA40-480… | F | MSP | Allen Bradley | 140M-C2E-A40 | 480Y/277V | 3 | 65 | 0.4 |  | 480Y/277 | 3 | 65 | 0.4 FLA/2.4 LRA | - | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***CA40-600… | F | MSP | Allen Bradley | 140M-C2E-A40 | 600Y/347V | 3 | 47 | 0.4 |  | 600Y/347 | 3 | 47 | 0.4 FLA/2.4 LRA | - | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***CA63-480… | F | MSP | Allen Bradley | 140M-C2E-A63 | 480Y/277V | 3 | 65 | 0.63 |  | 480Y/277 | 3 | 65 | 0.63 FLA/3.78 LRA | - | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***CA63-600… | F | MSP | Allen Bradley | 140M-C2E-A63 | 600Y/347V | 3 | 47 | 0.63 |  | 600Y/347 | 3 | 47 | 0.63 FLA/3.78 LRA | - | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***CB10-480… | F | MSP | Allen Bradley | 140M-C2E-B10 | 480Y/277V | 3 | 65 | 1 | 1/2 | 480Y/277 | 3 | 65 | 1.0 | 0.5 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***CB10-600… | F | MSP | Allen Bradley | 140M-C2E-B10 | 600Y/347V | 3 | 47 | 1 | 3/4 | 600Y/347 | 3 | 47 | 1.0 | 0.75 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***CB16-480… | F | MSP | Allen Bradley | 140M-C2E-B16 | 480Y/277V | 3 | 65 | 1.6 | 1 | 480Y/277 | 3 | 65 | 1.6 | 1 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***CB16-600… | F | MSP | Allen Bradley | 140M-C2E-B16 | 600Y/347V | 3 | 47 | 1.6 | 1 | 600Y/347 | 3 | 47 | 1.6 | 1 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***CB25-480… | F | MSP | Allen Bradley | 140M-C2E-B25 | 480Y/277V | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***CB25-600… | F | MSP | Allen Bradley | 140M-C2E-B25 | 600Y/347V | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 10 | 2.5 | 2 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***CB40-480… | F | MSP | Allen Bradley | 140M-C2E-B40 | 480Y/277V | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4.0 | 3 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***CB40-600… | F | MSP | Allen Bradley | 140M-C2E-B40 | 600Y/347V | 3 | 25 | 4 | 3 | 600Y/347 | 3 | 10 | 3.9 | 3 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***CB63-480… | F | MSP | Allen Bradley | 140M-C2E-B63 | 480Y/277V | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 6.3 | 5 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***CC10-480… | F | MSP | Allen Bradley | 140M-C2E-C10 | 480Y/277V | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***CC16-480… | F | MSP | Allen Bradley | 140M-C2E-C16 | 480Y/277V | 3 | 30 | 16 | 10 | 480Y/277 | 3 | 30 | 7.6 | 5 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***DB25-480… | F | MSP | Allen Bradley | 140M-D8E-B25 | 480Y/277V | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***DB25-600… | F | MSP | Allen Bradley | 140M-D8E-B25 | 600Y/347 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 10 | 2.5 | 2 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***DB40-480… | F | MSP | Allen Bradley | 140M-D8E-B40 | 480Y/277V | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4.0 | 3 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***DB40-600… | F | MSP | Allen Bradley | 140M-D8E-B40 | 600Y/347 | 3 | 30 | 4 | 3 | 600Y/347 | 3 | 10 | 3.9 | 3 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***DB63-480… | F | MSP | Allen Bradley | 140M-D8E-B63 | 480Y/277V | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 6.3 | 5 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***DB63-600… | F | MSP | Allen Bradley | 140M-D8E-B63 | 600Y/347 | 3 | 30 | 6.3 | 5 | 600Y/347 | 3 | 10 | 6.1 | 5 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***DC10-480… | F | MSP | Allen Bradley | 140M-D8E-C10 | 480Y/277V | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***DC10-600… | F | MSP | Allen Bradley | 140M-D8E-C10 | 600Y/347 | 3 | 30 | 10 | 10 | 600Y/347 | 3 | 30 | 6.1 | 5 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***DC16-480… | F | MSP | Allen Bradley | 140M-D8E-C16 | 480Y/277V | 3 | 65 | 16 | 10 | 480Y/277 | 3 | 65 | 7.6 | 5 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB303H-CN***DC16-600… | F | MSP | Allen Bradley | 140M-D8E-C16 | 600Y/347 | 3 | 30 | 16 | 10 | 600Y/347 | 3 | 30 | 6.1 | 5 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 300-AO*93 Series C* | 600V | 3 | 5 | 16 | 5
AB307H-CN***CA16-480… | F | MSP | Allen Bradley | 140M-C2E-A16 | 480Y/277V | 3 | 65 | 0.16 |  | 480Y/277 | 3 | 65 | 0.16 FLA/0.96 LRA | - | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***CA16-600… | F | MSP | Allen Bradley | 140M-C2E-A16 | 600Y/347 | 3 | 47 | 0.16 |  | 600Y/347 | 3 | 47 | 0.16 FLA/0.96 LRA | - | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***CA25-480… | F | MSP | Allen Bradley | 140M-C2E-A25 | 480Y/277V | 3 | 65 | 0.25 |  | 480Y/277 | 3 | 65 | 0.25 FLA/1.5 LRA | - | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***CA25-600… | F | MSP | Allen Bradley | 140M-C2E-A25 | 600Y/347 | 3 | 47 | 0.25 |  | 600Y/347 | 3 | 47 | 0.25 FLA/1.5 LRA | - | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***CA40-480… | F | MSP | Allen Bradley | 140M-C2E-A40 | 480Y/277V | 3 | 65 | 0.4 |  | 480Y/277 | 3 | 65 | 0.4 FLA/2.4 LRA | - | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***CA40-600… | F | MSP | Allen Bradley | 140M-C2E-A40 | 600Y/347 | 3 | 47 | 0.4 |  | 600Y/347 | 3 | 47 | 0.4 FLA/2.4 LRA | - | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***CA63-480… | F | MSP | Allen Bradley | 140M-C2E-A63 | 480Y/277V | 3 | 65 | 0.63 |  | 480Y/277 | 3 | 65 | 0.63 FLA/3.78 LRA | - | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***CA63-600… | F | MSP | Allen Bradley | 140M-C2E-A63 | 600Y/347 | 3 | 47 | 0.63 |  | 600Y/347 | 3 | 47 | 0.63 FLA/3.78 LRA | - | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***CB10-480… | F | MSP | Allen Bradley | 140M-C2E-B10 | 480Y/277V | 3 | 65 | 1 | 1/2 | 480Y/277 | 3 | 65 | 1.0 | 0.5 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***CB10-600… | F | MSP | Allen Bradley | 140M-C2E-B10 | 600Y/347 | 3 | 47 | 1 | 3/4 | 600Y/347 | 3 | 47 | 1.0 | 0.75 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***CB16-480… | F | MSP | Allen Bradley | 140M-C2E-B16 | 480Y/277V | 3 | 65 | 1.6 | 1 | 480Y/277 | 3 | 65 | 1.6 | 1 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***CB16-600… | F | MSP | Allen Bradley | 140M-C2E-B16 | 600Y/347 | 3 | 47 | 1.6 | 1 | 600Y/347 | 3 | 47 | 1.6 | 1 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***CB25-480… | F | MSP | Allen Bradley | 140M-C2E-B25 | 480Y/277V | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***CB25-600… | F | MSP | Allen Bradley | 140M-C2E-B25 | 600Y/347 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 10 | 2.5 | 2 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***CB40-480… | F | MSP | Allen Bradley | 140M-C2E-B40 | 480Y/277V | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4.0 | 3 | 655 | 1,5,6 | E125316, 2021-01-19
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***CB40-600… | F | MSP | Allen Bradley | 140M-C2E-B40 | 600Y/347 | 3 | 25 | 4 | 3 | 600Y/347 | 3 | 10 | 3.9 | 3 | 655 | 1,5,6 | E125316 dated xxx
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***CB63-480… | F | MSP | Allen Bradley | 140M-C2E-B63 | 480Y/277V | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 6.3 | 5 | 655 | 1,5,6 | E125316 dated xxx
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***CC10-480… | F | MSP | Allen Bradley | 140M-C2E-C10 | 480Y/277V | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 655 | 1,5,6 | E125316 dated xxx
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***CC16-480… | F | MSP | Allen Bradley | 140M-C2E-C16 | 480Y/277V | 3 | 30 | 16 | 10 | 480Y/277 | 3 | 30 | 7.6 | 5 | 655 | 1,5,6 | E125316 dated xxx
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-C-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***DB25-480… | F | MSP | Allen Bradley | 140M-D8E-B25 | 480Y/277V | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 655 | 1,5,6 | E125316 dated xxx
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***DB25-600… | F | MSP | Allen Bradley | 140M-D8E-B25 | 600Y/347 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 10 | 2.5 | 2 | 655 | 1,5,6 | E125316 dated xxx
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***DB40-480… | F | MSP | Allen Bradley | 140M-D8E-B40 | 480Y/277V | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4.0 | 3 | 655 | 1,5,6 | E125316 dated xxx
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***DB40-600… | F | MSP | Allen Bradley | 140M-D8E-B40 | 600Y/347 | 3 | 30 | 4 | 3 | 600Y/347 | 3 | 10 | 3.9 | 3 | 655 | 1,5,6 | E125316 dated xxx
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***DB63-480… | F | MSP | Allen Bradley | 140M-D8E-B63 | 480Y/277V | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 6.3 | 5 | 655 | 1,5,6 | E125316 dated xxx
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***DB63-600… | F | MSP | Allen Bradley | 140M-D8E-B63 | 600Y/347 | 3 | 30 | 6.3 | 5 | 600Y/347 | 3 | 10 | 6.1 | 5 | 655 | 1,5,6 | E125316 dated xxx
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***DC10-480… | F | MSP | Allen Bradley | 140M-D8E-C10 | 480Y/277V | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 655 | 1,5,6 | E125316 dated xxx
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 16 | 5
AB307H-CN***DC10-600… | F | MSP | Allen Bradley | 140M-D8E-C10 | 600Y/347 | 3 | 30 | 10 | 10 | 600Y/347 | 3 | 30 | 6.1 | 5 | 655 | 1,5,6 | E125316 dated xxx
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 18 | 5
AB307H-CN***DC16-480… | F | MSP | Allen Bradley | 140M-D8E-C16 | 480Y/277V | 3 | 65 | 16 | 10 | 480Y/277 | 3 | 65 | 7.6 | 5 | 655 | 1,5,6 | E125316 dated xxx
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 18 | 5
AB307H-CN***DC16-600… | F | MSP | Allen Bradley | 140M-D8E-C16 | 600Y/347 | 3 | 30 | 16 | 10 | 600Y/347 | 3 | 30 | 6.1 | 5 | 655 | 1,5,6 | E125316 dated xxx
|  | ACC (Terminal Adapt.) | Allen Bradley | 140M-C-TE1 | 600V | 3 | - | - | -
|  | ACC (Connect Mod.) | Allen Bradley | 140M-D-PEC23 | 600V | 3 | - | - | -
|  | MC | Allen Bradley | 305-AO*23 | 600V | 3 | 5 | 18 | 5
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = In lieu of the following R/C (NKCR2) Connection Modules the following Jumper wires may be used for the following Combination Motor Controllers.
|  | Connection Modules |  | Jumper Wire
|  | 140M-C-PEC23 |  | 105°C, 600V, 14, 12, or 10 AWG based on the ampacity of the device.
|  | 140M-D-PEC23 |  | 105°C, 600V, 14, 12, or 10 AWG based on the ampacity of the device.

## MCP 513 Series 4 E100
[23 empty] | Issued: | 2021-04-30
Database Identification Number | [B2] Listed Combination Motor Controller Information | [7 empty] | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability
| Listing Report Information |  |  |  |  | Enclosure or Unit Dimensions
| UL File Number | Report Issue Date YYYY-MM-DD | Volume / Section (Vol#).(Sec#) | Model Number or Product Style/ Designation | Product Description on Page/Figure/Ill. | Enclosure or Unit Height, inches | Width, inches | Depth, inches |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage | Number of Phases | SCCR, kA | Full Load Current, A | HP rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP Rating | Enclosure Volume, in3
AB500F-A…-B30+1EFCC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-B30 | 480 | 3 | -- | 3 | -- | 480 | 3 | 65 | 2.1 | 1 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFCC | 480 | 3 | 5 | 1 - 5 | --
AB500F-A…-B30+1EFCC..575V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-B30 | 600 | 3 | -- | 3 | -- | 600 | 3 | 25 | 1.7 | 1 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFCC | 600 | 3 | 5 | 1 - 5 | --
AB500F-A…-B70+1EFCC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-B70 | 200 | 3 | -- | 7 | -- | 200 | 3 | 65 | 2.5 | 0.5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFCC | 200 | 3 | 5 | 1 - 5 | --
AB500F-A…-B70+1EFCC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-B70 | 230 | 3 | -- | 7 | -- | 230 | 3 | 65 | 3.2 | 0.75 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFCC | 230 | 3 | 5 | 1 - 5 | --
AB500F-A…-B70+1EFCC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-B70 | 480 | 3 | -- | 7 | -- | 480 | 3 | 65 | 3.4 | 2 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFCC | 480 | 3 | 5 | 1 - 5 | --
AB500F-A…-B70+1EFCC..575V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-B70 | 600 | 3 | -- | 7 | -- | 600 | 3 | 25 | 3.9 | 3 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFCC | 600 | 3 | 5 | 1 - 5 | --
AB500F-A…-C15+1EFCC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 | 1 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFCC | 200 | 3 | 5 | 1 - 5 | --
AB500F-A…-C15+1EFCC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 | 1 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFCC | 230 | 3 | 5 | 1 - 5 | --
AB500F-A…-C15+1EFCC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 | 3 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFCC | 480 | 3 | 5 | 1 - 5 | --
AB500F-A…-C15+1EFCC..575V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 3.9 | 3 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFCC | 600 | 3 | 5 | 1 - 5 | --
AB500F-A…-B70+1EFDC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-B70 | 230 | 3 | -- | 7 | -- | 230 | 3 | 65 | 3.2 | 0.75 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-B70+1EFDC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-B70 | 480 | 3 | -- | 7 | -- | 480 | 3 | 65 | 3.4 | 2 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-A…-B70+1EFDC..575V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-B70 | 600 | 3 | -- | 7 | -- | 600 | 3 | 25 | 3.9 | 3 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-A…-C15+1EFDC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 | 1 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-C15+1EFDC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 6 | 1.5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-C15+1EFDC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 7.6 | 5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-A…-C15+1EFDC..575V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 6.1 | 5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-A…-C30+1EFDC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-C30+1EFDC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 9.6 | 3 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-C30+1EFDC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 7.6 | 5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-A…-C15+1EFEC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 6 | 1.5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-A…-C15+1EFEC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 7.6 | 5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-A…-C15+1EFEC..575V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 6.1 | 5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 600 | 3 | 5 | 6.1 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 600 | 3 | 5 | 5.4-27 | ---
AB500F-A…-C30+1EFEC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 200 | 3 | 5 | 5.4-27 | ---
AB500F-A…-C30+1EFEC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 9.6 | 3 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-A…-C30+1EFEC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 7.6 | 5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-A…-GB30+1EFCC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-B30 | 480 | 3 | -- | 3 | -- | 480 | 3 | 65 | 2.1 | 1 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFCC | 480 | 3 | 5 | 1 - 5 | --
AB500F-A…-GB70+1EFCC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-B70 | 200 | 3 | -- | 7 | -- | 200 | 3 | 65 | 2.5 | 0.5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFCC | 200 | 3 | 5 | 1 - 5 | --
AB500F-A…-GB70+1EFCC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-B70 | 230 | 3 | -- | 7 | -- | 230 | 3 | 65 | 3.2 | 0.75 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFCC | 230 | 3 | 5 | 1 - 5 | --
AB500F-A…-GB70+1EFCC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-B70 | 480 | 3 | -- | 7 | -- | 480 | 3 | 65 | 3.4 | 2 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFCC | 480 | 3 | 5 | 1 - 5 | --
AB500F-A…-GC15+1EFCC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 | 1 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFCC | 200 | 3 | 5 | 1 - 5 | --
AB500F-A…-GC15+1EFCC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 | 1 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFCC | 230 | 3 | 5 | 1 - 5 | --
AB500F-A…-GC15+1EFCC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 | 3 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFCC | 480 | 3 | 5 | 1 - 5 | --
AB500F-A…-GB70+1EFDC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-B70 | 230 | 3 | -- | 7 | -- | 230 | 3 | 65 | 3.2 | 0.75 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-GB70+1EFDC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-B70 | 480 | 3 | -- | 7 | -- | 480 | 3 | 65 | 3.4 | 2 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-A…-GC15+1EFDC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 | 1 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-A…-GC15+1EFDC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 6 | 1.5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-A…-GC15+1EFDC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 7.6 | 5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-A…-GC30+1EFDC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 7.6 | 5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-A…-GC15+1EFEC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 6 | 1.5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-A…-GC15+1EFEC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 7.6 | 5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-A…-GC30+1EFEC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 7.6 | 5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-A | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-B…-C30+1EFEC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 200 | 3 | 5 | 5.4-27 | ---
AB500F-B…-C30+1EFEC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 230 | 3 | 5 | 22 | 7.5
AB500F-B…-C30+1EFEC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | 5 | 22 | 7.5 | 480 | 3 | 65 | 14 | 10 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-B…-C30+1EFEC..575V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 11 | 10 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 600 | 3 | 5 | 5.4-27 | ---
AB500F-B…-GC30+1EFEC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 200 | 3 | 5 | 5.4-27 | ---
AB500F-B…-GC30+1EFEC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-B…-GC30+1EFEC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 14 | 10 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-B…-GC30+1EFDC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-B…-GC30+1EFDC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 15.2 | 5 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-B…-GC30+1EFDC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 14 | 10 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-C30+1EFDC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-B…-C30+1EFDC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 15.2 | 5 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-B…-C30+1EFDC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 14 | 10 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-B…-C30+1EFDC..575V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 11 | 10 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-B…-GC30+1EFFC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 200 | 3 | 5 | 11 - 55 | ---
AB500F-B…-GC30+1EFFC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 230 | 3 | 5 | 11 - 55 | ---
AB500F-B…-GC30+1EFFC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 14 | 10 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 480 | 3 | 5 | 11 - 55 | ---
AB500F-B…-C30+1EFFC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 200 | 3 | 5 | 11 - 55 | ---
AB500F-B…-C30+1EFFC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 230 | 3 | 5 | 11 - 55 | ---
AB500F-B…-C30+1EFFC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 14 | 10 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 480 | 3 | 5 | 11 - 55 | ---
AB500F-B…-C30+1EFFC..575V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 11 | 10 | 2310 | 1,5,7b
[10 empty] | MC | Allen-Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 600 | 3 | 5 | 11 - 55 | ---
AB500F-B…-GC30+1EFFC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 200 | 3 | 5 | 11 - 55 | ---
AB500F-B…-GC30+1EFFC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 15.2 | 5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 230 | 3 | 5 | 11 - 55 | ---
AB500F-B…-GC30+1EFFC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 14 | 10 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 480 | 3 | 5 | 11 - 55 | ---
AB500F-B…-C30+1EFFC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-B | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 200 | 3 | 5 | 11 - 55 | ---
AB500F-B…-C30+1EFFC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 15.2 | 5 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-B | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 230 | 3 | 5 | 11 - 55 | ---
AB500F-B…-C30+1EFFC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 14 | 10 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-B | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 480 | 3 | 5 | 11 - 55 | ---
AB500F-B…-C30+1EFFC..575V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 11 | 10 | 2310 | 1,5,7a
[10 empty] | MC | Allen-Bradley | 500F-B | 600 | 3 | 5 | 11 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 600 | 3 | 5 | 11 - 55 | ---
AB500F-C…-C50+1EFEC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 | 7.5 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 200 | 3 | 5 | 5.4-27 | ---
AB500F-C…-C50+1EFEC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-C…-C50+1EFEC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 | 20 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-C50+1EFEC..575V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 27 | 25 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 600 | 3 | 5 | 5.4-27 | ---
AB500F-C…-GC50+1EFEC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 | 7.5 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 200 | 3 | 5 | 5.4-27 | ---
AB500F-C…-GC50+1EFEC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-C…-GC50+1EFEC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 | 20 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 480 | 3 | 5 | 5.4-27 | ---
AB500F-C…-GC50+1EFDC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-C…-GC50+1EFDC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 15.2 | 5 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-C…-GC50+1EFDC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 14 | 10 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-C…-C50+1EFDC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 200 | 3 | 5 | 3.2-16 | ---
AB500F-C…-C50+1EFDC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 15.2 | 5 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 230 | 3 | 5 | 3.2-16 | ---
AB500F-C…-C50+1EFDC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 14 | 10 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 480 | 3 | 5 | 3.2-16 | ---
AB500F-C…-C50+1EFDC..575V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 11 | 10 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 592-1EFDC | 600 | 3 | 5 | 3.2-16 | ---
AB500F-C…-GC50+1EFFC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 | 10 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 200 | 3 | 5 | 11 - 55 | ---
AB500F-C…-GC50+1EFFC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 | 10 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 230 | 3 | 5 | 11 - 55 | ---
AB500F-C…-GC50+1EFFC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 34 | 25 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 480 | 3 | 5 | 11 - 55 | ---
AB500F-C…-C50+1EFFC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 | 10 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 200 | 3 | 5 | 11 - 55 | ---
AB500F-C…-C50+1EFFC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 | 10 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 230 | 3 | 5 | 11 - 55 | ---
AB500F-C…-C50+1EFFC..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 34 | 25 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 480 | 3 | 5 | 11 - 55 | ---
AB500F-C…-C50+1EFFC..575V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 27 | 25 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 600 | 3 | 5 | 11 - 55 | ---
AB500F-C…-C70+1EFEC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 25.3 | 7.5 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 200 | 3 | 5 | 5.4-27 | ---
AB500F-C…-C70+1EFEC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-C…-GC70+1EFEC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 25.3 | 7.5 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 200 | 3 | 5 | 5.4-27 | ---
AB500F-C…-GC70+1EFEC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-C…-GC70+1EFFC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 32.2 | 10 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 200 | 3 | 5 | 11 - 55 | ---
AB500F-C…-GC70+1EFFC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 28 | 10 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 230 | 3 | 5 | 11 - 55 | ---
AB500F-C…-C70+1EFFC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 32.2 | 10 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 200 | 3 | 5 | 11 - 55 | ---
AB500F-C…-C70+1EFFC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 28 | 10 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 230 | 3 | 5 | 11 - 55 | ---
AB500F-C…-D10+1EFEC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 25.3 | 7.5 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 200 | 3 | 5 | 5.4-27 | ---
AB500F-C…-D10+1EFEC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-C…-GD10+1EFEC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 25.3 | 7.5 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 200 | 3 | 5 | 5.4-27 | ---
AB500F-C…-GD10+1EFEC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 592-1EFEC | 230 | 3 | 5 | 5.4-27 | ---
AB500F-C…-GD10+1EFFC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 32.2 | 10 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 200 | 3 | 5 | 11 - 55 | ---
AB500F-C…-GD10+1EFFC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 28 | 10 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 230 | 3 | 5 | 11 - 55 | ---
AB500F-C…-D10+1EFFC..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 32.2 | 10 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 200 | 3 | 5 | 11 - 55 | ---
AB500F-C…-D10+1EFFC..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 28 | 10 | 2310 | 1,5,7c
[10 empty] | MC | Allen-Bradley | 500F-C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 592-1EFFC | 230 | 3 | 5 | 11 - 55 | ---
AB500F-D…-D10+1EFGD..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 30 | 20 | 10 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 78.2 | 25 | 6000 | 1,5,7d
[10 empty] | MC | Allen-Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 592-1EFGD | 200 | 3 | 5 | 20 - 100 | --
AB500F-D…-D10+1EFGD..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 30 | 20 | 10 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 80 | 30 | 6000 | 1,5,7d
[10 empty] | MC | Allen-Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 592-1EFGD | 230 | 3 | 5 | 20 - 100 | --
AB500F-D…-D10+1EFGD..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 30 | 20 | 10 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 480 | 3 | -- | 100 | -- | 480 | 3 | 65 | 65 | 50 | 6000 | 1,5,7d
[10 empty] | MC | Allen-Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 592-1EFGD | 480 | 3 | 5 | 20 - 100 | --
AB500F-D…-D10+1EFGD..575V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 30 | 20 | 10 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 600 | 3 | -- | 100 | -- | 600 | 3 | 25 | 52 | 50 | 6000 | 1,5,7d
[10 empty] | MC | Allen-Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 592-1EFGD | 600 | 3 | 5 | 20 - 100 | --
AB500F-D…-GD10+1EFGD..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 30 | 20 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 78.2 | 25 | 6000 | 1,5,7d
[10 empty] | MC | Allen-Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 592-1EFGD | 200 | 3 | 5 | 20 - 100 | --
AB500F-D…-GD10+1EFGD..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 30 | 20 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 80 | 30 | 6000 | 1,5,7d
[10 empty] | MC | Allen-Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 592-1EFGD | 230 | 3 | 5 | 20 - 100 | --
AB500F-D…-GD10+1EFGD..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 30 | 20 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 480 | 3 | -- | 100 | -- | 480 | 3 | 65 | 65 | 50 | 6000 | 1,5,7d
[10 empty] | MC | Allen-Bradley | 500F-D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 592-1EFGD | 480 | 3 | 5 | 20 - 100 | --
AB500F-D…-D12+1EFGD..200V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 30 | 20 | 10 | D | ICB | Allen-Bradley | 140MG-I8P-D15 | 200 | 3 | -- | 150 | -- | 200 | 3 | 65 | 78.2 | 25 | 6000 | 1,5,7d
[10 empty] | MC | Allen-Bradley | 500F-D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 592-1EFGD | 200 | 3 | 5 | 20 - 100 | --
AB500F-D…-D12+1EFGD..230V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 30 | 20 | 10 | D | ICB | Allen-Bradley | 140MG-I8P-D15 | 230 | 3 | -- | 150 | -- | 230 | 3 | 65 | 80 | 30 | 6000 | 1,5,7d
[10 empty] | MC | Allen-Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 592-1EFGD | 230 | 3 | 5 | 20 - 100 | --
AB500F-D…-D12+1EFGD..460V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 30 | 20 | 10 | D | ICB | Allen-Bradley | 140MG-J8P-D15 | 230 | 3 | -- | 150 | -- | 230 | 3 | 65 | 80 | 30 | 6000 | 1,5,7d
[10 empty] | MC | Allen-Bradley | 500F-D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 592-1EFGD | 230 | 3 | 5 | 20 - 100 | --
AB500F-D…-D12+1EFGD..575V | E125316 | 2001-09-12 | Vol. 4/Sec. 1 |  |  | 30 | 20 | 10 | D | ICB | Allen-Bradley | 140MG-J8P-D15 | 600 | 3 | -- | 150 | -- | 600 | 3 | 25 | 52 | 50 | 6000 | 1,5,7d
[10 empty] | MC | Allen-Bradley | 500F-D | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 592-1EFGD | 600 | 3 | 5 | 20 - 100 | --
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(7) = See Table 7 for minimum internal power wiring.
Table 7 - Minimum Internal Power Wiring
1/32in. thick thermoplastic insulation, rated 105C
Wire Code | [9 empty] | Wire Size
7a | [9 empty] | 10 AWG
7b | [9 empty] | 10 AWG
7c | [9 empty] | 8 AWG
7d | [9 empty] | 4 AWG
7e | [9 empty] | 1AWG
7f | [9 empty] | 250 MCM

## MPC 313 E100 Series 1
[23 empty] | Issued: | 2021-06-18
Note Columes N-R will be hidden before posting
Database Identification Number | [B2] Listed Combination Motor Controller Information | [7 empty] | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability
| Listing Report Information |  |  |  |  | Enclosure or Unit Dimensions
| UL File Number | Report Issue Date YYYY-MM-DD | Volume / Section (Vol#).(Sec#) | Model Number or Product Style/ Designation | Product Description on Page/Figure/Ill. | Enclosure or Unit Height, inches | Width, inches | Depth, inches |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP rating | Enclosure Volume, CU inches
AB300-A…-GC15+1EEEB..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 200 | 3 | 5 | 5.4-27 | --
AB300-A…-GC15+1EEEB..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 230 | 3 | 5 | 5.4-27 | --
AB300-A…-C15+1EEEB..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 7.6 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 480 | 3 | 5 | 5.4-27 | --
AB300-A…-C15+1EEEB..575V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 6.1 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 600 | 3 | 5 | 6.1 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 600 | 3 | 5 | 5.4-27 | --
AB300-A…-GC15+1EEEB..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 200 | 3 | 5 | 5.4-27 | --
AB300-A…-GC15+1EEEB..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 230 | 3 | 5 | 5.4-27 | --
AB300-A…-GC15+1EEEB..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 7.6 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 480 | 3 | 5 | 5.4-27 | --
AB300-A…-C15+1EEDB..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 200 | 3 | 5 | 3.2-16 | --
AB300-A…-C15+1EEDB..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 230 | 3 | 5 | 3.2-16 | --
AB300-A…-C15+1EEDB..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 7.6 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 480 | 3 | 5 | 3.2-16 | --
AB300-A…-C15+1EEDB..575V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 6.1 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 600 | 3 | 5 | 6.1 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 600 | 3 | 5 | 3.2-16 | --
AB300-A…-GC15+1EEDB..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 200 | 3 | 5 | 3.2-16 | --
AB300-A…-GC15+1EEDB..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 230 | 3 | 5 | 3.2-16 | --
AB300-A…-GC15+1EEDB..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 7.6 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 480 | 3 | 5 | 3.2-16 | --
AB300-A…-C15+1EECB..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 | 1 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 200 | 3 | 5 | 1-5 | --
AB300-A…-C15+1EECB..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 | 1 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 230 | 3 | 5 | 1-5 | --
AB300-A…-C15+1EECB..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 480 | 3 | 5 | 1-5 | --
AB300-A…-C15+1EECB..575V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 3.9 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 600 | 3 | 5 | 6.1 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 600 | 3 | 5 | 1-5 | --
AB300-A…-GC15+1EECB..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 | 1 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 200 | 3 | 5 | 1-5 | --
AB300-A…-GC15+1EECB..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 | 1 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 230 | 3 | 5 | 1-5 | --
AB300-A…-GC15+1EECB..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 480 | 3 | 5 | 1-5 | --
AB300-B…-C15+1EEED..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | --
AB300-B…-C15+1EEED..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | --
AB300-B…-GC15+1EEED..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | --
AB300-B…-GC15+1EEED..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 | 7.5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | --
AB300-B…-C30+1EEED..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | --
AB300-B…-C30+1EEED..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | --
AB300-B…-C30+1EEED..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 14 | 10 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | --
AB300-B…-GC30+1EEED..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | --
AB300-B…-GC30+1EEED..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | --
AB300-B…-GC30+1EEED..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 14 | 10 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | --
AB300-B…-C50+1EEED..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | --
AB300-B…-C50+1EEED..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | --
AB300-B…-C50+1EEED..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 14 | 10 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | --
AB300-B…-GC50+1EEED..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | --
AB300-B…-GC50+1EEED..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | --
AB300-B…-GC50+1EEED..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 14 | 10 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | --
AB300-C…-C15+1EEFD..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB300-C…-C15+1EEFD..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB300-C…-C15+1EEFD..575V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 | 10 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB300-C…-GC15+1EEFD..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB300-C…-GC15+1EEFD..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB300-C…-C30+1EEFD..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB300-C…-C30+1EEFD..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB300-C…-C30+1EEFD..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 | 15 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB300-C…-GC30+1EEFD..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB300-C…-GC30+1EEFD..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB300-C…-GC30+1EEFD..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 | 15 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB300-C…-C50+1EEFD..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 | 10 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB300-C…-C50+1EEFD..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 | 10 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB300-C…-C50+1EEFD..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 34 | 25 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB300-C…-GC50+1EEFD..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 | 10 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB300-C…-GC50+1EEFD..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 | 10 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB300-C…-GC50+1EEFD..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 34 | 25 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB300-C…-C30+1EEFD..575V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 22 | 20 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB300-C…-C50+1EEFD..575V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 27 | 25 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB300-C…-C15+1EEED..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | --
AB300-C…-C15+1EEED..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 | 3 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | --
AB300-C…-C15+1EEED..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | --
AB300-C…-C15+1EEED..575V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 | 10 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 600 | 3 | 5 | 5.4-27 | --
AB300-C…-GC15+1EEED..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | --
AB300-C…-GC15+1EEED..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 | 3 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | --
AB300-C…-GC15+1EEED..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | --
AB300-C…-C30+1EEED..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | --
AB300-C…-C30+1EEED..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | --
AB300-C…-C30+1EEED..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 | 15 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | --
AB300-C…-GC30+1EEED..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | --
AB300-C…-GC30+1EEED..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | --
AB300-C…-GC30+1EEED..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 | 15 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | --
AB300-C…-C50+1EEED..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | --
AB300-C…-C50+1EEED..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | --
AB300-C…-C50+1EEED..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 | 20 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | --
AB300-C…-GC50+1EEED..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | --
AB300-C…-GC50+1EEED..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | --
AB300-C…-GC50+1EEED..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 | 20 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | --
AB300-C…-C30+1EEED..575V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 22 | 20 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 600 | 3 | 5 | 5.4-27 | --
AB300-C…-C50+1EEED..575V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 27 | 25 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 600 | 3 | 5 | 5.4-27 | --
AB300-D…-C15+1EEFD..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-C15+1EEFD..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB300-D…-C15+1EEFD..575V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 | 10 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB300-D…-GC15+1EEFD..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-GC15+1EEFD..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB300-D…-C30+1EEFD..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-C30+1EEFD..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB300-D…-C30+1EEFD..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 | 15 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB300-D…-GC30+1EEFD..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-GC30+1EEFD..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB300-D…-GC30+1EEFD..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 | 15 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB300-D…-C50+1EEFD..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-C50+1EEFD..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB300-D…-C50+1EEFD..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 | 20 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB300-D…-GC50+1EEFD..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-GC50+1EEFD..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB300-D…-GC50+1EEFD..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 | 20 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB300-D…-C30+1EEFD..575V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 22 | 20 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB300-D…-C50+1EEFD..575V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 27 | 25 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB300-D…-C30+1EEGE..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 5 | 20 - 100 | --
AB300-D…-C30+1EEGE..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 | 15 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 5 | 20 - 100 | --
AB300-D…-C30+1EEGE..575V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 22 | 20 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 600 | 3 | 5 | 20 - 100 | --
AB300-D…-GC30+1EEGE..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 25.3 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 5 | 20 - 100 | --
AB300-D…-GC30+1EEGE..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 5 | 20 - 100 | --
AB300-D…-GC30+1EEGE..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 | 15 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 5 | 20 - 100 | --
AB300-D…-C50+1EEGE..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 | 10 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 5 | 20 - 100 | --
AB300-D…-C50+1EEGE..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 | 10 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 5 | 20 - 100 | --
AB300-D…-C50+1EEGE..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 40 | 30 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 5 | 20 - 100 | --
AB300-D…-C50+1EEGE..575V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 32 | 30 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 600 | 3 | 5 | 20 - 100 | --
AB300-D…-GC50+1EEGE..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 | 10 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 5 | 20 - 100 | --
AB300-D…-GC50+1EEGE..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 | 10 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 5 | 20 - 100 | --
AB300-D…-GC50+1EEGE..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 40 | 30 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 5 | 20 - 100 | --
AB300-D…-C70+1EEFD..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 48.3 | 15 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-C70+1EEFD..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 54 | 20 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB300-D…-C70+1EEFD..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 52 | 40 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB300-D…-C70+1EEFD..575V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 600 | 3 | -- | 70 | -- | 600 | 3 | 25 | 52 | 50 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB300-D…-GC70+1EEFD..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 48.3 | 15 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-GC70+1EEFD..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 54 | 20 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB300-D…-GC70+1EEFD..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 52 | 40 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB300-D…-C70+1EEGD..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 48.3 | 15 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-C70+1EEGD..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 54 | 20 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB300-D…-C70+1EEGD..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 52 | 40 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB300-D…-C70+1EEGD..575V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 600 | 3 | -- | 70 | -- | 600 | 3 | 25 | 52 | 50 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB300-D…-GC70+1EEGD..200V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 48.3 | 15 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-GC70+1EEGD..230V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 54 | 20 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB300-D…-GC70+1EEGD..460V .01 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 52 | 40 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB300-E…-D15+1EFJZ..200V | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 30 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-J8P-D15 | 200 | 3 | -- | 150 | -- | 200 | 3 | 65 | 120 | 40 | 4800 | 1,5,6,7e,9
[10 empty] | MC | Allen-Bradley | 300-EO**** | 200 | 3 | 10 | 120 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFJZ | 200 | 3 | 10 | 40 - 200 | --
AB300-E…-D15+1EFJZ..230V | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 30 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-J8P-D15 | 230 | 3 | -- | 150 | -- | 230 | 3 | 65 | 104 | 40 | 4800 | 1,5,6,7e,9
[10 empty] | MC | Allen-Bradley | 300-EO**** | 230 | 3 | 10 | 130 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFJZ | 230 | 3 | 10 | 40 - 200 | --
AB300-E…-D15+1EFJZ..460V | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 30 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-J8P-D15 | 480 | 3 | -- | 150 | -- | 480 | 3 | 65 | 96 | 75 | 4800 | 1,5,6,7e,9
[10 empty] | MC | Allen-Bradley | 300-EO**** | 480 | 3 | 10 | 124 | 100
[10 empty] | OLR | Allen-Bradley | 193-1EFJZ | 480 | 3 | 10 | 40 - 200 | --
AB300-E…-D15+1EFJZ..575V | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 30 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-J8P-D15 | 600 | 3 | -- | 150 | -- | 600 | 4 | 25 | 99 | 100 | 4800 | 1,5,6,7e,9
[10 empty] | MC | Allen-Bradley | 300-EO**** | 600 | 3 | 10 | 99 | 100
[10 empty] | OLR | Allen-Bradley | 193-1EFJZ | 600 | 3 | 10 | 40 - 200 | --
AB300-E…-D25+1EFJZ..200V | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 30 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 200 | 3 | -- | 250 | -- | 200 | 3 | 65 | 120 | 40 | 4800 | 1,5,6,7e,9
[10 empty] | MC | Allen-Bradley | 300-EO**** | 200 | 3 | 10 | 120 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFJZ | 200 | 3 | 10 | 40 - 200 | --
AB300-E…-D25+1EFJZ..230V | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 30 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 230 | 3 | -- | 250 | -- | 230 | 3 | 65 | 130 | 50 | 4800 | 1,5,6,7e,9
[10 empty] | MC | Allen-Bradley | 300-EO**** | 230 | 3 | 10 | 130 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFJZ | 230 | 3 | 10 | 40 - 200 | --
AB300-E…-D25+1EFJZ..460V | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 30 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 480 | 3 | -- | 250 | -- | 480 | 3 | 65 | 124 | 100 | 4800 | 1,5,6,7e,9
[10 empty] | MC | Allen-Bradley | 300-EO**** | 480 | 3 | 10 | 124 | 100
[10 empty] | OLR | Allen-Bradley | 193-1EFJZ | 480 | 3 | 10 | 40 - 200 | --
AB300-E…-D25+1EFJZ..575V | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 30 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 600 | 3 | -- | 250 | -- | 600 | 4 | 25 | 99 | 100 | 4800 | 1,5,6,7e,9
[10 empty] | MC | Allen-Bradley | 300-EO**** | 600 | 3 | 10 | 99 | 100
[10 empty] | OLR | Allen-Bradley | 193-1EFJZ | 600 | 3 | 10 | 40 - 200 | --
AB300-F…-D40+1EFKZ..200V | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 56 | 30 | 14 | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 200 | 3 | -- | 400 | -- | 200 | 3 | 65 | 221 | 75 | 23520 | 1,5,7f,8,9
[10 empty] | MC | Allen-Bradley | 300-FO**** | 200 | 3 | 10 | 221 | 75
[10 empty] | OLR | Allen-Bradley | 193-1EFKZ | 200 | 3 | 10 | 60 - 300 | --
AB300-F…-D40+1EFKZ..230V | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 56 | 30 | 14 | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 230 | 3 | -- | 400 | -- | 230 | 3 | 65 | 248 | 100 | 23520 | 1,5,7f,8,9
[10 empty] | MC | Allen-Bradley | 300-FO**** | 230 | 3 | 10 | 248 | 100
[10 empty] | OLR | Allen-Bradley | 193-1EFKZ | 230 | 3 | 10 | 60 - 300 | --
AB300-F…-D40+1EFKZ..460V | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 56 | 30 | 14 | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 480 | 3 | -- | 400 | -- | 480 | 3 | 65 | 240 | 200 | 23520 | 1,5,7f,8,9
[10 empty] | MC | Allen-Bradley | 300-FO**** | 480 | 3 | 10 | 240 | 200
[10 empty] | OLR | Allen-Bradley | 193-1EFKZ | 480 | 3 | 10 | 60 - 300 | --
AB300-F…-D25+1EFKZ..575V | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 56 | 30 | 14 | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 600 | 3 | -- | 400 | -- | 600 | 3 | 35 | 192 | 200 | 23520 | 1,5,7f,8,9
[10 empty] | MC | Allen-Bradley | 300-FO**** | 600 | 3 | 10 | 192 | 200
[10 empty] | OLR | Allen-Bradley | 193-1EFKZ | 600 | 3 | 10 | 60 - 300 | --
AB300-A…-C15+1EEEB..200V.02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EFEB | 200 | 3 | 5 | 5.4-27 | --
AB300-A…-C15+1EEEB..230V.02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EFEB | 230 | 3 | 5 | 5.4-27 | --
AB300-A…-C15+1EEEB..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 7.6 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFEB | 480 | 3 | 5 | 5.4-27 | --
AB300-A…-C15+1EEEB..575V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 6.1 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 600 | 3 | 5 | 6.1 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFEB | 600 | 3 | 5 | 5.4-27 | --
AB300-A…-GC15+1EEEB..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EFEB | 200 | 3 | 5 | 5.4-27 | --
AB300-A…-GC15+1EEEB..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EFEB | 230 | 3 | 5 | 5.4-27 | --
AB300-A…-GC15+1EEEB..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 7.6 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFEB | 480 | 3 | 5 | 5.4-27 | --
AB300-A…-C15+1EEDB..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 200 | 3 | 5 | 3.2-16 | --
AB300-A…-C15+1EEDB..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 230 | 3 | 5 | 3.2-16 | --
AB300-A…-C15+1EEDB..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 7.6 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 480 | 3 | 5 | 3.2-16 | --
AB300-A…-C15+1EEDB..575V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 6.1 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 600 | 3 | 5 | 6.1 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 600 | 3 | 5 | 3.2-16 | --
AB300-A…-GC15+1EEDB..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 200 | 3 | 5 | 3.2-16 | --
AB300-A…-GC15+1EEDB..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 230 | 3 | 5 | 3.2-16 | --
AB300-A…-GC15+1EEDB..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 7.6 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 480 | 3 | 5 | 3.2-16 | --
AB300-A…-C15+1EECB..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 | 1 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 200 | 3 | 5 | 1-5 | --
AB300-A…-C15+1EECB..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 | 1 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 230 | 3 | 5 | 1-5 | --
AB300-A…-C15+1EECB..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 480 | 3 | 5 | 1-5 | --
AB300-A…-C15+1EECB..575V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 3.9 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 600 | 3 | 5 | 6.1 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 600 | 3 | 5 | 1-5 | --
AB300-A…-GC15+1EECB..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 | 1 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 200 | 3 | 5 | 11 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 200 | 3 | 5 | 1-5 | --
AB300-A…-GC15+1EECB..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 | 1 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 230 | 3 | 5 | 9.6 | 3
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 230 | 3 | 5 | 1-5 | --
AB300-A…-GC15+1EECB..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-AO****, series C | 480 | 3 | 5 | 7.6 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 480 | 3 | 5 | 1-5 | --
AB300-B…-C15+1EEED..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | --
AB300-B…-C15+1EEED..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | --
AB300-B…-C15+1EEED..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 | 7.5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | --
AB300-B…-C15+1EEED..575V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 | 10 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 600 | 3 | 5 | 11 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 600 | 3 | 5 | 5.4-27 | --
AB300-B…-GC15+1EEED..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | --
AB300-B…-GC15+1EEED..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 | 3 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | --
AB300-B…-GC15+1EEED..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 | 7.5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | --
AB300-B…-C30+1EEED..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | --
AB300-B…-C30+1EEED..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | --
AB300-B…-C30+1EEED..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 14 | 10 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | --
AB300-B…-GC30+1EEED..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | --
AB300-B…-GC30+1EEED..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | --
AB300-B…-GC30+1EEED..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 14 | 10 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | --
AB300-B…-C50+1EEED..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | --
AB300-B…-C50+1EEED..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | --
AB300-B…-C50+1EEED..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 14 | 10 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | --
AB300-B…-GC50+1EEED..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | --
AB300-B…-GC50+1EEED..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | --
AB300-B…-GC50+1EEED..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 14 | 10 | 2310 | 1,5,7a,9
[10 empty] | MC | Allen-Bradley | 300-BO**** | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | --
AB300-C…-C15+1EEFD..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB300-C…-C15+1EEFD..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB300-C…-C15+1EEFD..575V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 | 10 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB300-C…-GC15+1EEFD..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB300-C…-GC15+1EEFD..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB300-C…-C30+1EEFD..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB300-C…-C30+1EEFD..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB300-C…-C30+1EEFD..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 | 15 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB300-C…-GC30+1EEFD..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB300-C…-GC30+1EEFD..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB300-C…-GC30+1EEFD..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 | 15 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB300-C…-C50+1EEFD..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 | 10 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB300-C…-C50+1EEFD..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 | 10 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB300-C…-C50+1EEFD..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 34 | 25 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB300-C…-GC50+1EEFD..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 | 10 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB300-C…-GC50+1EEFD..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 | 10 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB300-C…-GC50+1EEFD..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 34 | 25 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB300-C…-C30+1EEFD..575V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 22 | 20 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB300-C…-C50+1EEFD..575V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 27 | 25 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB300-C…-C15+1EEED..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | --
AB300-C…-C15+1EEED..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 | 3 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | --
AB300-C…-C15+1EEED..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | --
AB300-C…-C15+1EEED..575V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 | 10 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 600 | 3 | 5 | 5.4-27 | --
AB300-C…-GC15+1EEED..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | --
AB300-C…-GC15+1EEED..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 | 3 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | --
AB300-C…-GC15+1EEED..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | --
AB300-C…-C30+1EEED..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | --
AB300-C…-C30+1EEED..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | --
AB300-C…-C30+1EEED..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 | 15 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | --
AB300-C…-GC30+1EEED..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | --
AB300-C…-GC30+1EEED..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | --
AB300-C…-GC30+1EEED..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 | 15 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | --
AB300-C…-C50+1EEED..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | --
AB300-C…-C50+1EEED..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | --
AB300-C…-C50+1EEED..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 | 20 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | --
AB300-C…-GC50+1EEED..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | --
AB300-C…-GC50+1EEED..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | --
AB300-C…-GC50+1EEED..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 | 20 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | --
AB300-C…-C30+1EEED..575V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 22 | 20 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 600 | 3 | 5 | 5.4-27 | --
AB300-C…-C50+1EEED..575V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 27 | 25 | 2310 | 1,5,7c,9
[10 empty] | MC | Allen-Bradley | 300-CO****, series C | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 600 | 3 | 5 | 5.4-27 | --
AB300-D…-C15+1EEFD..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-C15+1EEFD..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB300-D…-C15+1EEFD..575V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 | 10 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB300-D…-GC15+1EEFD..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 | 3 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-GC15+1EEFD..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB300-D…-C30+1EEFD..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-C30+1EEFD..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB300-D…-C30+1EEFD..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 | 15 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB300-D…-GC30+1EEFD..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-GC30+1EEFD..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB300-D…-GC30+1EEFD..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 | 15 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB300-D…-C50+1EEFD..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-C50+1EEFD..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB300-D…-C50+1EEFD..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 | 20 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB300-D…-GC50+1EEFD..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-GC50+1EEFD..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB300-D…-GC50+1EEFD..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 | 20 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB300-D…-C30+1EEFD..575V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 22 | 20 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB300-D…-C50+1EEFD..575V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 27 | 25 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB300-D…-C30+1EEGE..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 5 | 20 - 100 | --
AB300-D…-C30+1EEGE..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 5 | 20 - 100 | --
AB300-D…-C30+1EEGE..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 | 15 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 5 | 20 - 100 | --
AB300-D…-C30+1EEGE..575V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 22 | 20 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 600 | 3 | 5 | 20 - 100 | --
AB300-D…-GC30+1EEGE..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 | 5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 5 | 20 - 100 | --
AB300-D…-GC30+1EEGE..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 | 7.5 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 5 | 20 - 100 | --
AB300-D…-GC30+1EEGE..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 | 15 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 5 | 20 - 100 | --
AB300-D…-C50+1EEGE..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 | 10 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 5 | 20 - 100 | --
AB300-D…-C50+1EEGE..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 | 10 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 5 | 20 - 100 | --
AB300-D…-C50+1EEGE..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 40 | 30 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 5 | 20 - 100 | --
AB300-D…-C50+1EEGE..575V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 32 | 30 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 600 | 3 | 5 | 20 - 100 | --
AB300-D…-GC50+1EEGE..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 | 10 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 5 | 20 - 100 | --
AB300-D…-GC50+1EEGE..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 | 10 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 5 | 20 - 100 | --
AB300-D…-GC50+1EEGE..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 40 | 30 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 5 | 20 - 100 | --
AB300-D…-C70+1EEFD..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 48.3 | 15 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-C70+1EEFD..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 54 | 20 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB300-D…-C70+1EEFD..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 52 | 40 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB300-D…-C70+1EEFD..575V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 600 | 3 | -- | 70 | -- | 600 | 3 | 25 | 52 | 50 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB300-D…-GC70+1EEFD..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 48.3 | 15 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-GC70+1EEFD..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 54 | 20 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB300-D…-GC70+1EEFD..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 52 | 40 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB300-D…-C70+1EEGD..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 48.3 | 15 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-C70+1EEGD..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 54 | 20 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB300-D…-C70+1EEGD..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 52 | 40 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB300-D…-C70+1EEGD..575V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 600 | 3 | -- | 70 | -- | 600 | 3 | 25 | 52 | 50 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB300-D…-GC70+1EEGD..200V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 48.3 | 15 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 200 | 3 | 5 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB300-D…-GC70+1EEGD..230V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 54 | 20 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 230 | 3 | 5 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB300-D…-GC70+1EEGD..460V .02 | E125316 | 2019-07-26 | Vol. 4/Sec. 3 |  |  | 27.5 | 10.5 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 52 | 40 | 2310 | 1,5,7d,9
[10 empty] | MC | Allen-Bradley | 300-DO****, Series D | 480 | 3 | 5 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
6) 193-1EFJZ must be used with CT's: 25645-005-09, 1411-AL-201, or 1411-2DRL-201 manufactured by Rockwell Automation; or 2SFT201 by ITI; or CT225-201 by Amran.
(7) = See Table 7 for minimum internal power wiring.
Table 7 - Minimum Internal Power Wiring
1/32in. thick thermoplastic insulation, rated 105C
Wire Code | [9 empty] | Wire Size
7a | [9 empty] | 10 AWG
7b | [9 empty] | 10 AWG
7c | [9 empty] | 8 AWG
7d | [9 empty] | 2 AWG
7e | [9 empty] | 1AWG
7f | [9 empty] | 250 MCM
8) 193-1EFKZ must be used with CT's: 25645-005-11, 14ll-AL-301 or 1411-2DRL-301 manufactured by Rockwell Automation; or 2SFT301 by ITI; or CT225-300 manufactured by Arman.
9) *** for the contactor indicates options for coil voltage