## 200V
Issued: 2021-11-30
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Minimum Enclosure Volume (cu in) | Conditions of Use | File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | HP Rating | Current Rating FLA or FLA/LRA |  |  | UL File Number | Volume / Section (Vol#).(Sec#)
200 V AC, 3-PHASE
LOVSF00016BG06R | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  |  |  | -
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  |  |  | -
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  |  |  | -
LOVSF00016BG06 | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BG09R | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 200 | 3 | 5 | 7.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BG09 | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 200 | 3 | 5 | 7.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BG12R | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BG12 | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF09AR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF09A | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF12AR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF12A | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF18AR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF18A | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF25AR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF25A | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF09LR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF09L | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF12LR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF12L | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF18LR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF18L | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF25LR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF25L | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF09DR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF09D | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF12DR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF12D | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF18DR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF18D | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF25DR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF25D | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016BF26AR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00016BF26A | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00016BF32AR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00016BF32A | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00016BF38AR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00016BF38A | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00025BG06R | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BG06 | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BG09R | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 200 | 3 | 5 | 7.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BG09 | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 200 | 3 | 5 | 7.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BG12R | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BG12 | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF09AR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF09A | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF12AR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF12A | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF18AR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF18A | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF25AR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF25A | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF09LR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF09L | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF12LR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF12L | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF18LR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF18L | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF25LR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF25L | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF09DR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF09D | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF12DR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF12D | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF18DR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF18D | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF25DR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF25D | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025BF26AR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00025BF26A | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00025BF32AR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00025BF32A | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00025BF38AR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00025BF38A | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00040BG06R | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BG06 | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BG09R | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 200 | 3 | 5 | 7.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BG09 | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 200 | 3 | 5 | 7.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BG12R | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BG12 | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF09AR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF09A | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF12AR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF12A | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF18AR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF18A | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF25AR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF25A | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF09LR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF09L | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF12LR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF12L | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF18LR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF18L | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF25LR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF25L | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF09DR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF09D | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF12DR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF12D | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF18DR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF18D | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF25DR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF25D | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040BF26AR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00040BF26A | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00040BF32AR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00040BF32A | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00040BF38AR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00040BF38A | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00063BG06R | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BG06 | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BG09R | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 200 | 3 | 5 | 7.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BG09 | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 200 | 3 | 5 | 7.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BG12R | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BG12 | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF09AR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF09A | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF12AR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF12A | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF18AR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF18A | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF25AR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF25A | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF09LR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF09L | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF12LR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF12L | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF18LR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF18L | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF25LR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF25L | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF09DR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF09D | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF12DR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF12D | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF18DR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF18D | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF25DR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF25D | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063BF26AR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00063BF26A | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00063BF32AR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00063BF32A | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00063BF38AR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00063BF38A | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00100BG06R | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BG06 | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BG09R | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 200 | 3 | 5 | 7.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BG09 | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 200 | 3 | 5 | 7.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BG12R | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BG12 | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF09AR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF09A | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF12AR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF12A | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF18AR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF18A | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF25AR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF25A | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF09LR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF09L | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF12LR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF12L | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF18LR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF18L | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF25LR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF25L | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF09DR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF09D | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF12DR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF12D | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF18DR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF18D | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF25DR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF25D | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100BF26AR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00100BF26A | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00100BF32AR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00100BF32A | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00100BF38AR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00100BF38A | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00160BG06R | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BG06 | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BG09R | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 200 | 3 | 5 | 7.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BG09 | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 200 | 3 | 5 | 7.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BG12R | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BG12 | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF09AR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF09A | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF12AR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF12A | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF18AR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF18A | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF25AR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF25A | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF09LR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF09L | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF12LR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF12L | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF18LR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF18L | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF25LR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF25L | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF09DR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF09D | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF12DR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF12D | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF18DR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF18D | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF25DR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF25D | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160BF26AR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00160BF26A | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00160BF32AR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00160BF32A | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00160BF38AR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00160BF38A | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00250BG06R | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BG06 | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BG09R | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 200 | 3 | 5 | 7.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BG09 | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 200 | 3 | 5 | 7.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BG12R | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BG12 | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF09AR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF09A | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF12AR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF12A | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF18AR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF18A | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF25AR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF25A | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF09LR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF09L | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF12LR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF12L | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF18LR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF18L | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF25LR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF25L | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF09DR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF09D | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF12DR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF12D | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF18DR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF18D | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF25DR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF25D | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250BF26AR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00250BF26A | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00250BF32AR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00250BF32A | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00250BF38AR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00250BF38A | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00400BG06R | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BG06 | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BG09R | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 200 | 3 | 5 | 7.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BG09 | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 200 | 3 | 5 | 7.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BG12R | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BG12 | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF09AR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF09A | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF12AR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF12A | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF18AR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF18A | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF25AR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF25A | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF09LR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF09L | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF12LR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF12L | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF18LR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF18L | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF25LR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF25L | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF09DR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF09D | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF12DR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF12D | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF18DR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF18D | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF25DR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF25D | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400BF26AR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00400BF26A | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00400BF32AR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00400BF32A | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00400BF38AR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00400BF38A | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00650BG06R | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BG06 | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BG09R | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 200 | 3 | 5 | 7.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BG09 | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 200 | 3 | 5 | 7.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BG12R | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BG12 | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF09AR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF09A | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF12AR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF12A | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF18AR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF18A | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF25AR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF25A | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF09LR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF09L | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF12LR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF12L | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF18LR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF18L | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF25LR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF25L | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF09DR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF09D | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF12DR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF12D | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF18DR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF18D | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF25DR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF25D | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BF26AR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00650BF26A | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00650BF32AR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00650BF32A | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00650BF38AR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00650BF38A | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00650BG06R | F | MSP | Lovato Electric SpA | SM1R0650_BG06 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650BG06 | F | MSP | Lovato Electric SpA | SM1R0650_BG06 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 200 | 3 | 5 | 6.9 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF0E1000BF09AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF09A | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF12AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF12A | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF18AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF18A | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF25AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF25A | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF09LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF09L | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF12LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF12L | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF18LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF18L | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF25LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF25L | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF09DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF09D | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF12DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF12D | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF18DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF18D | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF25DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF25D | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF26AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF26A | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF32AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF32A | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF38AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000BF38A | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF09AR | F | MSP | Lovato Electric SpA | SM1RE1400_BF09 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF09A | F | MSP | Lovato Electric SpA | SM1RE1400_BF09 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF09LR | F | MSP | Lovato Electric SpA | SM1RE1400_BF09 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF09L | F | MSP | Lovato Electric SpA | SM1RE1400_BF09 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF09DR | F | MSP | Lovato Electric SpA | SM1RE1400_BF09 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF09D | F | MSP | Lovato Electric SpA | SM1RE1400_BF09 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF12AR | F | MSP | Lovato Electric SpA | SM1RE1400_BF12 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF12A | F | MSP | Lovato Electric SpA | SM1RE1400_BF12 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF12LR | F | MSP | Lovato Electric SpA | SM1RE1400_BF12 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF12L | F | MSP | Lovato Electric SpA | SM1RE1400_BF12 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF12DR | F | MSP | Lovato Electric SpA | SM1RE1400_BF12 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF12D | F | MSP | Lovato Electric SpA | SM1RE1400_BF12 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF18AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF18A | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF25AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF25A | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF18LR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF18L | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF25LR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF25L | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF18DR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF18D | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF25DR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF25D | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF26AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF26A | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF32AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF32A | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF38AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400BF38A | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF12AR | F | MSP | Lovato Electric SpA | SM1RE1800_BF12 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF12A | F | MSP | Lovato Electric SpA | SM1RE1800_BF12 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF12LR | F | MSP | Lovato Electric SpA | SM1RE1800_BF12 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF12L | F | MSP | Lovato Electric SpA | SM1RE1800_BF12 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF12DR | F | MSP | Lovato Electric SpA | SM1RE1800_BF12 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF12D | F | MSP | Lovato Electric SpA | SM1RE1800_BF12 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF18AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF18A | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF25AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF25A | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF18LR | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF18L | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF25LR | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF25L | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF18DR | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF18D | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF25DR | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF25D | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF26AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF26A | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF32AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF32A | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF38AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800BF38A | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF12AR | F | MSP | Lovato Electric SpA | SM1RE2300_BF12_BF18 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF12A | F | MSP | Lovato Electric SpA | SM1RE2300_BF12_BF18 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF18AR | F | MSP | Lovato Electric SpA | SM1RE2300_BF12_BF18 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF18A | F | MSP | Lovato Electric SpA | SM1RE2300_BF12_BF18 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF12LR | F | MSP | Lovato Electric SpA | SM1RE2300_BF12_BF18 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF12L | F | MSP | Lovato Electric SpA | SM1RE2300_BF12_BF18 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF18LR | F | MSP | Lovato Electric SpA | SM1RE2300_BF12_BF18 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF18L | F | MSP | Lovato Electric SpA | SM1RE2300_BF12_BF18 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF12DR | F | MSP | Lovato Electric SpA | SM1RE2300_BF12_BF18 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF12D | F | MSP | Lovato Electric SpA | SM1RE2300_BF12_BF18 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF18DR | F | MSP | Lovato Electric SpA | SM1RE2300_BF12_BF18 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF18D | F | MSP | Lovato Electric SpA | SM1RE2300_BF12_BF18 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF25AR | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF25A | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF25LR | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF25L | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF25DR | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF25D | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF26AR | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF26A | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF32AR | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF32A | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF38AR | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300BF38A | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2500BF25AR | F | MSP | Lovato Electric SpA | SM1RE2500 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2500BF25A | F | MSP | Lovato Electric SpA | SM1RE2500 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2500BF25LR | F | MSP | Lovato Electric SpA | SM1RE2500 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2500BF25L | F | MSP | Lovato Electric SpA | SM1RE2500 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2500BF25DR | F | MSP | Lovato Electric SpA | SM1RE2500 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2500BF25D | F | MSP | Lovato Electric SpA | SM1RE2500 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2500BF26AR | F | MSP | Lovato Electric SpA | SM1RE2500 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2500BF26A | F | MSP | Lovato Electric SpA | SM1RE2500 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2500BF32AR | F | MSP | Lovato Electric SpA | SM1RE2500 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2500BF32A | F | MSP | Lovato Electric SpA | SM1RE2500 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2500BF38AR | F | MSP | Lovato Electric SpA | SM1RE2500 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2500BF38A | F | MSP | Lovato Electric SpA | SM1RE2500 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E3200BF32AR | F | MSP | Lovato Electric SpA | SM1RE3200 | 200 | 3 | 10 | 32.2 | 10 | 200 | 3 | 10 | 10 | 32.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E3200BF32A | F | MSP | Lovato Electric SpA | SM1RE3200 | 200 | 3 | 10 | 32.2 | 10 | 200 | 3 | 10 | 10 | 32.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E3200BF38AR | F | MSP | Lovato Electric SpA | SM1RE3200 | 200 | 3 | 10 | 32.2 | 10 | 200 | 3 | 10 | 10 | 32.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E3200BF38A | F | MSP | Lovato Electric SpA | SM1RE3200 | 200 | 3 | 10 | 32.2 | 10 | 200 | 3 | 10 | 10 | 32.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF05000BF50 | F | MSP | Lovato Electric SpA | SM2R5000 | 200 | 3 | 100 | 48.3 | 15 | 200 | 3 | 50 | 15 | 48.3 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF50 | 200 | 3 | 100 | 48.3 | 15 |  |  | - | - | - | 1904
LOVSF05000BF65 | F | MSP | Lovato Electric SpA | SM2R5000 | 200 | 3 | 100 | 48.3 | 15 | 200 | 3 | 50 | 15 | 48.3 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF65 | 200 | 3 | 100 | 62.1 | 20 |  |  | - | - | - | 1904
LOVSF05000BF80 | F | MSP | Lovato Electric SpA | SM2R5000 | 200 | 3 | 100 | 48.3 | 15 | 200 | 3 | 50 | 15 | 48.3 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF80 | 200 | 3 | 100 | 78.2 | 25 |  |  | - | - | - | 1904
LOVSF05000BF94 | F | MSP | Lovato Electric SpA | SM2R5000 | 200 | 3 | 100 | 48.3 | 15 | 200 | 3 | 50 | 15 | 48.3 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF94 | 200 | 3 | 100 | 78.2 | 25 |  |  | - | - | - | 1904
LOVSF05000BF95 | F | MSP | Lovato Electric SpA | SM2R5000 | 200 | 3 | 100 | 48.3 | 15 | 200 | 3 | 50 | 15 | 48.3 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF95 | 200 | 3 | 100 | 92 | 30 |  |  | - | - | - | 1904
LOVSF05000BF115 | F | MSP | Lovato Electric SpA | SM2R5000 | 200 | 3 | 100 | 48.3 | 15 | 200 | 3 | 50 | 15 | 48.3 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF115 | 200 | 3 | 100 | 120 | 40 |  |  | - | - | - | 1904
LOVSF05000BF150 | F | MSP | Lovato Electric SpA | SM2R5000 | 200 | 3 | 100 | 48.3 | 15 | 200 | 3 | 50 | 15 | 48.3 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF150 | 200 | 3 | 100 | 150 | 50 |  |  | - | - | - | 1904
LOVSF06300BF50 | F | MSP | Lovato Electric SpA | SM2R6300 | 200 | 3 | 100 | 62.1 | 20 | 200 | 3 | 50 | 15 | 48.3 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF50 | 200 | 3 | 100 | 48.3 | 15 |  |  | - | - | - | 1904
LOVSF06300BF65 | F | MSP | Lovato Electric SpA | SM2R6300 | 200 | 3 | 100 | 62.1 | 20 | 200 | 3 | 50 | 20 | 62.1 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF65 | 200 | 3 | 100 | 62.1 | 20 |  |  | - | - | - | 1904
LOVSF06300BF80 | F | MSP | Lovato Electric SpA | SM2R6300 | 200 | 3 | 100 | 62.1 | 20 | 200 | 3 | 50 | 20 | 62.1 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF80 | 200 | 3 | 100 | 78.2 | 25 |  |  | - | - | - | 1904
LOVSF06300BF94 | F | MSP | Lovato Electric SpA | SM2R6300 | 200 | 3 | 100 | 62.1 | 20 | 200 | 3 | 50 | 20 | 62.1 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF94 | 200 | 3 | 100 | 78.2 | 25 |  |  | - | - | - | 1904
LOVSF06300BF95 | F | MSP | Lovato Electric SpA | SM2R6300 | 200 | 3 | 100 | 62.1 | 20 | 200 | 3 | 50 | 20 | 62.1 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF95 | 200 | 3 | 100 | 92 | 30 |  |  | - | - | - | 1904
LOVSF06300BF115 | F | MSP | Lovato Electric SpA | SM2R6300 | 200 | 3 | 100 | 62.1 | 20 | 200 | 3 | 50 | 20 | 62.1 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF115 | 200 | 3 | 100 | 120 | 40 |  |  | - | - | - | 1904
LOVSF06300BF150 | F | MSP | Lovato Electric SpA | SM2R6300 | 200 | 3 | 100 | 62.1 | 20 | 200 | 3 | 50 | 20 | 62.1 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF150 | 200 | 3 | 100 | 150 | 50 |  |  | - | - | - | 1904
LOVSF07500BF65 | F | MSP | Lovato Electric SpA | SM3R7500 | 200 | 3 | 100 | 62.1 | 20 | 200 | 3 | 40 | 20 | 62.1 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF65 | 200 | 3 | 100 | 62.1 | 20 |  |  | - | - | - | 1904
LOVSF07500BF80 | F | MSP | Lovato Electric SpA | SM3R7500 | 200 | 3 | 100 | 62.1 | 20 | 200 | 3 | 40 | 20 | 62.1 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF80 | 200 | 3 | 100 | 78.2 | 25 |  |  | - | - | - | 1904
LOVSF07500BF94 | F | MSP | Lovato Electric SpA | SM3R7500 | 200 | 3 | 100 | 62.1 | 20 | 200 | 3 | 40 | 20 | 62.1 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF94 | 200 | 3 | 100 | 78.2 | 25 |  |  | - | - | - | 1904
LOVSF07500BF95 | F | MSP | Lovato Electric SpA | SM3R7500 | 200 | 3 | 100 | 62.1 | 20 | 200 | 3 | 40 | 20 | 62.1 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF95 | 200 | 3 | 100 | 92 | 30 |  |  | - | - | - | 1904
LOVSF07500BF115 | F | MSP | Lovato Electric SpA | SM3R7500 | 200 | 3 | 100 | 62.1 | 20 | 200 | 3 | 40 | 20 | 62.1 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF115 | 200 | 3 | 100 | 120 | 40 |  |  | - | - | - | 1904
LOVSF07500BF150 | F | MSP | Lovato Electric SpA | SM3R7500 | 200 | 3 | 100 | 62.1 | 20 | 200 | 3 | 40 | 20 | 62.1 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF150 | 200 | 3 | 100 | 150 | 50 |  |  | - | - | - | 1904
LOVSF09000BF80 | F | MSP | Lovato Electric SpA | SM3R9000 | 200 | 3 | 100 | 78.2 | 25 | 200 | 3 | 40 | 25 | 78.2 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF80 | 200 | 3 | 100 | 78.2 | 25 |  |  | - | - | - | 1904
LOVSF09000BF94 | F | MSP | Lovato Electric SpA | SM3R9000 | 200 | 3 | 100 | 78.2 | 25 | 200 | 3 | 40 | 25 | 78.2 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF94 | 200 | 3 | 100 | 78.2 | 25 |  |  | - | - | - | 1904
LOVSF09000BF95 | F | MSP | Lovato Electric SpA | SM3R9000 | 200 | 3 | 100 | 78.2 | 25 | 200 | 3 | 40 | 25 | 78.2 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF95 | 200 | 3 | 100 | 92 | 30 |  |  | - | - | - | 1904
LOVSF09000BF115 | F | MSP | Lovato Electric SpA | SM3R9000 | 200 | 3 | 100 | 78.2 | 25 | 200 | 3 | 40 | 25 | 78.2 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF115 | 200 | 3 | 100 | 120 | 40 |  |  | - | - | - | 1904
LOVSF09000BF150 | F | MSP | Lovato Electric SpA | SM3R9000 | 200 | 3 | 100 | 78.2 | 25 | 200 | 3 | 40 | 25 | 78.2 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF150 | 200 | 3 | 100 | 150 | 50 |  |  | - | - | - | 1904
LOVSF09900BF115 | F | MSP | Lovato Electric SpA | SM3R9900 | 200 | 3 | 100 | 92 | 30 | 200 | 3 | 40 | 30 | 92 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF115 | 200 | 3 | 100 | 120 | 40 |  |  | - | - | - | 1904
LOVSF09900BF150 | F | MSP | Lovato Electric SpA | SM3R9900 | 200 | 3 | 100 | 92 | 30 | 200 | 3 | 40 | 30 | 92 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF150 | 200 | 3 | 100 | 150 | 50 |  |  | - | - | - | 1904
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having an ampacity of
125 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor
controllers shall be considered in the end-product application.
|  | 6 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu) No. 14 AWG wire.
|  | 7 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu), for size of conductor see table below.
|  | 8 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu), for size of conductor see table below.

## 208V
Issued: 2021-11-30
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Minimum Enclosure Volume (cu in) | Conditions of Use | File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | HP Rating | Current Rating FLA or FLA/LRA |  |  | UL File Number | Volume / Section (Vol#).(Sec#)
208 V AC, 3-PHASE
LOVSF10016BG06R | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  |  |  | -
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  |  |  | -
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  |  |  | -
LOVSF10016BG06 | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BG09R | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 208 | 3 | 5 | 7.5 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BG09 | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 208 | 3 | 5 | 7.5 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BG12R | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BG12 | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF09AR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF09A | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF12AR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF12A | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF18AR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF18A | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF25AR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF25A | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF09LR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF09L | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF12LR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF12L | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF18LR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF18L | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF25LR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF25L | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF09DR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF09D | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF12DR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF12D | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF18DR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF18D | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF25DR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF25D | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016BF26AR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10016BF26A | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10016BF32AR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10016BF32A | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10016BF38AR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10016BF38A | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10025BG06R | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BG06 | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BG09R | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 208 | 3 | 5 | 7.5 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BG09 | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 208 | 3 | 5 | 7.5 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BG12R | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BG12 | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF09AR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF09A | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF12AR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF12A | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF18AR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF18A | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF25AR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF25A | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF09LR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF09L | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF12LR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF12L | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF18LR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF18L | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF25LR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF25L | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF09DR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF09D | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF12DR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF12D | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF18DR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF18D | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF25DR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF25D | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025BF26AR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10025BF26A | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10025BF32AR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10025BF32A | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10025BF38AR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10025BF38A | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10040BG06R | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BG06 | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BG09R | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 208 | 3 | 5 | 7.5 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BG09 | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 208 | 3 | 5 | 7.5 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BG12R | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BG12 | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF09AR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF09A | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF12AR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF12A | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF18AR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF18A | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF25AR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF25A | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF09LR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF09L | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF12LR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF12L | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF18LR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF18L | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF25LR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF25L | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF09DR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF09D | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF12DR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF12D | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF18DR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF18D | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF25DR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF25D | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040BF26AR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10040BF26A | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10040BF32AR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10040BF32A | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10040BF38AR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10040BF38A | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10063BG06R | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BG06 | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BG09R | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 208 | 3 | 5 | 7.5 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BG09 | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 208 | 3 | 5 | 7.5 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BG12R | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BG12 | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF09AR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF09A | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF12AR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF12A | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF18AR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF18A | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF25AR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF25A | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF09LR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF09L | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF12LR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF12L | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF18LR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF18L | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF25LR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF25L | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF09DR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF09D | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF12DR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF12D | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF18DR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF18D | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF25DR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF25D | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063BF26AR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10063BF26A | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10063BF32AR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10063BF32A | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10063BF38AR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10063BF38A | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10100BG06R | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BG06 | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BG09R | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 208 | 3 | 5 | 7.5 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BG09 | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 208 | 3 | 5 | 7.5 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BG12R | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BG12 | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF09AR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF09A | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF12AR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF12A | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF18AR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF18A | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF25AR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF25A | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF09LR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF09L | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF12LR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF12L | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF18LR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF18L | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF25LR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF25L | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF09DR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF09D | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF12DR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF12D | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF18DR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF18D | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF25DR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF25D | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100BF26AR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10100BF26A | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10100BF32AR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10100BF32A | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10100BF38AR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10100BF38A | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10160BG06R | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BG06 | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BG09R | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 208 | 3 | 5 | 7.5 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BG09 | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 208 | 3 | 5 | 7.5 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BG12R | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BG12 | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF09AR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF09A | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF12AR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF12A | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF18AR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF18A | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF25AR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF25A | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF09LR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF09L | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF12LR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF12L | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF18LR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF18L | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF25LR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF25L | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF09DR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF09D | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF12DR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF12D | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF18DR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF18D | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF25DR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF25D | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160BF26AR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10160BF26A | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10160BF32AR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10160BF32A | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10160BF38AR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10160BF38A | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10250BG06R | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - |  | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - |  | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - |  | 439
LOVSF10250BG06 | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - |  | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - |  | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - |  | 439
LOVSF10250BG09R | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 208 | 3 | 5 | 7.5 | 2 |  |  | - | - |  | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - |  | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - |  | 439
LOVSF10250BG09 | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 208 | 3 | 5 | 7.5 | 2 |  |  | - | - |  | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - |  | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - |  | 439
LOVSF10250BG12R | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - |  | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - |  | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - |  | 439
LOVSF10250BG12 | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - |  | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - |  | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - |  | 439
LOVSF10250BF09AR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - |  | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - |  | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - |  | 439
LOVSF10250BF09A | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - |  | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - |  | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - |  | 439
LOVSF10250BF12AR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - |  | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - |  | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - |  | 439
LOVSF10250BF12A | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF18AR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF18A | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF25AR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF25A | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF09LR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF09L | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF12LR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF12L | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF18LR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF18L | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF25LR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF25L | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF09DR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF09D | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF12DR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF12D | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF18DR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF18D | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF25DR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF25D | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250BF26AR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10250BF26A | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10250BF32AR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10250BF32A | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10250BF38AR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10250BF38A | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10400BG06R | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BG06 | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BG09R | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 208 | 3 | 5 | 7.5 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BG09 | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 208 | 3 | 5 | 7.5 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BG12R | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BG12 | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF09AR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF09A | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF12AR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF12A | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF18AR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF18A | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF25AR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF25A | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF09LR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF09L | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF12LR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF12L | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF18LR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF18L | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF25LR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF25L | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF09DR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF09D | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF12DR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF12D | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF18DR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF18D | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF25DR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF25D | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400BF26AR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10400BF26A | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10400BF32AR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10400BF32A | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10400BF38AR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10400BF38A | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10650BG06R | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BG06 | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BG09R | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 208 | 3 | 5 | 7.5 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BG09 | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 208 | 3 | 5 | 7.5 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BG12R | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BG12 | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF09AR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF09A | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF12AR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF12A | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF18AR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF18A | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF25AR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF25A | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF09LR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF09L | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF12LR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF12L | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF18LR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF18L | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF25LR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF25L | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF09DR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF09D | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF12DR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF12D | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF18DR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF18D | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF25DR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF25D | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BF26AR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10650BF26A | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10650BF32AR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10650BF32A | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10650BF38AR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10650BF38A | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10650BG06R | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650BG06 | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 208 | 3 | 5 | 6.6 | 1 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF1E1000BF09AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF09A | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF12AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF12A | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF18AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF18A | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF25AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF25A | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF09LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF09L | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF12LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF12L | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF18LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF18L | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF25LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF25L | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF09DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF09D | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF12DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF12D | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF18DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF18D | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF25DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF25D | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF26AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF26A | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF32AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF32A | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF38AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000BF38A | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF09AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF09A | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF09LR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF09L | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF09DR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF09D | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF12AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF12A | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF12LR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF12L | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF12DR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF12D | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF18AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF18A | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF25AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF25A | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF18LR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF18L | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF25LR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF25L | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF18DR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF18D | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF25DR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF25D | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF26AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF26A | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF32AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF32A | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF38AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400BF38A | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF12AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF12A | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF12LR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF12L | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF12DR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF12D | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF18AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF18A | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF25AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF25A | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF18LR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF18L | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF25LR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF25L | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF18DR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF18D | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF25DR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF25D | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF26AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF26A | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF32AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF32A | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF38AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800BF38A | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF12AR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF12A | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF18AR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF18A | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF12LR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF12L | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF18LR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF18L | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF12DR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF12D | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF18DR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF18D | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF25AR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF25A | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF25LR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF25L | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF25DR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF25D | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF26AR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF26A | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF32AR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF32A | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF38AR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300BF38A | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2500BF25AR | F | MSP | Lovato Electric SpA | SM1RE2500 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2500BF25A | F | MSP | Lovato Electric SpA | SM1RE2500 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2500BF25LR | F | MSP | Lovato Electric SpA | SM1RE2500 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2500BF25L | F | MSP | Lovato Electric SpA | SM1RE2500 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2500BF25DR | F | MSP | Lovato Electric SpA | SM1RE2500 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2500BF25D | F | MSP | Lovato Electric SpA | SM1RE2500 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2500BF26AR | F | MSP | Lovato Electric SpA | SM1RE2500 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2500BF26A | F | MSP | Lovato Electric SpA | SM1RE2500 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2500BF32AR | F | MSP | Lovato Electric SpA | SM1RE2500 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2500BF32A | F | MSP | Lovato Electric SpA | SM1RE2500 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2500BF38AR | F | MSP | Lovato Electric SpA | SM1RE2500 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2500BF38A | F | MSP | Lovato Electric SpA | SM1RE2500 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E3200BF32AR | F | MSP | Lovato Electric SpA | SM1RE3200 | 208 | 3 | 10 | 30.8 | 10 | 208 | 3 | 10 | 10 | 30.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E3200BF32A | F | MSP | Lovato Electric SpA | SM1RE3200 | 208 | 3 | 10 | 30.8 | 10 | 208 | 3 | 10 | 10 | 30.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E3200BF38AR | F | MSP | Lovato Electric SpA | SM1RE3200 | 208 | 3 | 10 | 30.8 | 10 | 208 | 3 | 10 | 10 | 30.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E3200BF38A | F | MSP | Lovato Electric SpA | SM1RE3200 | 208 | 3 | 10 | 30.8 | 10 | 208 | 3 | 10 | 10 | 30.8 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having an ampacity of
125 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor
controllers shall be considered in the end-product application.
|  | 6 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu) No. 14 AWG wire.
|  | 7 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu), for size of conductor see table below.

## 240V
Issued: 2021-11-30
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Minimum Enclosure Volume (cu in) | Conditions of Use | File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | HP Rating | Current Rating FLA or FLA/LRA |  |  | UL File Number | Volume / Section (Vol#).(Sec#)
240 V AC, 3-PHASE
LOVSF20016BG06R | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BG06 | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BG09R | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BG09 | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BG12R | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BG12 | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF09AR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF09A | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF12AR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF12A | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF18AR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF18A | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF25AR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF25A | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF09LR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF09L | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF12LR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF12L | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF18LR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF18L | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF25LR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF25L | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF09DR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF09D | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF12DR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF12D | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF18DR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF18D | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF25DR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF25D | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016BF26AR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20016BF26A | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20016BF32AR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20016BF32A | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20016BF38AR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20016BF38A | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20025BG06R | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BG06 | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BG09R | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BG09 | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BG12R | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BG12 | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF09AR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF09A | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF12AR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF12A | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF18AR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF18A | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF25AR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF25A | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF09LR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF09L | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF12LR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF12L | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF18LR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF18L | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF25LR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF25L | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF09DR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF09D | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF12DR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF12D | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF18DR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF18D | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF25DR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF25D | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025BF26AR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20025BF26A | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20025BF32AR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20025BF32A | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20025BF38AR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20025BF38A | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20040BG06R | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BG06 | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BG09R | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BG09 | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BG12R | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BG12 | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF09AR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF09A | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF12AR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF12A | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF18AR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF18A | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF25AR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF25A | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF09LR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF09L | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF12LR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF12L | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF18LR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF18L | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF25LR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF25L | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF09DR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF09D | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF12DR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF12D | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF18DR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF18D | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF25DR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF25D | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040BF26AR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20040BF26A | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20040BF32AR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20040BF32A | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20040BF38AR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20040BF38A | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20063BG06R | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BG06 | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BG09R | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BG09 | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BG12R | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BG12 | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF09AR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF09A | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF12AR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF12A | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF18AR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF18A | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF25AR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF25A | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF09LR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF09L | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF12LR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF12L | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF18LR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF18L | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF25LR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF25L | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF09DR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF09D | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF12DR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF12D | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF18DR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF18D | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF25DR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF25D | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063BF26AR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20063BF26A | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20063BF32AR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20063BF32A | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20063BF38AR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20063BF38A | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20100BG06R | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BG06 | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BG09R | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BG09 | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BG12R | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BG12 | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF09AR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF09A | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF12AR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF12A | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF18AR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF18A | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF25AR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF25A | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF09LR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF09L | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF12LR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF12L | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF18LR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF18L | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF25LR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF25L | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF09DR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF09D | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF12DR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF12D | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF18DR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF18D | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF25DR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF25D | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100BF26AR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20100BF26A | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20100BF32AR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20100BF32A | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20100BF38AR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20100BF38A | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20160BG06R | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BG06 | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BG09R | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BG09 | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BG12R | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BG12 | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF09AR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF09A | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF12AR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF12A | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF18AR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF18A | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF25AR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF25A | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF09LR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF09L | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF12LR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF12L | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF18LR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF18L | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF25LR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF25L | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF09DR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF09D | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF12DR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF12D | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF18DR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF18D | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF25DR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF25D | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160BF26AR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20160BF26A | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20160BF32AR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20160BF32A | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20160BF38AR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20160BF38A | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20250BG06R | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BG06 | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BG09R | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BG09 | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BG12R | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BG12 | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF09AR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF09A | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF12AR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF12A | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF18AR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF18A | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF25AR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF25A | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF09LR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF09L | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF12LR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF12L | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF18LR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF18L | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF25LR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF25L | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF09DR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF09D | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF12DR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF12D | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF18DR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF18D | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF25DR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF25D | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250BF26AR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20250BF26A | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20250BF32AR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20250BF32A | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20250BF38AR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20250BF38A | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20400BG06R | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BG06 | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BG09R | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BG09 | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BG12R | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BG12 | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF09AR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF09A | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF12AR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF12A | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF18AR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF18A | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF25AR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF25A | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF09LR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF09L | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF12LR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF12L | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF18LR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF18L | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF25LR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF25L | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF09DR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF09D | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF12DR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF12D | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF18DR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF18D | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF25DR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF25D | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400BF26AR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20400BF26A | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20400BF32AR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20400BF32A | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20400BF38AR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20400BF38A | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.2 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20650BG06R | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BG06 | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BG09R | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BG09 | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BG12R | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BG12 | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF09AR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF09A | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF12AR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF12A | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF18AR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF18A | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF25AR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF25A | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF09LR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF09L | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF12LR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF12L | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF18LR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF18L | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF25LR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF25L | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF09DR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF09D | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF12DR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF12D | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF18DR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF18D | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF25DR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF25D | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BF26AR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20650BF26A | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20650BF32AR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20650BF32A | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20650BF38AR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20650BF38A | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20650BG06R | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650BG06 | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.0 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 240 | 3 | 5 | 6.8 | 2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF2E1000BF09AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF09A | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF12AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF12A | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF18AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF18A | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF25AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF25A | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF09LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF09L | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF12LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF12L | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF18LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF18L | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF25LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF25L | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF09DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF09D | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF12DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF12D | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF18DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF18D | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF25DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF25D | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF26AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF26A | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF32AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF32A | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF38AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000BF38A | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF09AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF09A | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF09LR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF09L | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF09DR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF09D | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF12AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF12A | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF12LR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF12L | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF12DR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF12D | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF18AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF18A | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF25AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF25A | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF18LR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF18L | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF25LR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF25L | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF18DR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF18D | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF25DR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF25D | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF26AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF26A | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF32AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF32A | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF38AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400BF38A | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF12AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF12A | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF12LR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF12L | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF12DR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF12D | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF18AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF18A | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF25AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF25A | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF18LR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF18L | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF25LR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF25L | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF18DR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF18D | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF25DR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF25D | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF26AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF26A | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF32AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF32A | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF38AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800BF38A | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2300BF25AR | F | MSP | Lovato Electric SpA | SM1RE2300 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2300BF25A | F | MSP | Lovato Electric SpA | SM1RE2300 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2300BF25LR | F | MSP | Lovato Electric SpA | SM1RE2300 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2300BF25L | F | MSP | Lovato Electric SpA | SM1RE2300 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2300BF25DR | F | MSP | Lovato Electric SpA | SM1RE2300 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2300BF25D | F | MSP | Lovato Electric SpA | SM1RE2300 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2300BF26AR | F | MSP | Lovato Electric SpA | SM1RE2300 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2300BF26A | F | MSP | Lovato Electric SpA | SM1RE2300 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2300BF32AR | F | MSP | Lovato Electric SpA | SM1RE2300 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2300BF32A | F | MSP | Lovato Electric SpA | SM1RE2300 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2300BF38AR | F | MSP | Lovato Electric SpA | SM1RE2300 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2300BF38A | F | MSP | Lovato Electric SpA | SM1RE2300 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2500BF25AR | F | MSP | Lovato Electric SpA | SM1RE2500 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2500BF25A | F | MSP | Lovato Electric SpA | SM1RE2500 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2500BF25LR | F | MSP | Lovato Electric SpA | SM1RE2500 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2500BF25L | F | MSP | Lovato Electric SpA | SM1RE2500 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2500BF25DR | F | MSP | Lovato Electric SpA | SM1RE2500 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2500BF25D | F | MSP | Lovato Electric SpA | SM1RE2500 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2500BF26AR | F | MSP | Lovato Electric SpA | SM1RE2500 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2500BF26A | F | MSP | Lovato Electric SpA | SM1RE2500 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2500BF32AR | F | MSP | Lovato Electric SpA | SM1RE2500 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2500BF32A | F | MSP | Lovato Electric SpA | SM1RE2500 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2500BF38AR | F | MSP | Lovato Electric SpA | SM1RE2500 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2500BF38A | F | MSP | Lovato Electric SpA | SM1RE2500 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E3200BF32AR | F | MSP | Lovato Electric SpA | SM1RE3200 | 240 | 3 | 10 | 28 | 10 | 240 | 3 | 10 | 10 | 28 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E3200BF32A | F | MSP | Lovato Electric SpA | SM1RE3200 | 240 | 3 | 10 | 28 | 10 | 240 | 3 | 10 | 10 | 28 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E3200BF38AR | F | MSP | Lovato Electric SpA | SM1RE3200 | 240 | 3 | 10 | 28 | 10 | 240 | 3 | 10 | 10 | 28 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E3200BF38A | F | MSP | Lovato Electric SpA | SM1RE3200 | 240 | 3 | 10 | 28 | 10 | 240 | 3 | 10 | 10 | 28 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 240 | 3 | 5 | 42.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF25000BF40 | F | MSP | Lovato Electric SpA | SM2R5000 | 230 | 3 | 100 | 42 | 15 | 230 | 3 | 50 | 15 | 42 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF40 | 240 | 3 | 100 | 42 | 15 |  |  | - | - | - | 1904
LOVSF25000BF50 | F | MSP | Lovato Electric SpA | SM2R5000 | 230 | 3 | 100 | 42 | 15 | 230 | 3 | 50 | 15 | 42 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF50 | 240 | 3 | 100 | 54 | 20 |  |  | - | - | - | 1904
LOVSF25000BF65 | F | MSP | Lovato Electric SpA | SM2R5000 | 230 | 3 | 100 | 42 | 15 | 230 | 3 | 50 | 15 | 42 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF65 | 240 | 3 | 100 | 68 | 25 |  |  | - | - | - | 1904
LOVSF25000BF80 | F | MSP | Lovato Electric SpA | SM2R5000 | 230 | 3 | 100 | 42 | 15 | 230 | 3 | 50 | 15 | 42 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF80 | 240 | 3 | 100 | 80 | 30 |  |  | - | - | - | 1904
LOVSF25000BF94 | F | MSP | Lovato Electric SpA | SM2R5000 | 230 | 3 | 100 | 42 | 15 | 230 | 3 | 50 | 15 | 42 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF94 | 240 | 3 | 100 | 80 | 30 |  |  | - | - | - | 1904
LOVSF25000BF95 | F | MSP | Lovato Electric SpA | SM2R5000 | 230 | 3 | 100 | 42 | 15 | 230 | 3 | 50 | 15 | 42 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF95 | 240 | 3 | 100 | 80 | 30 |  |  | - | - | - | 1904
LOVSF25000BF115 | F | MSP | Lovato Electric SpA | SM2R5000 | 230 | 3 | 100 | 50 | 15 | 230 | 3 | 50 | 15 | 42 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF115 | 240 | 3 | 100 | 104 | 40 |  |  | - | - | - | 1904
LOVSF25000BF150 | F | MSP | Lovato Electric SpA | SM2R5000 | 230 | 3 | 100 | 42 | 15 | 230 | 3 | 50 | 15 | 42 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF150 | 240 | 3 | 100 | 130 | 50 |  |  | - | - | - | 1904
LOVSF26300BF50 | F | MSP | Lovato Electric SpA | SM2R6300 | 230 | 3 | 100 | 54 | 20 | 230 | 3 | 50 | 20 | 54 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF50 | 240 | 3 | 100 | 54 | 20 |  |  | - | - | - | 1904
LOVSF26300BF65 | F | MSP | Lovato Electric SpA | SM2R6300 | 230 | 3 | 100 | 54 | 20 | 230 | 3 | 50 | 20 | 54 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF65 | 240 | 3 | 100 | 68 | 25 |  |  | - | - | - | 1904
LOVSF26300BF80 | F | MSP | Lovato Electric SpA | SM2R6300 | 230 | 3 | 100 | 54 | 20 | 230 | 3 | 50 | 20 | 54 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF80 | 240 | 3 | 100 | 80 | 30 |  |  | - | - | - | 1904
LOVSF26300BF94 | F | MSP | Lovato Electric SpA | SM2R6300 | 230 | 3 | 100 | 54 | 20 | 230 | 3 | 50 | 20 | 54 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF94 | 240 | 3 | 100 | 80 | 30 |  |  | - | - | - | 1904
LOVSF26300BF95 | F | MSP | Lovato Electric SpA | SM2R6300 | 230 | 3 | 100 | 54 | 20 | 230 | 3 | 50 | 20 | 54 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF95 | 240 | 3 | 100 | 80 | 30 |  |  | - | - | - | 1904
LOVSF26300BF115 | F | MSP | Lovato Electric SpA | SM2R6300 | 230 | 3 | 100 | 54 | 20 | 230 | 3 | 50 | 20 | 54 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF115 | 240 | 3 | 100 | 104 | 40 |  |  | - | - | - | 1904
LOVSF26300BF150 | F | MSP | Lovato Electric SpA | SM2R6300 | 230 | 3 | 100 | 54 | 20 | 230 | 3 | 50 | 20 | 54 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF150 | 240 | 3 | 100 | 130 | 50 |  |  | - | - | - | 1904
LOVSF27500BF65 | F | MSP | Lovato Electric SpA | SM3R7500 | 230 | 3 | 100 | 68 | 25 | 230 | 3 | 40 | 25 | 68 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF65 | 240 | 3 | 100 | 68 | 25 |  |  | - | - | - | 1904
LOVSF27500BF80 | F | MSP | Lovato Electric SpA | SM3R7500 | 230 | 3 | 100 | 68 | 25 | 230 | 3 | 40 | 25 | 68 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF80 | 240 | 3 | 100 | 80 | 30 |  |  | - | - | - | 1904
LOVSF27500BF94 | F | MSP | Lovato Electric SpA | SM3R7500 | 230 | 3 | 100 | 68 | 25 | 230 | 3 | 40 | 25 | 68 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF94 | 240 | 3 | 100 | 80 | 30 |  |  | - | - | - | 1904
LOVSF27500BF95 | F | MSP | Lovato Electric SpA | SM3R7500 | 230 | 3 | 100 | 68 | 25 | 230 | 3 | 40 | 25 | 68 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF95 | 240 | 3 | 100 | 80 | 30 |  |  | - | - | - | 1904
LOVSF27500BF115 | F | MSP | Lovato Electric SpA | SM3R7500 | 230 | 3 | 100 | 68 | 25 | 230 | 3 | 40 | 25 | 68 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF115 | 240 | 3 | 100 | 104 | 40 |  |  | - | - | - | 1904
LOVSF27500BF150 | F | MSP | Lovato Electric SpA | SM3R7500 | 230 | 3 | 100 | 68 | 25 | 230 | 3 | 40 | 25 | 68 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF150 | 240 | 3 | 100 | 130 | 50 |  |  | - | - | - | 1904
LOVSF29000BF80 | F | MSP | Lovato Electric SpA | SM3R9000 | 230 | 3 | 100 | 80 | 30 | 230 | 3 | 40 | 30 | 80 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF80 | 240 | 3 | 100 | 80 | 30 |  |  | - | - | - | 1904
LOVSF29000BF94 | F | MSP | Lovato Electric SpA | SM3R9000 | 230 | 3 | 100 | 80 | 30 | 230 | 3 | 40 | 30 | 80 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF94 | 240 | 3 | 100 | 80 | 30 |  |  | - | - | - | 1904
LOVSF29000BF95 | F | MSP | Lovato Electric SpA | SM3R9000 | 230 | 3 | 100 | 80 | 30 | 230 | 3 | 40 | 30 | 80 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF95 | 240 | 3 | 100 | 80 | 30 |  |  | - | - | - | 1904
LOVSF29000BF115 | F | MSP | Lovato Electric SpA | SM3R9000 | 230 | 3 | 100 | 80 | 30 | 230 | 3 | 40 | 30 | 80 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF115 | 240 | 3 | 100 | 104 | 40 |  |  | - | - | - | 1904
LOVSF29000BF150 | F | MSP | Lovato Electric SpA | SM3R9000 | 230 | 3 | 100 | 80 | 30 | 230 | 3 | 40 | 30 | 80 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF150 | 240 | 3 | 100 | 130 | 50 |  |  | - | - | - | 1904
LOVSF29900BF115 | F | MSP | Lovato Electric SpA | SM3R9900 | 230 | 3 | 100 | 80 | 30 | 230 | 3 | 40 | 30 | 80 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF115 | 240 | 3 | 100 | 104 | 40 |  |  | - | - | - | 1904
LOVSF29900BF150 | F | MSP | Lovato Electric SpA | SM3R9900 | 230 | 3 | 100 | 80 | 30 | 230 | 3 | 40 | 30 | 80 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF150 | 240 | 3 | 100 | 130 | 50 |  |  | - | - | - | 1904
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having an ampacity of
125 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor
controllers shall be considered in the end-product application.
|  | 6 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu) No. 14 AWG wire.
|  | 7 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu), for size of conductor see table below.
|  | 8 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu), for size of conductor see table below.

## 480V
Issued: 2021-11-30
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Minimum Enclosure Volume (cu in) | Conditions of Use | File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | HP Rating | Current Rating FLA or FLA/LRA |  |  | UL File Number | Volume / Section (Vol#).(Sec#)
480 V AC, 3-PHASE
LOVSF30016BG06R | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BG06 | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BG09R | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BG09 | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BG12R | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BG12 | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF09AR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF09A | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF12AR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF12A | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF18AR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF18A | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF25AR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF25A | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF09LR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF09L | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF12LR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF12L | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF18LR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF18L | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF25LR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF25L | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF09DR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF09D | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF12DR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF12D | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF18DR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF18D | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF25DR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF25D | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016BF26AR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30016BF26A | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30016BF32AR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30016BF32A | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30016BF38AR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30016BF38A | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30025BG06R | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BG06 | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BG09R | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BG09 | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BG12R | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BG12 | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF09AR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF09A | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF12AR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF12A | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF18AR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF18A | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF25AR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF25A | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF09LR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF09L | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF12LR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF12L | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF18LR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF18L | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF25LR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF25L | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF09DR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF09D | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF12DR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF12D | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF18DR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF18D | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF25DR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF25D | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025BF26AR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30025BF26A | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30025BF32AR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30025BF32A | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30025BF38AR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30025BF38A | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30040BG06R | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BG06 | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BG09R | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BG09 | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BG12R | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BG12 | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF09AR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF09A | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF12AR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF12A | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF18AR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF18A | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF25AR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF25A | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF09LR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF09L | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF12LR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF12L | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF18LR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF18L | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF25LR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF25L | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF09DR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF09D | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF12DR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF12D | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF18DR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF18D | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF25DR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF25D | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040BF26AR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30040BF26A | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30040BF32AR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30040BF32A | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30040BF38AR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30040BF38A | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30063BG06R | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BG06 | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BG09R | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BG09 | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BG12R | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BG12 | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF09AR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF09A | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF12AR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF12A | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF18AR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF18A | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF25AR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF25A | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF09LR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF09L | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF12LR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF12L | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF18LR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF18L | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF25LR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF25L | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF09DR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF09D | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF12DR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF12D | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF18DR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF18D | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF25DR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF25D | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063BF26AR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30063BF26A | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30063BF32AR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30063BF32A | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30063BF38AR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30063BF38A | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30100BG06R | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BG06 | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BG09R | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BG09 | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BG12R | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BG12 | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF09AR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF09A | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF12AR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF12A | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF18AR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF18A | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF25AR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF25A | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF09LR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF09L | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF12LR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF12L | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF18LR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF18L | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF25LR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF25L | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF09DR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF09D | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF12DR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF12D | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF18DR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF18D | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF25DR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF25D | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100BF26AR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30100BF26A | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30100BF32AR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30100BF32A | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30100BF38AR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30100BF38A | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30160BG06R | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BG06 | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BG09R | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BG09 | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BG12R | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BG12 | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF09AR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF09A | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF12AR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF12A | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF18AR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF18A | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF25AR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF25A | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF09LR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF09L | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF12LR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF12L | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF18LR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF18L | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF25LR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF25L | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF09DR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF09D | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF12DR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF12D | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF18DR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF18D | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF25DR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF25D | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160BF26AR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30160BF26A | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30160BF32AR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30160BF32A | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30160BF38AR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30160BF38A | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30250BG06R | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BG06 | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BG09R | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BG09 | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BG12R | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BG12 | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF09AR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF09A | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF12AR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF12A | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF18AR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF18A | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF25AR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF25A | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF09LR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF09L | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF12LR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF12L | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF18LR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF18L | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF25LR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF25L | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF09DR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF09D | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF12DR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF12D | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF18DR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF18D | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF25DR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF25D | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250BF26AR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30250BF26A | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30250BF32AR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30250BF32A | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30250BF38AR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30250BF38A | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30400BG06R | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BG06 | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BG09R | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BG09 | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BG12R | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BG12 | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF09AR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF09A | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF12AR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF12A | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF18AR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF18A | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF25AR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF25A | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF09LR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF09L | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF12LR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF12L | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF18LR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF18L | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF25LR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF25L | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF09DR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF09D | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF12DR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF12D | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF18DR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF18D | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF25DR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF25D | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400BF26AR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30400BF26A | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30400BF32AR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30400BF32A | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30400BF38AR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30400BF38A | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30650BG06R | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BG06 | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BG09R | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BG09 | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BG12R | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BG12 | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF09AR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF09A | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF12AR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF12A | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF18AR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF18A | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF25AR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF25A | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF09LR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF09L | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF12LR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF12L | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF18LR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF18L | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF25LR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF25L | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF09DR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF09D | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF12DR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF12D | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF18DR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF18D | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF25DR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF25D | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BF26AR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30650BF26A | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30650BF32AR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30650BF32A | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30650BF38AR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30650BF38A | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30650BG06R | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650BG06 | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 480 | 3 | 5 | 4.8 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF3E1000BF09AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF09A | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF12AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF12A | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF18AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF18A | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF25AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF25A | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF09LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF09L | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF12LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF12L | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF18LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF18L | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF25LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF25L | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF09DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF09D | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF12DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF12D | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF18DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF18D | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF25DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF25D | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF26AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF26A | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF32AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF32A | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF38AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000BF38A | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400BF18AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400BF18A | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400BF25AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400BF25A | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400BF18LR | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400BF18L | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400BF25LR | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400BF25L | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400BF18DR | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400BF18D | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400BF25DR | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400BF25D | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400BF26AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400BF26A | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400BF32AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400BF32A | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400BF38AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400BF38A | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800BF18AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800BF18A | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800BF25AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800BF25A | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800BF18LR | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800BF18L | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800BF25LR | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800BF25L | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800BF18DR | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800BF18D | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800BF25DR | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800BF25D | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800BF26AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800BF26A | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800BF32AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800BF32A | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800BF38AR | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800BF38A | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2300BF25AR | F | MSP | Lovato Electric SpA | SM1RE2300 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2300BF25A | F | MSP | Lovato Electric SpA | SM1RE2300 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2300BF25LR | F | MSP | Lovato Electric SpA | SM1RE2300 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2300BF25L | F | MSP | Lovato Electric SpA | SM1RE2300 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2300BF25DR | F | MSP | Lovato Electric SpA | SM1RE2300 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2300BF25D | F | MSP | Lovato Electric SpA | SM1RE2300 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2300BF26AR | F | MSP | Lovato Electric SpA | SM1RE2300 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2300BF26A | F | MSP | Lovato Electric SpA | SM1RE2300 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2300BF32AR | F | MSP | Lovato Electric SpA | SM1RE2300 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2300BF32A | F | MSP | Lovato Electric SpA | SM1RE2300 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2300BF38AR | F | MSP | Lovato Electric SpA | SM1RE2300 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2300BF38A | F | MSP | Lovato Electric SpA | SM1RE2300 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2500BF25AR | F | MSP | Lovato Electric SpA | SM1RE2500 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2500BF25A | F | MSP | Lovato Electric SpA | SM1RE2500 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2500BF25LR | F | MSP | Lovato Electric SpA | SM1RE2500 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2500BF25L | F | MSP | Lovato Electric SpA | SM1RE2500 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2500BF25DR | F | MSP | Lovato Electric SpA | SM1RE2500 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2500BF25D | F | MSP | Lovato Electric SpA | SM1RE2500 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2500BF26AR | F | MSP | Lovato Electric SpA | SM1RE2500 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2500BF26A | F | MSP | Lovato Electric SpA | SM1RE2500 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2500BF32AR | F | MSP | Lovato Electric SpA | SM1RE2500 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2500BF32A | F | MSP | Lovato Electric SpA | SM1RE2500 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2500BF38AR | F | MSP | Lovato Electric SpA | SM1RE2500 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2500BF38A | F | MSP | Lovato Electric SpA | SM1RE2500 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E3200BF32AR | F | MSP | Lovato Electric SpA | SM1RE3200 | 480Y/277V | 3 | 10 | 27 | 20 | 480Y/277V | 3 | 10 | 20 | 27 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E3200BF32A | F | MSP | Lovato Electric SpA | SM1RE3200 | 480Y/277V | 3 | 10 | 27 | 20 | 480Y/277V | 3 | 10 | 20 | 27 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E3200BF38AR | F | MSP | Lovato Electric SpA | SM1RE3200 | 480Y/277V | 3 | 10 | 27 | 20 | 480Y/277V | 3 | 10 | 20 | 27 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E3200BF38A | F | MSP | Lovato Electric SpA | SM1RE3200 | 480Y/277V | 3 | 10 | 27 | 20 | 480Y/277V | 3 | 10 | 20 | 27 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 480 | 3 | 5 | 40.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF35000BF40 | F | MSP | Lovato Electric SpA | SM2R5000 | 460 | 3 | 50 | 40 | 30 | 460 (480Y/277V) | 3 | 50 | 30 | 40 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF40 | 480 | 3 | 100 | 40 | 30 |  |  | - | - | - | 1904
LOVSF35000BF50 | F | MSP | Lovato Electric SpA | SM2R5000 | 460 | 3 | 50 | 40 | 30 | 460 (480Y/277V) | 3 | 50 | 30 | 40 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF50 | 480 | 3 | 100 | 52 | 40 |  |  | - | - | - | 1904
LOVSF35000BF65 | F | MSP | Lovato Electric SpA | SM2R5000 | 460 | 3 | 50 | 40 | 30 | 460 (480Y/277V) | 3 | 50 | 30 | 40 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF65 | 480 | 3 | 100 | 65 | 50 |  |  | - | - | - | 1904
LOVSF35000BF80 | F | MSP | Lovato Electric SpA | SM2R5000 | 460 | 3 | 50 | 40 | 30 | 460 (480Y/277V) | 3 | 50 | 30 | 40 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF80 | 480 | 3 | 100 | 77 | 60 |  |  | - | - | - | 1904
LOVSF35000BF94 | F | MSP | Lovato Electric SpA | SM2R5000 | 460 | 3 | 50 | 40 | 30 | 460 (480Y/277V) | 3 | 50 | 30 | 40 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF94 | 480 | 3 | 100 | 77 | 60 |  |  | - | - | - | 1904
LOVSF35000BF95 | F | MSP | Lovato Electric SpA | SM2R5000 | 460 | 3 | 50 | 40 | 30 | 460 (480Y/277V) | 3 | 50 | 30 | 40 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF95 | 480 | 3 | 100 | 77 | 60 |  |  | - | - | - | 1904
LOVSF35000BF115 | F | MSP | Lovato Electric SpA | SM2R5000 | 460 | 3 | 50 | 40 | 30 | 460 (480Y/277V) | 3 | 50 | 30 | 40 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF115 | 480 | 3 | 100 | 96 | 75 |  |  | - | - | - | 1904
LOVSF35000BF150 | F | MSP | Lovato Electric SpA | SM2R5000 | 460 | 3 | 50 | 40 | 30 | 460 (480Y/277V) | 3 | 50 | 30 | 40 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF150 | 480 | 3 | 100 | 124 | 100 |  |  | - | - | - | 1904
LOVSF36300BF50 | F | MSP | Lovato Electric SpA | SM2R6300 | 460 | 3 | 50 | 52 | 40 | 460 (480Y/277V) | 3 | 50 | 40 | 52 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF50 | 480 | 3 | 100 | 52 | 40 |  |  | - | - | - | 1904
LOVSF36300BF65 | F | MSP | Lovato Electric SpA | SM2R6300 | 460 | 3 | 50 | 52 | 40 | 460 (480Y/277V) | 3 | 50 | 40 | 52 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF65 | 480 | 3 | 100 | 65 | 50 |  |  | - | - | - | 1904
LOVSF36300BF80 | F | MSP | Lovato Electric SpA | SM2R6300 | 460 | 3 | 50 | 52 | 40 | 460 (480Y/277V) | 3 | 50 | 40 | 52 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF80 | 480 | 3 | 100 | 77 | 60 |  |  | - | - | - | 1904
LOVSF36300BF94 | F | MSP | Lovato Electric SpA | SM2R6300 | 460 | 3 | 50 | 52 | 40 | 460 (480Y/277V) | 3 | 50 | 40 | 52 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF94 | 480 | 3 | 100 | 77 | 60 |  |  | - | - | - | 1904
LOVSF36300BF95 | F | MSP | Lovato Electric SpA | SM2R6300 | 460 | 3 | 50 | 52 | 40 | 460 (480Y/277V) | 3 | 50 | 40 | 52 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF95 | 480 | 3 | 100 | 77 | 60 |  |  | - | - | - | 1904
LOVSF36300BF115 | F | MSP | Lovato Electric SpA | SM2R6300 | 460 | 3 | 50 | 52 | 40 | 460 (480Y/277V) | 3 | 50 | 40 | 52 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF115 | 480 | 3 | 100 | 96 | 75 |  |  | - | - | - | 1904
LOVSF36300BF150 | F | MSP | Lovato Electric SpA | SM2R6300 | 460 | 3 | 50 | 52 | 40 | 460 (480Y/277V) | 3 | 50 | 40 | 52 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF150 | 480 | 3 | 100 | 124 | 100 |  |  | - | - | - | 1904
LOVSF37500BF65 | F | MSP | Lovato Electric SpA | SM3R7500 | 460 | 3 | 50 | 65 | 50 | 460 (480Y/277V) | 3 | 40 | 50 | 65 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF65 | 480 | 3 | 100 | 65 | 50 |  |  | - | - | - | 1904
LOVSF37500BF80 | F | MSP | Lovato Electric SpA | SM3R7500 | 460 | 3 | 50 | 65 | 50 | 460 (480Y/277V) | 3 | 40 | 50 | 65 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF80 | 480 | 3 | 100 | 77 | 60 |  |  | - | - | - | 1904
LOVSF37500BF94 | F | MSP | Lovato Electric SpA | SM3R7500 | 460 | 3 | 50 | 65 | 50 | 460 (480Y/277V) | 3 | 40 | 50 | 65 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF94 | 480 | 3 | 100 | 77 | 60 |  |  | - | - | - | 1904
LOVSF37500BF95 | F | MSP | Lovato Electric SpA | SM3R7500 | 460 | 3 | 50 | 65 | 50 | 460 (480Y/277V) | 3 | 40 | 50 | 65 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF95 | 480 | 3 | 100 | 77 | 60 |  |  | - | - | - | 1904
LOVSF37500BF115 | F | MSP | Lovato Electric SpA | SM3R7500 | 460 | 3 | 50 | 65 | 50 | 460 (480Y/277V) | 3 | 40 | 50 | 65 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF115 | 480 | 3 | 100 | 96 | 75 |  |  | - | - | - | 1904
LOVSF37500BF150 | F | MSP | Lovato Electric SpA | SM3R7500 | 460 | 3 | 50 | 65 | 50 | 460 (480Y/277V) | 3 | 40 | 50 | 65 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF150 | 480 | 3 | 100 | 124 | 100 |  |  | - | - | - | 1904
LOVSF39000BF80 | F | MSP | Lovato Electric SpA | SM3R9000 | 460 | 3 | 50 | 77 | 60 | 460 (480Y/277V) | 3 | 40 | 60 | 77 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF80 | 480 | 3 | 100 | 77 | 60 |  |  | - | - | - | 1904
LOVSF39000BF94 | F | MSP | Lovato Electric SpA | SM3R9000 | 460 | 3 | 50 | 77 | 60 | 460 (480Y/277V) | 3 | 40 | 60 | 77 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF94 | 480 | 3 | 100 | 77 | 60 |  |  | - | - | - | 1904
LOVSF39000BF95 | F | MSP | Lovato Electric SpA | SM3R9000 | 460 | 3 | 50 | 77 | 60 | 460 (480Y/277V) | 3 | 40 | 60 | 77 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF95 | 480 | 3 | 100 | 77 | 60 |  |  | - | - | - | 1904
LOVSF39000BF115 | F | MSP | Lovato Electric SpA | SM3R9000 | 460 | 3 | 50 | 77 | 60 | 460 (480Y/277V) | 3 | 40 | 60 | 77 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF115 | 480 | 3 | 100 | 96 | 75 |  |  | - | - | - | 1904
LOVSF39000BF150 | F | MSP | Lovato Electric SpA | SM3R9000 | 460 | 3 | 50 | 77 | 60 | 460 (480Y/277V) | 3 | 40 | 60 | 77 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF150 | 480 | 3 | 100 | 124 | 100 |  |  | - | - | - | 1904
LOVSF39900BF115 | F | MSP | Lovato Electric SpA | SM3R9900 | 460 | 3 | 50 | 96 | 75 | 460 (480Y/277V) | 3 | 40 | 75 | 96 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF115 | 480 | 3 | 100 | 96 | 75 |  |  | - | - | - | 1904
LOVSF39900BF150 | F | MSP | Lovato Electric SpA | SM3R9900 | 460 | 3 | 50 | 96 | 75 | 460 (480Y/277V) | 3 | 40 | 75 | 96 | 1904 | 1, 5, 8 | E327729 | 1.5
|  | MC | Lovato Electric SpA | BF150 | 480 | 3 | 100 | 124 | 100 |  |  | - | - | - | 1904
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having an ampacity of
125 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor
controllers shall be considered in the end-product application.
|  | 6 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu) No. 14 AWG wire.
|  | 7 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu), for size of conductor see table below.
|  | 8 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu), for size of conductor see table below.

## 600V
Issued: 2021-11-30
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Minimum Enclosure Volume (cu in) | Conditions of Use | File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | HP Rating | Current Rating FLA or FLA/LRA |  |  | UL File Number | Volume / Section (Vol#).(Sec#)
600 V AC, 3-PHASE
LOVSF40016BG06R | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 600 | 3 | 5 | 3.9 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BG06 | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 600 | 3 | 5 | 3.9 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BG09R | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 600 | 3 | 5 | 6.1 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BG09 | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 600 | 3 | 5 | 6.1 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BG12R | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BG12 | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF09AR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF09A | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF12AR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF12A | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF18AR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF18A | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF25AR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF25A | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF09LR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF09L | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF12LR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF12L | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF18LR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF18L | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF25LR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF25L | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF09DR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF09D | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF12DR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF12D | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF18DR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF18D | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF25DR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF25D | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016BF26AR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40016BF26A | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40016BF32AR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40016BF32A | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40016BF38AR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40016BF38A | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40025BG06R | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 600 | 3 | 5 | 3.9 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BG06 | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 600 | 3 | 5 | 3.9 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BG09R | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 600 | 3 | 5 | 6.1 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BG09 | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 600 | 3 | 5 | 6.1 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BG12R | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BG12 | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF09AR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF09A | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF12AR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF12A | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF18AR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF18A | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF25AR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF25A | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF09LR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF09L | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF12LR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF12L | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF18LR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF18L | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF25LR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF25L | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF09DR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF09D | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF12DR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF12D | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF18DR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF18D | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF25DR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF25D | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025BF26AR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40025BF26A | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40025BF32AR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40025BF32A | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40025BF38AR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40025BF38A | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40040BG06R | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 600 | 3 | 5 | 3.9 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BG06 | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 600 | 3 | 5 | 3.9 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BG09R | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 600 | 3 | 5 | 6.1 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BG09 | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 600 | 3 | 5 | 6.1 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BG12R | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BG12 | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF09AR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF09A | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF12AR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF12A | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF18AR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF18A | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF25AR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF25A | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF09LR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF09L | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF12LR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF12L | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF18LR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF18L | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF25LR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF25L | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF09DR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF09D | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF12DR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF12D | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF18DR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF18D | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF25DR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF25D | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040BF26AR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40040BF26A | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40040BF32AR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40040BF32A | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40040BF38AR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40040BF38A | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40063BG06R | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 600 | 3 | 5 | 3.9 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BG06 | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 600 | 3 | 5 | 3.9 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BG09R | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 600 | 3 | 5 | 6.1 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BG09 | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 600 | 3 | 5 | 6.1 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BG12R | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BG12 | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF09AR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF09A | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF12AR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF12A | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF18AR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF18A | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF25AR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF25A | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF09LR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF09L | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF12LR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF12L | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF18LR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF18L | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF25LR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF25L | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF09DR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF09D | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF12DR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF12D | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF18DR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF18D | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF25DR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF25D | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063BF26AR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40063BF26A | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40063BF32AR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40063BF32A | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40063BF38AR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40063BF38A | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40100BG06R | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 600 | 3 | 5 | 3.9 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BG06 | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 600 | 3 | 5 | 3.9 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BG09R | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 600 | 3 | 5 | 6.1 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BG09 | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 600 | 3 | 5 | 6.1 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BG12R | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BG12 | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF09AR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF09A | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF12AR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF12A | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF18AR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF18A | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF25AR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF25A | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF09LR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF09L | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF12LR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF12L | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF18LR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF18L | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF25LR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF25L | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF09DR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF09D | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF12DR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF12D | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF18DR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF18D | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF25DR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF25D | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100BF26AR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40100BF26A | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40100BF32AR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40100BF32A | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40100BF38AR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40100BF38A | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40160BG06R | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 600 | 3 | 5 | 3.9 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BG06 | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 600 | 3 | 5 | 3.9 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BG09R | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 600 | 3 | 5 | 6.1 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BG09 | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 600 | 3 | 5 | 6.1 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BG12R | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BG12 | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF09AR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF09A | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF12AR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF12A | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF18AR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF18A | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF25AR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF25A | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF09LR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF09L | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF12LR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF12L | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF18LR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF18L | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF25LR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF25L | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF09DR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF09D | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF12DR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF12D | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF18DR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF18D | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF25DR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF25D | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160BF26AR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40160BF26A | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40160BF32AR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40160BF32A | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40160BF38AR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40160BF38A | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40250BG06R | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 600 | 3 | 5 | 3.9 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BG06 | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 600 | 3 | 5 | 3.9 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BG09R | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 600 | 3 | 5 | 6.1 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BG09 | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 600 | 3 | 5 | 6.1 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BG12R | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BG12 | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF09AR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF09A | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF12AR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF12A | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF18AR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF18A | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF25AR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF25A | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF09LR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF09L | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF12LR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF12L | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF18LR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF18L | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF25LR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF25L | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF09DR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF09D | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF12DR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF12D | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF18DR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF18D | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF25DR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF25D | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250BF26AR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40250BF26A | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40250BF32AR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40250BF32A | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40250BF38AR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40250BF38A | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40400BG06R | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 600 | 3 | 5 | 3.9 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BG06 | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG06 | 600 | 3 | 5 | 3.9 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BG09R | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 600 | 3 | 5 | 6.1 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BG09 | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 600 | 3 | 5 | 6.1 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BG12R | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BG12 | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF09AR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF09A | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF12AR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF12A | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF18AR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF18A | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF25AR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF25A | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF09LR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF09L | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF12LR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF12L | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF18LR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF18L | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF25LR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF25L | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF09DR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF09D | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF12DR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF12D | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF18DR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF18D | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF25DR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF25D | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400BF26AR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40400BF26A | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40400BF32AR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40400BF32A | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40400BF38AR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40400BF38A | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40650BG09R | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 600 | 3 | 5 | 6.1 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BG09 | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG09 | 600 | 3 | 5 | 6.1 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BG12R | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BG12 | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BG12 | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF09AR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF09A | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF12AR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF12A | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF18AR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF18A | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF25AR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF25A | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF09LR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF09L | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF12LR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF12L | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF18LR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF18L | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF25LR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF25L | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF09DR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF09D | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF12DR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF12D | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF18DR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF18D | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF25DR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF25D | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650BF26AR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40650BF26A | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40650BF32AR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40650BF32A | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40650BF38AR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40650BF38A | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 1172 | 1, 5, 6 | E327729 | 1.3
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF09AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF09A | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF12AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF12A | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF18AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF18A | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF25AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF25A | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF09LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF09L | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF12LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF12L | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF18LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF18L | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF25LR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF25L | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF09DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF09D | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF09/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF12DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF12D | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF18DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF18D | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF25DR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF25D | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF26AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF26A | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF32AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF32A | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF38AR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000BF38A | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF12AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF12A | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF12LR | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF12L | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF12DR | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF12D | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF12/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF18AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF18A | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF25AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF25A | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF18LR | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF18L | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF25LR | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF25L | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF18DR | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF18D | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF18/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF25DR | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF25D | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF25/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF26AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF26A | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF26/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF32AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF32A | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF32/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF38AR | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400BF38A | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7 | E327729 | 1.4
|  | MC | Lovato Electric SpA | BF38/A | 600 | 3 | 5 | 32.0 | 30 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having an ampacity of
125 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor
controllers shall be considered in the end-product application.
|  | 6 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu) No. 14 AWG wire.
|  | 7 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu), for size of conductor see table below.