## C.O.A.
Conditions of Acceptability For Combination Motor Controllers:
Unless specified otherwise in the individual Recognitions, consideration is to be given to the following Conditions of Acceptability when these
components are employed as a combination motor controller in the end-use equipment: Specific Conditions of Use - Number refers to specific
condition number as defined below and number in parenthesis identifies specific information applicable to the combination motor controller.
C.O. A #:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = Refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = Shorting contactor ((SHORT)MC) and Isolation contactor ((ISO)MC) coils shall be connected to the control terminals of the soft starter. See soft starter instruction manual for details.
(10) = '*" - Catalog no. LC1D80A (Everlink BTR screw connector type) may not be used.
(11) = "&" - Electronic trip unit required for circuit breaker to allow adjustment of overcurrent trip setting
(12) = Circuit breaker catalog number shown is for the base breaker and may be followed by various suffixes (representing trip unit functionality and various accessories)
(13) = The third character of the CB catalog number (shown as 'x' ) may be an "L”, an "F”, an "M “, or a "P”, indicating lugs on both ends, no lugs, lugs "ON “end only, or lugs "OFF” end only, respectively.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
Wire Code | Wire Size
7a | 12 AWG
7b | 8 AWG
7c | 2 AWG
7d | 1 AWG
7e | 250 MCM
7f | 300 MCM
7g | (2) 250 MCM
7h | 2/0 AWG
7i | 4/0 AWG
7j | (2) 4/0 AWG
7k | 10 AWG
7l | 6 AWG
7m | 4 AWG
7n | 3 AWG
7p | 1/0 AWG
7q | (2) 3/0 AWG
7r | (2) 2/0 AWG
7s | 3/0 AWG

## ATS48-IEC
Issued: 2007-04-09
Last Revised: 2007-04-30
Contactor is to be used as a shorting contactor only and may be optionally provided
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File | Other UL File Reference
SE102090 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 7920 | 1, 5, 7a | E169933 V1 S2 | E40610 V12 S20
SE102090 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 7920 | 1, 5, 7a | E169933 V1 S2 | E40610 V12 S20
SE102090 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 7920 | 1, 5, 7a | E169933 V1 S2 | E40610 V12 S20
SE102091 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 7920 | 1, 5, 7a | E169933 V1 S2 | E40610 V12 S20
SE102091 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 7920 | 1, 5, 7a | E169933 V1 S2 | E40610 V12 S20
SE102091 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 7920 | 1, 5, 7a | E169933 V1 S2 | E40610 V12 S20
SE102092 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 25 | 208 | 3 | 7.5 | 24.2 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102092 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 25 | 208 | 3 | 7.5 | 24.2 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102092 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 25 | 208 | 3 | 7.5 | 24.2 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102093 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102093 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102093 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102094 | C | CB | Square D | FHL36090 | 65 | 90 | 600 | 3 | 25 | 208 | 3 | 15 | 46.2 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102094 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 25 | 208 | 3 | 15 | 46.2 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102094 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 25 | 208 | 3 | 15 | 46.2 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102095 | C | CB | Square D | FHL36100 | 65 | 100 | 600 | 3 | 25 | 208 | 3 | 20 | 59.4 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102095 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 25 | 208 | 3 | 20 | 59.4 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102095 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 25 | 208 | 3 | 20 | 59.4 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102096 | C | CB | Square D | KCL34110 | 100 | 110 | 480 | 3 | 25 | 208 | 3 | 25 | 74.8 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102096 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 25 | 208 | 3 | 25 | 74.8 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102096 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 25 | 208 | 3 | 25 | 74.8 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102097 | C | CB | Square D | KCL34125 | 100 | 125 | 480 | 3 | 25 | 208 | 3 | 30 | 88 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102097 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 25 | 208 | 3 | 30 | 88 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102097 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 25 | 208 | 3 | 30 | 88 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102098 | C | CB | Square D | KCL34250 | 100 | 250 | 480 | 3 | 25 | 208 | 3 | 40 | 114 | 8316 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102098 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 25 | 208 | 3 | 40 | 114 | 8316 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102098 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 25 | 208 | 3 | 40 | 114 | 8316 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102099 | C | CB | Square D | KCL34250 | 100 | 250 | 480 | 3 | 25 | 208 | 3 | 50 | 143 | 8316 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102099 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 25 | 208 | 3 | 50 | 143 | 8316 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102099 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 25 | 208 | 3 | 50 | 143 | 8316 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102100 | C | CB | Square D | KCL34250 | 100 | 250 | 480 | 3 | 25 | 208 | 3 | 60 | 169 | 28800 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102100 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 25 | 208 | 3 | 60 | 169 | 28800 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102100 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 25 | 208 | 3 | 60 | 169 | 28800 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102101 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 25 | 208 | 3 | 75 | 211 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102101 |  | MC | Telemecanique | LC1F225 | 10 | 225 | 600 | 3 | 25 | 208 | 3 | 75 | 211 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102101 |  | STR | Telemecanique | ATS48C25Y | 18 | 250 | 600 | 3 | 25 | 208 | 3 | 75 | 211 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102102 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 25 | 208 | 3 | 100 | 273 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102102 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 25 | 208 | 3 | 100 | 273 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102102 |  | STR | Telemecanique | ATS48C32Y | 18 | 320 | 600 | 3 | 25 | 208 | 3 | 100 | 273 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102103 | D | ICB | Square D | MHL3660040M | - | 600 | 600 | 3 | 25 | 208 | 3 | 125 | 343 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102103 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 25 | 208 | 3 | 125 | 343 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102103 |  | STR | Telemecanique | ATS48C41Y | 65 | 410 | 600 | 3 | 25 | 208 | 3 | 125 | 343 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102104 | D | ICB | Square D | MHL3660042M | - | 600 | 600 | 3 | 30 | 208 | 3 | 150 | 396 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102104 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 30 | 208 | 3 | 150 | 396 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102104 |  | STR | Telemecanique | ATS48C48Y | 65 | 480 | 600 | 3 | 30 | 208 | 3 | 150 | 396 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102105 | D | ICB | Square D | MHL3660044M | - | 600 | 600 | 3 | 30 | 208 | 3 | 200 | 528 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102105 |  | MC | Telemecanique | LC1F630 | 42 | 630 | 600 | 3 | 30 | 208 | 3 | 200 | 528 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102105 |  | STR | Telemecanique | ATS48C66Y | 65 | 660 | 600 | 3 | 30 | 208 | 3 | 200 | 528 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102106 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 7920 | 1, 5, 7a | E169933 V1 S2 | E40610 V12 S20
SE102106 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 7920 | 1, 5, 7a | E169933 V1 S2 | E40610 V12 S20
SE102106 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 7920 | 1, 5, 7a | E169933 V1 S2 | E40610 V12 S20
SE102107 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102107 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102107 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102108 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102108 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102108 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102109 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102109 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102109 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102110 | C | CB | Square D | FHL36090 | 65 | 90 | 600 | 3 | 25 | 240 | 3 | 20 | 54 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102110 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 25 | 240 | 3 | 20 | 54 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102110 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 25 | 240 | 3 | 20 | 54 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102111 | C | CB | Square D | FHL36100 | 65 | 100 | 600 | 3 | 25 | 240 | 3 | 25 | 68 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102111 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 25 | 240 | 3 | 25 | 68 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102111 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 25 | 240 | 3 | 25 | 68 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102112 | C | CB | Square D | KCL34110 | 100 | 110 | 480 | 3 | 25 | 240 | 3 | 30 | 80 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102112 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 25 | 240 | 3 | 30 | 80 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102112 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 25 | 240 | 3 | 30 | 80 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102113 | C | CB | Square D | KCL34150 | 100 | 150 | 480 | 3 | 25 | 240 | 3 | 40 | 104 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102113 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 25 | 240 | 3 | 40 | 104 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102113 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 25 | 240 | 3 | 40 | 104 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102114 | C | CB | Square D | KCL34250 | 100 | 250 | 480 | 3 | 25 | 240 | 3 | 50 | 130 | 8316 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102114 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 25 | 240 | 3 | 50 | 130 | 8316 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102114 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 25 | 240 | 3 | 50 | 130 | 8316 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102115 | C | CB | Square D | KCL34250 | 100 | 250 | 480 | 3 | 25 | 240 | 3 | 60 | 154 | 8316 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102115 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 25 | 240 | 3 | 60 | 154 | 8316 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102115 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 25 | 240 | 3 | 60 | 154 | 8316 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102116 | D | ICB | Square D | LHL3625032M | - | 250 | 600 | 3 | 25 | 240 | 3 | 75 | 192 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102116 |  | MC | Telemecanique | LC1F225 | 10 | 225 | 600 | 3 | 25 | 240 | 3 | 75 | 192 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102116 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 25 | 240 | 3 | 75 | 192 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102117 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 25 | 240 | 3 | 100 | 248 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102117 |  | MC | Telemecanique | LC1F265 | 18 | 265 | 600 | 3 | 25 | 240 | 3 | 100 | 248 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102117 |  | STR | Telemecanique | ATS48C25Y | 18 | 250 | 600 | 3 | 25 | 240 | 3 | 100 | 248 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102118 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 25 | 240 | 3 | 125 | 312 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102118 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 25 | 240 | 3 | 125 | 312 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102118 |  | STR | Telemecanique | ATS48C32Y | 18 | 320 | 600 | 3 | 25 | 240 | 3 | 125 | 312 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102119 | D | ICB | Square D | MHL3660040M | - | 600 | 600 | 3 | 30 | 240 | 3 | 150 | 360 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102119 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 30 | 240 | 3 | 150 | 360 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102119 |  | STR | Telemecanique | ATS48C41Y | 65 | 410 | 600 | 3 | 30 | 240 | 3 | 150 | 360 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102120 | D | ICB | Square D | MHL3660044M | - | 600 | 600 | 3 | 30 | 240 | 3 | 200 | 480 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102120 |  | MC | Telemecanique | LC1F630 | 42 | 630 | 600 | 3 | 30 | 240 | 3 | 200 | 480 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102120 |  | STR | Telemecanique | ATS48C59Y | 65 | 590 | 600 | 3 | 30 | 240 | 3 | 200 | 480 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102121 | D | ICB | Square D | MHL3680045M | - | 800 | 600 | 3 | 30 | 240 | 3 | 250 | 604 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102121 |  | MC | Telemecanique | LC1F630 | 42 | 630 | 600 | 3 | 30 | 240 | 3 | 250 | 604 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102121 |  | STR | Telemecanique | ATS48C66Y | 65 | 660 | 600 | 3 | 30 | 240 | 3 | 250 | 604 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102122 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 7920 | 1, 5, 7a | E169933 V1 S2 | E40610 V12 S20
SE102122 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 7920 | 1, 5, 7a | E169933 V1 S2 | E40610 V12 S20
SE102122 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 7920 | 1, 5, 7a | E169933 V1 S2 | E40610 V12 S20
SE102123 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102123 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102123 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102124 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102124 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102124 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102125 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102125 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102125 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102126 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102126 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102126 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 7920 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102127 | C | CB | Square D | FHL36090 | 25 | 90 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102127 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102127 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102128 | C | CB | Square D | FHL36100 | 25 | 100 | 600 | 3 | 25 | 480 | 3 | 50 | 65 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102128 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 25 | 480 | 3 | 50 | 65 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102128 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 25 | 480 | 3 | 50 | 65 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102129 | C | CB | Square D | KCL34110 | 65 | 110 | 480 | 3 | 25 | 480 | 3 | 60 | 77 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102129 |  | MC | Telemecanique | LC1D115 | 5 | 115 | 600 | 3 | 25 | 480 | 3 | 60 | 77 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102129 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 25 | 480 | 3 | 60 | 77 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102130 | C | CB | Square D | KCL34125 | 65 | 125 | 480 | 3 | 25 | 480 | 3 | 75 | 96 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102130 |  | MC | Telemecanique | LC1D115 | 5 | 115 | 600 | 3 | 25 | 480 | 3 | 75 | 96 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102130 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 25 | 480 | 3 | 75 | 96 | 7920 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102131 | C | CB | Square D | KCL34250 | 65 | 250 | 480 | 3 | 25 | 480 | 3 | 100 | 124 | 8316 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102131 |  | MC | Telemecanique | LC1D150 | 5 | 150 | 600 | 3 | 25 | 480 | 3 | 100 | 124 | 8316 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102131 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 25 | 480 | 3 | 100 | 124 | 8316 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102132 | C | CB | Square D | KCL34250 | 65 | 250 | 480 | 3 | 25 | 480 | 3 | 125 | 156 | 8316 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102132 |  | MC | Telemecanique | LC1F185 | 5 | 185 | 600 | 3 | 25 | 480 | 3 | 125 | 156 | 8316 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102132 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 25 | 480 | 3 | 125 | 156 | 8316 | 1 | E169933 V1 S2 | E40610 V12 S20
SE102133 | D | ICB | Square D | LHL3625032M | - | 250 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102133 |  | MC | Telemecanique | LC1F225 | 10 | 225 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102133 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102134 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102134 |  | MC | Telemecanique | LC1F265 | 18 | 265 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102134 |  | STR | Telemecanique | ATS48C25Y | 18 | 250 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102135 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102135 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102135 |  | STR | Telemecanique | ATS48C32Y | 18 | 320 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 28800 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102136 | D | ICB | Square D | MHL3660040M | - | 600 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102136 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102136 |  | STR | Telemecanique | ATS48C41Y | 65 | 410 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102137 | D | ICB | Square D | MHL3660042M | - | 600 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102137 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102137 |  | STR | Telemecanique | ATS48C48Y | 65 | 480 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102138 | D | ICB | Square D | MHL3660044M | - | 600 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102138 |  | MC | Telemecanique | LC1F630 | 42 | 630 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102138 |  | STR | Telemecanique | ATS48C59Y | 65 | 590 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102139 | D | ICB | Square D | MHL3680045M | - | 800 | 600 | 3 | 30 | 480 | 3 | 500 | 590 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102139 |  | MC | Telemecanique | LC1F630 | 42 | 630 | 600 | 3 | 30 | 480 | 3 | 500 | 590 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102139 |  | STR | Telemecanique | ATS48C66Y | 65 | 660 | 600 | 3 | 30 | 480 | 3 | 500 | 590 | 50400 | 1, 5 | E169933 V1 S2 | E40610 V12 S20
SE102140 | C | CB | Square D | FCL34020 | 100 | 20 | 480 | 3 | 65 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102140 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102140 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102141 | C | CB | Square D | FCL34030 | 100 | 30 | 480 | 3 | 65 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102141 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102141 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102142 | C | CB | Square D | FCL34030 | 100 | 30 | 480 | 3 | 65 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102142 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102142 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102143 | C | CB | Square D | FCL34045 | 100 | 45 | 480 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102143 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102143 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102144 | C | CB | Square D | FCL34045 | 100 | 45 | 480 | 3 | 65 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102144 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102144 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102145 | C | CB | Square D | FCL34060 | 100 | 60 | 480 | 3 | 65 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102145 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102145 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102146 | C | CB | Square D | FCL34050 | 100 | 50 | 480 | 3 | 65 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102146 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102146 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102147 | C | CB | Square D | FCL34025 | 65 | 25 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102147 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102147 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102148 | C | CB | Square D | KIL36110 | 200 | 110 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102148 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102148 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102149 | C | CB | Square D | FCL34080 | 100 | 80 | 480 | 3 | 65 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE102149 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE102149 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE102150 | C | CB | Square D | FCL34040 | 65 | 40 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102150 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102150 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102151 | C | CB | Square D | KIL36110 | 200 | 110 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102151 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102151 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102152 | C | CB | Square D | KIL36110 | 200 | 110 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102152 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102152 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102153 | C | CB | Square D | FCL34050 | 65 | 50 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102153 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102153 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102154 | C | CB | Square D | KIL36110 | 200 | 110 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE102154 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE102154 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE102155 | C | CB | Square D | KIL36110 | 200 | 110 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102155 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102155 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102156 | C | CB | Square D | FCL34060 | 65 | 60 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102156 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102156 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102157 | C | CB | Square D | KIL36125 | 200 | 125 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE102157 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE102157 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE102158 | C | CB | Square D | KIL36110 | 200 | 110 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE102158 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE102158 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE102159 | C | CB | Square D | FCL34080 | 65 | 80 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE102159 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE102159 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE102160 | C | CB | Square D | KCL34175 | 100 | 175 | 480 | 3 | 65 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE102160 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE102160 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE102161 | C | CB | Square D | KIL36150 | 200 | 150 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE102161 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE102161 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE102162 | C | CB | Square D | KIL36110 | 200 | 110 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102162 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102162 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102163 | C | CB | Square D | KCL34200 | 100 | 200 | 480 | 3 | 65 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE102163 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 65 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE102163 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 65 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE102164 | C | CB | Square D | KCL34200 | 100 | 200 | 480 | 3 | 65 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE102164 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE102164 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE102165 | C | CB | Square D | KIL36110 | 200 | 110 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102165 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102165 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102166 | C | CB | Square D | LIL36300 | 200 | 300 | 600 | 3 | 65 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE102166 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 65 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE102166 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 65 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE102167 | C | CB | Square D | KCL34225 | 100 | 225 | 480 | 3 | 65 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE102167 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 65 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE102167 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 65 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE102168 | C | CB | Square D | KIL36110 | 200 | 110 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE102168 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE102168 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE102169 | C | CB | Square D | LIL36450 | 200 | 450 | 600 | 3 | 65 | 208 | 3 | 75 | 211 | 28800 | 1, 6, 7(p) | E40610 V12 S20
SE102169 |  | STR | Telemecanique | ATS48C25Y | 18 | 250 | 600 | 3 | 65 | 208 | 3 | 75 | 211 | 28800 | 1, 6, 7(p) | E40610 V12 S20
SE102169 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 65 | 208 | 3 | 75 | 211 | 28800 | 1, 6, 7(p) | E40610 V12 S20
SE102170 | C | CB | Square D | LIL36300 | 200 | 300 | 600 | 3 | 65 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE102170 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 65 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE102170 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 65 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE102171 | C | CB | Square D | KIL36125 | 200 | 125 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE102171 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE102171 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE102172 | C | CB | Square D | LIL36450 | 200 | 450 | 600 | 3 | 65 | 208 | 3 | 100 | 273 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE102172 |  | STR | Telemecanique | ATS48C32Y | 18 | 320 | 600 | 3 | 65 | 208 | 3 | 100 | 273 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE102172 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 65 | 208 | 3 | 100 | 273 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE102173 | C | CB | Square D | LIL36450 | 200 | 450 | 600 | 3 | 65 | 240 | 3 | 100 | 248 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE102173 |  | STR | Telemecanique | ATS48C25Y | 18 | 250 | 600 | 3 | 65 | 240 | 3 | 100 | 248 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE102173 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 65 | 240 | 3 | 100 | 248 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE102174 | C | CB | Square D | KCL34200 | 65 | 200 | 480 | 3 | 65 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE102174 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE102174 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE102175 | C | CB | Square D | MHL36500 | 65 | 500 | 600 | 3 | 65 | 208 | 3 | 125 | 343 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE102175 |  | STR | Telemecanique | ATS48C41Y | 18 | 410 | 600 | 3 | 65 | 208 | 3 | 125 | 343 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE102175 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 65 | 208 | 3 | 125 | 343 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE102176 | C | CB | Square D | LIL36450 | 200 | 450 | 600 | 3 | 65 | 240 | 3 | 125 | 312 | 28800 | 1, 6, 7(i) | E40610 V12 S20
SE102176 |  | STR | Telemecanique | ATS48C32Y | 18 | 320 | 600 | 3 | 65 | 240 | 3 | 125 | 312 | 28800 | 1, 6, 7(i) | E40610 V12 S20
SE102176 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 65 | 240 | 3 | 125 | 312 | 28800 | 1, 6, 7(i) | E40610 V12 S20
SE102177 | C | CB | Square D | KCL34225 | 65 | 225 | 480 | 3 | 65 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE102177 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE102177 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE102178 | C | CB | Square D | MHL36600 | 65 | 600 | 600 | 3 | 65 | 208 | 3 | 150 | 396 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE102178 |  | STR | Telemecanique | ATS48C48Y | 18 | 480 | 600 | 3 | 65 | 208 | 3 | 150 | 396 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE102178 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 65 | 208 | 3 | 150 | 396 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE102179 | C | CB | Square D | MHL36600 | 65 | 600 | 600 | 3 | 65 | 240 | 3 | 150 | 360 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE102179 |  | STR | Telemecanique | ATS48C41Y | 18 | 410 | 600 | 3 | 65 | 240 | 3 | 150 | 360 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE102179 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 65 | 240 | 3 | 150 | 360 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE102180 | C | CB | Square D | LIL36300 | 200 | 300 | 600 | 3 | 65 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE102180 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 65 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE102180 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 65 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE102181 | C | CB | Square D | MHL36800 | 65 | 800 | 600 | 3 | 65 | 208 | 3 | 200 | 528 | 50400 | 1, 6, 7(q) | E40610 V12 S20
SE102181 |  | STR | Telemecanique | ATS48C66Y | 30 | 660 | 600 | 3 | 65 | 208 | 3 | 200 | 528 | 50400 | 1, 6, 7(q) | E40610 V12 S20
SE102181 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 65 | 208 | 3 | 200 | 528 | 50400 | 1, 6, 7(q) | E40610 V12 S20
SE102182 | C | CB | Square D | MHL36800 | 65 | 800 | 600 | 3 | 65 | 240 | 3 | 200 | 480 | 50400 | 1, 6, 7(r) | E40610 V12 S20
SE102182 |  | STR | Telemecanique | ATS48C59Y | 30 | 590 | 600 | 3 | 65 | 240 | 3 | 200 | 480 | 50400 | 1, 6, 7(r) | E40610 V12 S20
SE102182 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 65 | 240 | 3 | 200 | 480 | 50400 | 1, 6, 7(r) | E40610 V12 S20
SE102183 | C | CB | Square D | LIL36450 | 200 | 450 | 600 | 3 | 65 | 480 | 3 | 200 | 240 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE102183 |  | STR | Telemecanique | ATS48C25Y | 18 | 250 | 600 | 3 | 65 | 480 | 3 | 200 | 240 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE102183 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 65 | 480 | 3 | 200 | 240 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE102184 | C | CB | Square D | MHL36900 | 65 | 900 | 600 | 3 | 65 | 240 | 3 | 250 | 604 | 50400 | 1, 6, 7(q) | E40610 V12 S20
SE102184 |  | STR | Telemecanique | ATS48C66Y | 30 | 660 | 600 | 3 | 65 | 240 | 3 | 250 | 604 | 50400 | 1, 6, 7(q) | E40610 V12 S20
SE102184 |  | MC | Telemecanique | LC1F630 | 30 | 630 | 600 | 3 | 65 | 240 | 3 | 250 | 604 | 50400 | 1, 6, 7(q) | E40610 V12 S20
SE102185 | C | CB | Square D | LIL36450 | 200 | 450 | 600 | 3 | 65 | 480 | 3 | 250 | 302 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE102185 |  | STR | Telemecanique | ATS48C32Y | 18 | 320 | 600 | 3 | 65 | 480 | 3 | 250 | 302 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE102185 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 65 | 480 | 3 | 250 | 302 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE102186 | C | CB | Square D | MHL36600 | 65 | 600 | 600 | 3 | 65 | 480 | 3 | 300 | 361 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE102186 |  | STR | Telemecanique | ATS48C41Y | 18 | 410 | 600 | 3 | 65 | 480 | 3 | 300 | 361 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE102186 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 65 | 480 | 3 | 300 | 361 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE102187 | C | CB | Square D | MHL36600 | 65 | 600 | 600 | 3 | 65 | 480 | 3 | 350 | 414 | 50400 | 1, 6, 7(f) | E40610 V12 S20
SE102187 |  | STR | Telemecanique | ATS48C48Y | 18 | 480 | 600 | 3 | 65 | 480 | 3 | 350 | 414 | 50400 | 1, 6, 7(f) | E40610 V12 S20
SE102187 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 65 | 480 | 3 | 350 | 414 | 50400 | 1, 6, 7(f) | E40610 V12 S20
SE102188 | C | CB | Square D | MHL36800 | 65 | 800 | 600 | 3 | 65 | 480 | 3 | 400 | 477 | 50400 | 1, 6, 7(r) | E40610 V12 S20
SE102188 |  | STR | Telemecanique | ATS48C59Y | 30 | 590 | 600 | 3 | 65 | 480 | 3 | 400 | 477 | 50400 | 1, 6, 7(r) | E40610 V12 S20
SE102188 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 65 | 480 | 3 | 400 | 477 | 50400 | 1, 6, 7(r) | E40610 V12 S20
SE102189 | C | CB | Square D | MHL36900 | 65 | 900 | 600 | 3 | 65 | 480 | 3 | 500 | 590 | 50400 | 1, 6, 7(q) | E40610 V12 S20
SE102189 |  | STR | Telemecanique | ATS48C66Y | 30 | 660 | 600 | 3 | 65 | 480 | 3 | 500 | 590 | 50400 | 1, 6, 7(q) | E40610 V12 S20
SE102189 |  | MC | Telemecanique | LC1F630 | 30 | 630 | 600 | 3 | 65 | 480 | 3 | 500 | 590 | 50400 | 1, 6, 7(q) | E40610 V12 S20

## ATS48-IEC-PwrPact
Issued: 2007-04-09
Last Revised: 2007-04-20
Contactor is to be used as a shorting contactor only and may be optionally provided
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Min Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE153740 | C | CB | Square D | HLL36020 | 125 | 20 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153740 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153740 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153741 | C | CB | Square D | HLL36030 | 125 | 30 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153741 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153741 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153742 | C | CB | Square D | HLL36030 | 125 | 30 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153742 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153742 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153743 | C | CB | Square D | HLL36045 | 125 | 45 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153743 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153743 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153744 | C | CB | Square D | HLL36045 | 125 | 45 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153744 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153744 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153745 | C | CB | Square D | HLL36060 | 125 | 60 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153745 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153745 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153746 | C | CB | Square D | HLL36050 | 125 | 50 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153746 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153746 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153747 | C | CB | Square D | HLL36025 | 100 | 25 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153747 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153747 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153748 | C | CB | Square D | HLL36110 | 125 | 110 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153748 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153748 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153749 | C | CB | Square D | HLL36080 | 125 | 80 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE153749 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE153749 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE153750 | C | CB | Square D | HLL36040 | 100 | 40 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153750 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153750 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153751 | C | CB | Square D | HLL36110 | 125 | 110 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153751 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153751 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153752 | C | CB | Square D | HLL36110 | 125 | 110 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153752 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153752 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153753 | C | CB | Square D | HLL36050 | 100 | 50 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153753 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153753 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153754 | C | CB | Square D | HLL36110 | 125 | 110 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE153754 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE153754 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE153755 | C | CB | Square D | HLL36110 | 125 | 110 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153755 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153755 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153756 | C | CB | Square D | HLL36060 | 100 | 60 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153756 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153756 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153757 | C | CB | Square D | HLL36125 | 125 | 125 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE153757 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE153757 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE153758 | C | CB | Square D | HLL36110 | 125 | 110 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE153758 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE153758 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE153759 | C | CB | Square D | HLL36080 | 100 | 80 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE153759 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE153759 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE153760 | C | CB | Square D | JLL36175 | 125 | 175 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE153760 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE153760 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE153761 | C | CB | Square D | HLL36150 | 125 | 150 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE153761 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE153761 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE153762 | C | CB | Square D | HLL36110 | 100 | 110 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153762 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153762 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153763 | C | CB | Square D | JLL36200 | 125 | 200 | 600 | 3 | 65 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE153763 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 65 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE153763 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 65 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE153764 | C | CB | Square D | JLL36200 | 125 | 200 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE153764 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE153764 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE153765 | C | CB | Square D | HLL36110 | 100 | 110 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153765 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153765 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153766 | C | CB | Square D | JLL36225 | 125 | 225 | 600 | 3 | 65 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE153766 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 65 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE153766 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 65 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE153767 | C | CB | Square D | HLL36110 | 100 | 110 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE153767 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE153767 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE153768 | C | CB | Square D | HLL36125 | 100 | 125 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE153768 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE153768 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE153769 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE153769 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE153769 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE153770 | C | CB | Square D | JLL36225 | 100 | 225 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE153770 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE153770 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20

## ATS48-IEC-Fuse
Issued: 2007-04-20
Last Revised: 2007-04-20
Contactor is to be used as a shorting contactor only and may be optionally provided
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Min Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE500260 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500260 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500260 |  | F | Any | Class J Fuse | 200 | 20 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500260 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
500260 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500261 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500261 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500261 |  | F | Any | Class J Fuse | 200 | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500261 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500261 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500262 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500262 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500262 |  | F | Any | Class J Fuse | 200 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500262 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500262 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500263 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500263 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500263 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500263 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500263 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500264 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500264 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500264 |  | F | Any | Class J Fuse | 200 | 40 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500264 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500264 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500265 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500265 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500265 |  | F | Any | Class J Fuse | 200 | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500265 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500265 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500266 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500266 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500266 |  | F | Any | Class J Fuse | 200 | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500266 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500266 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500267 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500267 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500267 |  | F | Any | Class J Fuse | 200 | 25 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500267 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500267 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500268 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500268 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500268 |  | F | Any | Class J Fuse | 200 | 80 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500268 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500268 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500269 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500269 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500269 |  | F | Any | Class J Fuse | 200 | 70 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500269 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500269 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500270 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500270 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500270 |  | F | Any | Class J Fuse | 200 | 35 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500270 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500270 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500271 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500271 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500271 |  | F | Any | Class J Fuse | 200 | 30 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500271 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500271 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500272 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500272 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500272 |  | F | Any | Class J Fuse | 200 | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500272 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500272 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500273 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500273 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500273 |  | F | Any | Class J Fuse | 200 | 90 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500273 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500273 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500274 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500274 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500274 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500274 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500274 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500275 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500275 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500275 |  | F | Any | Class J Fuse | 200 | 40 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500275 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500275 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500276 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500276 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500276 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500276 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500276 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500277 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500277 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500277 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500277 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500277 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500278 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500278 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500278 |  | F | Any | Class J Fuse | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500278 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500278 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500279 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500279 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500279 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500279 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500279 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500280 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500280 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500280 |  | F | Any | Class J Fuse | 200 | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500280 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500280 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500281 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500281 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500281 |  | F | Any | Class J Fuse | 200 | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500281 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500281 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500282 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500282 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500282 |  | F | Any | Class J Fuse | 200 | 70 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500282 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500282 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500283 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500283 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500283 |  | F | Any | Class J Fuse | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500283 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500283 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500284 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500284 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500284 |  | F | Any | Class J Fuse | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500284 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500284 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500285 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500285 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500285 |  | F | Any | Class J Fuse | 200 | 175 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500285 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500285 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500286 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500286 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500286 |  | F | Any | Class J Fuse | 200 | 90 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500286 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500286 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500287 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500287 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500287 |  | F | Any | Class J Fuse | 200 | 70 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500287 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500287 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500288 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500288 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500288 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500288 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500288 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500289 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500289 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500289 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500289 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500289 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500290 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500290 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500290 |  | F | Any | Class J Fuse | 200 | 110 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500290 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500290 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500291 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500291 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500291 |  | F | Any | Class J Fuse | 200 | 90 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500291 |  | STR | Telemecanique | ATS48D62Y | 10 | 62 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500291 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500292 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500292 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500292 |  | F | Any | Class J Fuse | 200 | 300 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500292 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500292 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500293 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500293 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500293 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500293 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500293 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500294 | A | DS | Square D | KHL36000M | 35 | 250 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500294 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500294 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500294 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500294 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500295 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500295 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500295 |  | F | Any | Class J Fuse | 200 | 110 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500295 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500295 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500296 | A | DS | Square D | LHL36000M | 65 | 400 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 28800 | 1, 6, 7(p) | E40610 V12 S20
SE500296 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 28800 | 1, 6, 7(p) | E40610 V12 S20
SE500296 |  | F | Any | Class J Fuse | 200 | 350 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 28800 | 1, 6, 7(p) | E40610 V12 S20
SE500296 |  | STR | Telemecanique | ATS48C25Y | 18 | 250 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 28800 | 1, 6, 7(p) | E40610 V12 S20
SE500296 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 28800 | 1, 6, 7(p) | E40610 V12 S20
SE500297 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500297 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500297 |  | F | Any | Class J Fuse | 200 | 350 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500297 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500297 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500298 | A | DS | Square D | KHL36000M | 35 | 250 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500298 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500298 |  | F | Any | Class J Fuse | 200 | 175 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500298 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500298 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500299 | A | DS | Square D | KHL36000M | 25 | 250 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500299 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500299 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500299 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500299 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500300 | A | DS | Square D | LHL36000M | 65 | 400 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500300 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500300 |  | F | Any | Class J Fuse | 200 | 450 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500300 |  | STR | Telemecanique | ATS48C32Y | 18 | 320 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500300 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500301 | A | DS | Square D | LHL36000M | 65 | 400 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500301 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500301 |  | F | Any | Class J Fuse | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500301 |  | STR | Telemecanique | ATS48C25Y | 18 | 250 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500301 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500302 | A | DS | Square D | KHL36000M | 35 | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500302 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500302 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500302 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500302 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500303 | A | DS | Square D | KHL36000M | 25 | 250 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500303 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500303 |  | F | Any | Class J Fuse | 200 | 175 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500303 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500303 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500304 | A | DS | Square D | MHL360006M | 65 | 600 | 600 | 3 | 100 | 208 | 3 | 125 | 343 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE500304 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 208 | 3 | 125 | 343 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE500304 |  | F | Any | Class J Fuse | 200 | 600 | 600 | 3 | 100 | 208 | 3 | 125 | 343 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE500304 |  | STR | Telemecanique | ATS48C41Y | 18 | 410 | 600 | 3 | 100 | 208 | 3 | 125 | 343 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE500304 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 208 | 3 | 125 | 343 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE500305 | A | DS | Square D | LHL36000M | 65 | 400 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 28800 | 1, 6, 7(i) | E40610 V12 S20
SE500305 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 28800 | 1, 6, 7(i) | E40610 V12 S20
SE500305 |  | F | Any | Class J Fuse | 200 | 500 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 28800 | 1, 6, 7(i) | E40610 V12 S20
SE500305 |  | STR | Telemecanique | ATS48C32Y | 18 | 320 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 28800 | 1, 6, 7(i) | E40610 V12 S20
SE500305 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 28800 | 1, 6, 7(i) | E40610 V12 S20
SE500306 | A | DS | Square D | KHL36000M | 35 | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500306 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500306 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500306 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500306 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500307 | A | DS | Square D | KHL36000M | 25 | 250 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500307 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500307 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500307 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500307 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500308 | A | DS | Square D | MHL360006M | 65 | 600 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500308 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500308 |  | F | Any | Class J Fuse | 200 | 600 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500308 |  | STR | Telemecanique | ATS48C41Y | 18 | 410 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500308 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500309 | A | DS | Square D | KHL36000M | 35 | 250 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500309 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500309 |  | F | Any | Class J Fuse | 200 | 300 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500309 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500309 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500310 | A | DS | Square D | KHL36000M | 25 | 250 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500310 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500310 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500310 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500310 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500311 | A | DS | Square D | LHL36000M | 35 | 400 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500311 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500311 |  | F | Any | Class J Fuse | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500311 |  | STR | Telemecanique | ATS48C25Y | 18 | 250 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500311 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500312 | A | DS | Square D | LHL36000M | 25 | 400 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500312 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500312 |  | F | Any | Class J Fuse | 200 | 350 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500312 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500312 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500313 | A | DS | Square D | LHL36000M | 35 | 400 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500313 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500313 |  | F | Any | Class J Fuse | 200 | 500 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500313 |  | STR | Telemecanique | ATS48C32Y | 18 | 320 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500313 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500314 | A | DS | Square D | LHL36000M | 25 | 400 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500314 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500314 |  | F | Any | Class J Fuse | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500314 |  | STR | Telemecanique | ATS48C25Y | 18 | 250 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500314 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500315 | A | DS | Square D | MHL360006M | 65 | 600 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500315 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500315 |  | F | Any | Class J Fuse | 200 | 600 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500315 |  | STR | Telemecanique | ATS48C41Y | 18 | 410 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500315 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500316 | A | DS | Square D | MHL360006M | 25 | 600 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500316 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500316 |  | F | Any | Class J Fuse | 200 | 500 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500316 |  | STR | Telemecanique | ATS48C32Y | 18 | 320 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500316 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500317 | A | DS | Square D | MHL360006M | 25 | 600 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE500317 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE500317 |  | F | Any | Class J Fuse | 200 | 600 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE500317 |  | STR | Telemecanique | ATS48C41Y | 18 | 410 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE500317 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE550000 | A | DS | Square D | HLL36000S15 | 125 | 150 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550000 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550000 |  | F | Any | Class J Fuse | 200 | 20 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550000 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550000 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550001 | A | DS | Square D | HLL36000S15 | 125 | 150 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550001 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550001 |  | F | Any | Class J Fuse | 200 | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550001 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550001 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550002 | A | DS | Square D | HLL36000S15 | 125 | 150 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550002 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550002 |  | F | Any | Class J Fuse | 200 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550002 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550002 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550003 | A | DS | Square D | HLL36000S15 | 125 | 150 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550003 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550003 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550003 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550003 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550004 | A | DS | Square D | HLL36000S15 | 125 | 150 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550004 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550004 |  | F | Any | Class J Fuse | 200 | 40 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550004 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550004 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550005 | A | DS | Square D | HLL36000S15 | 125 | 150 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550005 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550005 |  | F | Any | Class J Fuse | 200 | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550005 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550005 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550006 | A | DS | Square D | HLL36000S15 | 125 | 150 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550006 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550006 |  | F | Any | Class J Fuse | 200 | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550006 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550006 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550007 | A | DS | Square D | HLL36000S15 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550007 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550007 |  | F | Any | Class J Fuse | 200 | 25 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550007 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550007 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550008 | A | DS | Square D | HLL36000S15 | 125 | 150 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550008 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550008 |  | F | Any | Class J Fuse | 200 | 80 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550008 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550008 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550009 | A | DS | Square D | HLL36000S15 | 125 | 150 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550009 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550009 |  | F | Any | Class J Fuse | 200 | 70 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550009 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550009 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550010 | A | DS | Square D | HLL36000S15 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550010 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550010 |  | F | Any | Class J Fuse | 200 | 35 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550010 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550010 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550011 | A | DS | Square D | HLL36000S15 | 50 | 150 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550011 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550011 |  | F | Any | Class J Fuse | 200 | 30 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550011 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550011 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550012 | A | DS | Square D | HLL36000S15 | 125 | 150 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550012 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550012 |  | F | Any | Class J Fuse | 200 | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550012 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550012 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550013 | A | DS | Square D | HLL36000S15 | 125 | 150 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550013 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550013 |  | F | Any | Class J Fuse | 200 | 90 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550013 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550013 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550014 | A | DS | Square D | HLL36000S15 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550014 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550014 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550014 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550014 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550015 | A | DS | Square D | HLL36000S15 | 50 | 150 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550015 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550015 |  | F | Any | Class J Fuse | 200 | 40 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550015 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550015 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550016 | A | DS | Square D | HLL36000S15 | 125 | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550016 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550016 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550016 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550016 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550017 | A | DS | Square D | HLL36000S15 | 125 | 150 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550017 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550017 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550017 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550017 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550018 | A | DS | Square D | HLL36000S15 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550018 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550018 |  | F | Any | Class J Fuse | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550018 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550018 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550019 | A | DS | Square D | HLL36000S15 | 50 | 150 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550019 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550019 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550019 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550019 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550020 | A | DS | Square D | HLL36000S15 | 125 | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550020 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550020 |  | F | Any | Class J Fuse | 200 | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550020 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550020 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550021 | A | DS | Square D | HLL36000S15 | 125 | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550021 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550021 |  | F | Any | Class J Fuse | 200 | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550021 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550021 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550022 | A | DS | Square D | HLL36000S15 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550022 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550022 |  | F | Any | Class J Fuse | 200 | 70 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550022 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550022 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550023 | A | DS | Square D | HLL36000S15 | 50 | 150 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550023 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550023 |  | F | Any | Class J Fuse | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550023 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550023 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550024 | A | DS | Square D | JLL36000S17 | 125 | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550024 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550024 |  | F | Any | Class J Fuse | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550024 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550024 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550025 | A | DS | Square D | HLL36000S15 | 125 | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550025 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550025 |  | F | Any | Class J Fuse | 200 | 175 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550025 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550025 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550026 | A | DS | Square D | HLL36000S15 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550026 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550026 |  | F | Any | Class J Fuse | 200 | 90 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550026 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550026 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550027 | A | DS | Square D | HLL36000S15 | 50 | 150 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550027 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550027 |  | F | Any | Class J Fuse | 200 | 70 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550027 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550027 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550028 | A | DS | Square D | JLL36000S25 | 125 | 250 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550028 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550028 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550028 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550028 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550029 | A | DS | Square D | JLL36000S17 | 125 | 175 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550029 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550029 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550029 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550029 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550030 | A | DS | Square D | HLL36000S15 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550030 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550030 |  | F | Any | Class J Fuse | 200 | 110 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550030 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550030 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550031 | A | DS | Square D | HLL36000S15 | 50 | 150 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550031 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550031 |  | F | Any | Class J Fuse | 200 | 90 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550031 |  | STR | Telemecanique | ATS48D62Y | 10 | 62 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550031 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550032 | A | DS | Square D | JLL36000S25 | 125 | 250 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550032 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550032 |  | F | Any | Class J Fuse | 200 | 300 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550032 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550032 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550033 | A | DS | Square D | JLL36000S25 | 125 | 250 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550033 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550033 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550033 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550033 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550034 | A | DS | Square D | HLL36000S15 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550034 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550034 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550034 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550034 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550035 | A | DS | Square D | HLL36000S15 | 50 | 150 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550035 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550035 |  | F | Any | Class J Fuse | 200 | 110 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550035 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550035 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550036 | A | DS | Square D | JLL36000S25 | 125 | 250 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550036 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550036 |  | F | Any | Class J Fuse | 200 | 350 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550036 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550036 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550037 | A | DS | Square D | HLL36000S15 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550037 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550037 |  | F | Any | Class J Fuse | 200 | 175 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550037 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550037 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550038 | A | DS | Square D | HLL36000S15 | 50 | 150 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550038 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550038 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550038 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550038 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550039 | A | DS | Square D | JLL36000S17 | 100 | 175 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550039 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550039 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550039 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550039 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550040 | A | DS | Square D | HLL36000S15 | 50 | 150 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550040 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550040 |  | F | Any | Class J Fuse | 200 | 175 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550040 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550040 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550041 | A | DS | Square D | JLL36000S25 | 100 | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550041 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550041 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550041 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550041 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550042 | A | DS | Square D | HLL36000S15 | 50 | 175 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550042 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550042 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550042 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550042 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550043 | A | DS | Square D | JLL36000S25 | 100 | 250 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550043 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550043 |  | F | Any | Class J Fuse | 200 | 300 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550043 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550043 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550044 | A | DS | Square D | JLL36000S17 | 50 | 250 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550044 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550044 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550044 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550044 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20

## ATS48-NEMA
Issued: 2007-04-27
Last Revised: 2007-04-27
Contactor is to be used as a shorting contactor only and may be optionally provided
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Min Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE102190 | C | CB | Square D | FCL34020 | 100 | 20 | 480 | 3 | 65 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102190 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102190 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102191 | C | CB | Square D | FCL34030 | 100 | 30 | 480 | 3 | 65 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102191 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102191 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102192 | C | CB | Square D | FCL34030 | 100 | 30 | 480 | 3 | 65 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102192 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102192 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102193 | C | CB | Square D | FCL34045 | 100 | 45 | 480 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102193 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102193 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102194 | C | CB | Square D | FCL34045 | 100 | 45 | 480 | 3 | 65 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102194 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102194 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102195 | C | CB | Square D | FCL34060 | 100 | 60 | 480 | 3 | 65 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102195 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102195 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102196 | C | CB | Square D | FCL34050 | 100 | 50 | 480 | 3 | 65 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102196 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102196 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102197 | C | CB | Square D | FCL34025 | 65 | 25 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102197 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102197 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102198 | C | CB | Square D | KIL36110 | 200 | 110 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102198 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102198 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102199 | C | CB | Square D | FCL34080 | 100 | 80 | 480 | 3 | 65 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE102199 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE102199 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE102200 | C | CB | Square D | FCL34040 | 65 | 40 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102200 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102200 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102201 | C | CB | Square D | KIL36110 | 200 | 110 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102201 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102201 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102202 | C | CB | Square D | KIL36110 | 200 | 110 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102202 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102202 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102203 | C | CB | Square D | FCL34050 | 65 | 50 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102203 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102203 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102204 | C | CB | Square D | KIL36110 | 200 | 110 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE102204 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE102204 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE102205 | C | CB | Square D | KIL36110 | 200 | 110 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102205 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102205 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102206 | C | CB | Square D | FCL34060 | 65 | 60 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102206 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102206 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE102207 | C | CB | Square D | KIL36125 | 200 | 125 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE102207 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE102207 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE102208 | C | CB | Square D | KIL36110 | 200 | 110 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE102208 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE102208 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE102209 | C | CB | Square D | FCL34080 | 65 | 80 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE102209 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE102209 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE102210 | C | CB | Square D | KCL34175 | 100 | 175 | 480 | 3 | 65 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE102210 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE102210 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE102211 | C | CB | Square D | KIL36150 | 200 | 150 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE102211 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE102211 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE102212 | C | CB | Square D | KIL36110 | 200 | 110 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102212 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102212 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102213 | C | CB | Square D | KCL34200 | 100 | 200 | 480 | 3 | 65 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE102213 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 65 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE102213 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 65 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE102214 | C | CB | Square D | KCL34200 | 100 | 200 | 480 | 3 | 65 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE102214 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE102214 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE102215 | C | CB | Square D | KIL36110 | 200 | 110 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102215 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102215 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE102216 | C | CB | Square D | LIL36300 | 200 | 300 | 600 | 3 | 65 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE102216 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 65 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE102216 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 65 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE102217 | C | CB | Square D | KCL34225 | 100 | 225 | 480 | 3 | 65 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE102217 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 65 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE102217 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 65 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE102218 | C | CB | Square D | KIL36110 | 200 | 110 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE102218 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE102218 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE102219 | C | CB | Square D | LIL36450 | 200 | 450 | 600 | 3 | 65 | 208 | 3 | 75 | 211 | 28800 | 1, 6, 7(p) | E40610 V12 S20
SE102219 |  | STR | Telemecanique | ATS48C25Y | 18 | 250 | 600 | 3 | 65 | 208 | 3 | 75 | 211 | 28800 | 1, 6, 7(p) | E40610 V12 S20
SE102219 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 65 | 208 | 3 | 75 | 211 | 28800 | 1, 6, 7(p) | E40610 V12 S20
SE102220 | C | CB | Square D | LIL36300 | 200 | 300 | 600 | 3 | 65 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE102220 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 65 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE102220 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 65 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE102221 | C | CB | Square D | KIL36125 | 200 | 125 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE102221 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE102221 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE102222 | C | CB | Square D | LIL36450 | 200 | 450 | 600 | 3 | 65 | 208 | 3 | 100 | 273 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE102222 |  | STR | Telemecanique | ATS48C32Y | 18 | 320 | 600 | 3 | 65 | 208 | 3 | 100 | 273 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE102222 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 65 | 208 | 3 | 100 | 273 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE102223 | C | CB | Square D | LIL36450 | 200 | 450 | 600 | 3 | 65 | 240 | 3 | 100 | 248 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE102223 |  | STR | Telemecanique | ATS48C25Y | 18 | 250 | 600 | 3 | 65 | 240 | 3 | 100 | 248 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE102223 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 65 | 240 | 3 | 100 | 248 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE102224 | C | CB | Square D | KCL34200 | 65 | 200 | 480 | 3 | 65 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE102224 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE102224 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE102225 | C | CB | Square D | MHL36500 | 65 | 500 | 600 | 3 | 65 | 208 | 3 | 125 | 343 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE102225 |  | STR | Telemecanique | ATS48C41Y | 18 | 410 | 600 | 3 | 65 | 208 | 3 | 125 | 343 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE102225 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 65 | 208 | 3 | 125 | 343 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE102226 | C | CB | Square D | LIL36450 | 200 | 450 | 600 | 3 | 65 | 240 | 3 | 125 | 312 | 28800 | 1, 6, 7(i) | E40610 V12 S20
SE102226 |  | STR | Telemecanique | ATS48C32Y | 18 | 320 | 600 | 3 | 65 | 240 | 3 | 125 | 312 | 28800 | 1, 6, 7(i) | E40610 V12 S20
SE102226 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 65 | 240 | 3 | 125 | 312 | 28800 | 1, 6, 7(i) | E40610 V12 S20
SE102227 | C | CB | Square D | KCL34225 | 65 | 225 | 480 | 3 | 65 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE102227 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE102227 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE102228 | C | CB | Square D | MHL36600 | 65 | 600 | 600 | 3 | 65 | 208 | 3 | 150 | 396 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE102228 |  | STR | Telemecanique | ATS48C48Y | 18 | 480 | 600 | 3 | 65 | 208 | 3 | 150 | 396 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE102228 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 65 | 208 | 3 | 150 | 396 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE102229 | C | CB | Square D | MHL36600 | 65 | 600 | 600 | 3 | 65 | 240 | 3 | 150 | 360 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE102229 |  | STR | Telemecanique | ATS48C41Y | 18 | 410 | 600 | 3 | 65 | 240 | 3 | 150 | 360 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE102229 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 65 | 240 | 3 | 150 | 360 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE102230 | C | CB | Square D | LIL36300 | 200 | 300 | 600 | 3 | 65 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE102230 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 65 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE102230 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 65 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE102231 | C | CB | Square D | MHL36800 | 65 | 800 | 600 | 3 | 65 | 208 | 3 | 200 | 528 | 50400 | 1, 6, 7(q) | E40610 V12 S20
SE102231 |  | STR | Telemecanique | ATS48C66Y | 30 | 660 | 600 | 3 | 65 | 208 | 3 | 200 | 528 | 50400 | 1, 6, 7(q) | E40610 V12 S20
SE102231 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 65 | 208 | 3 | 200 | 528 | 50400 | 1, 6, 7(q) | E40610 V12 S20
SE102232 | C | CB | Square D | MHL36800 | 65 | 800 | 600 | 3 | 65 | 240 | 3 | 200 | 480 | 50400 | 1, 6, 7(r) | E40610 V12 S20
SE102232 |  | STR | Telemecanique | ATS48C59Y | 30 | 590 | 600 | 3 | 65 | 240 | 3 | 200 | 480 | 50400 | 1, 6, 7(r) | E40610 V12 S20
SE102232 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 65 | 240 | 3 | 200 | 480 | 50400 | 1, 6, 7(r) | E40610 V12 S20
SE102233 | C | CB | Square D | LIL36450 | 200 | 450 | 600 | 3 | 65 | 480 | 3 | 200 | 240 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE102233 |  | STR | Telemecanique | ATS48C25Y | 18 | 250 | 600 | 3 | 65 | 480 | 3 | 200 | 240 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE102233 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 65 | 480 | 3 | 200 | 240 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE102234 | C | CB | Square D | MHL36900 | 65 | 900 | 600 | 3 | 65 | 240 | 3 | 250 | 604 | 50400 | 1, 6, 7(q) | E40610 V12 S20
SE102234 |  | STR | Telemecanique | ATS48C66Y | 30 | 660 | 600 | 3 | 65 | 240 | 3 | 250 | 604 | 50400 | 1, 6, 7(r) | E40610 V12 S20
SE102234 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 65 | 240 | 3 | 250 | 604 | 50400 | 1, 6, 7(r) | E40610 V12 S20
SE102235 | C | CB | Square D | LIL36450 | 200 | 450 | 600 | 3 | 65 | 480 | 3 | 250 | 302 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE102235 |  | STR | Telemecanique | ATS48C32Y | 18 | 320 | 600 | 3 | 65 | 480 | 3 | 250 | 302 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE102235 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 65 | 480 | 3 | 250 | 302 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE102236 | C | CB | Square D | MHL36600 | 65 | 600 | 600 | 3 | 65 | 480 | 3 | 300 | 361 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE102236 |  | STR | Telemecanique | ATS48C41Y | 18 | 410 | 600 | 3 | 65 | 480 | 3 | 300 | 361 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE102236 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 65 | 480 | 3 | 300 | 361 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE102237 | C | CB | Square D | MHL36600 | 65 | 600 | 600 | 3 | 65 | 480 | 3 | 350 | 414 | 50400 | 1, 6, 7(f) | E40610 V12 S20
SE102237 |  | STR | Telemecanique | ATS48C48Y | 18 | 480 | 600 | 3 | 65 | 480 | 3 | 350 | 414 | 50400 | 1, 6, 7(f) | E40610 V12 S20
SE102237 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 65 | 480 | 3 | 350 | 414 | 50400 | 1, 6, 7(f) | E40610 V12 S20
SE102238 | C | CB | Square D | MHL36800 | 65 | 800 | 600 | 3 | 65 | 480 | 3 | 400 | 477 | 50400 | 1, 6, 7(r) | E40610 V12 S20
SE102238 |  | STR | Telemecanique | ATS48C59Y | 30 | 590 | 600 | 3 | 65 | 480 | 3 | 400 | 477 | 50400 | 1, 6, 7(r) | E40610 V12 S20
SE102238 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 65 | 480 | 3 | 400 | 477 | 50400 | 1, 6, 7(r) | E40610 V12 S20
SE102239 | C | CB | Square D | MHL36900 | 65 | 900 | 600 | 3 | 65 | 480 | 3 | 500 | 590 | 50400 | 1, 6, 7(q) | E40610 V12 S20
SE102239 |  | STR | Telemecanique | ATS48C66Y | 30 | 660 | 600 | 3 | 65 | 480 | 3 | 500 | 590 | 50400 | 1, 6, 7(q) | E40610 V12 S20
SE102239 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 65 | 480 | 3 | 500 | 590 | 50400 | 1, 6, 7(q) | E40610 V12 S20

## ATS48-NEMA-PwrPact
Issued: 2007-04-27
Last Revised: 2007-04-27
Contactor is to be used as a shorting contactor only and may be optionally provided
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Min Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE153771 | C | CB | Square D | HLL36020 | 125 | 20 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153771 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153771 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153772 | C | CB | Square D | HLL36030 | 125 | 30 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153772 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153772 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153773 | C | CB | Square D | HLL36030 | 125 | 30 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153773 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153773 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153774 | C | CB | Square D | HLL36045 | 125 | 45 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153774 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153774 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153775 | C | CB | Square D | HLL36045 | 125 | 45 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153775 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153775 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153776 | C | CB | Square D | HLL36060 | 125 | 60 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153776 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153776 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153777 | C | CB | Square D | HLL36050 | 125 | 50 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153777 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153777 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153778 | C | CB | Square D | HLL36025 | 100 | 25 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153778 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153778 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153779 | C | CB | Square D | HLL36110 | 125 | 110 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153779 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153779 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153780 | C | CB | Square D | HLL36080 | 125 | 80 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE153780 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE153780 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE153781 | C | CB | Square D | HLL36040 | 100 | 40 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153781 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153781 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153782 | C | CB | Square D | HLL36110 | 125 | 110 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153782 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153782 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153783 | C | CB | Square D | HLL36110 | 125 | 110 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153783 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153783 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153784 | C | CB | Square D | HLL36050 | 100 | 50 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153784 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153784 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153785 | C | CB | Square D | HLL36110 | 125 | 110 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE153785 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE153785 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE153786 | C | CB | Square D | HLL36110 | 125 | 110 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153786 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153786 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153787 | C | CB | Square D | HLL36060 | 100 | 60 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153787 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153787 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE153788 | C | CB | Square D | HLL36125 | 125 | 125 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE153788 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE153788 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE153789 | C | CB | Square D | HLL36110 | 125 | 110 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE153789 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE153789 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE153790 | C | CB | Square D | HLL36080 | 100 | 80 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE153790 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE153790 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE153791 | C | CB | Square D | JLL36175 | 125 | 175 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE153791 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE153791 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE153792 | C | CB | Square D | HLL36150 | 125 | 150 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE153792 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE153792 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE153793 | C | CB | Square D | HLL36110 | 100 | 110 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153793 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153793 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153794 | C | CB | Square D | JLL36200 | 125 | 200 | 600 | 3 | 65 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE153794 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 65 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE153794 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 65 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE153795 | C | CB | Square D | JLL36200 | 125 | 200 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE153795 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE153795 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE153796 | C | CB | Square D | HLL36110 | 100 | 110 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153796 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153796 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE153797 | C | CB | Square D | JLL36225 | 125 | 225 | 600 | 3 | 65 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE153797 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 65 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE153797 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 65 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE153798 | C | CB | Square D | HLL36110 | 100 | 110 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE153798 |  | STR | Telemecanique | ATS48D88Y | 5 | 88 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE153798 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE153799 | C | CB | Square D | HLL36125 | 100 | 125 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE153799 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE153799 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE153800 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE153800 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE153800 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE153801 | C | CB | Square D | JLL36225 | 100 | 225 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE153801 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE153801 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20

## ATS48-NEMA-Fuse
Issued: 2007-04-27
Last Revised: 2007-04-27
Contactor is to be used as a shorting contactor only and may be optionally provided
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Min Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE500318 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500318 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500318 |  | F | Any | Class J Fuse | 200 | 20 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500318 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500318 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500319 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500319 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500319 |  | F | Any | Class J Fuse | 200 | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500319 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500319 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500320 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500320 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500320 |  | F | Any | Class J Fuse | 200 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500320 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500320 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500321 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500321 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500321 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500321 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500321 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500322 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500322 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500322 |  | F | Any | Class J Fuse | 200 | 40 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500322 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500322 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500323 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500323 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500323 |  | F | Any | Class J Fuse | 200 | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500323 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500323 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500324 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500324 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500324 |  | F | Any | Class J Fuse | 200 | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500324 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500324 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500325 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500325 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500325 |  | F | Any | Class J Fuse | 200 | 25 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500325 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500325 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500326 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500326 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500326 |  | F | Any | Class J Fuse | 200 | 80 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500326 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500326 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500327 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500327 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500327 |  | F | Any | Class J Fuse | 200 | 70 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500327 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500327 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500328 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500328 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500328 |  | F | Any | Class J Fuse | 200 | 35 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500328 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500328 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500329 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500329 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500329 |  | F | Any | Class J Fuse | 200 | 30 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500329 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500329 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500330 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500330 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500330 |  | F | Any | Class J Fuse | 200 | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500330 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500330 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500331 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500331 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500331 |  | F | Any | Class J Fuse | 200 | 90 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500331 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500331 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500332 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500332 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500332 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500332 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500332 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500333 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500333 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500333 |  | F | Any | Class J Fuse | 200 | 40 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500333 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500333 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500334 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500334 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500334 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500334 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500334 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500335 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500335 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500335 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500335 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500335 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500336 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500336 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500336 |  | F | Any | Class J Fuse | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500336 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500336 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500337 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500337 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500337 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500337 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500337 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500338 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500338 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500338 |  | F | Any | Class J Fuse | 200 | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500338 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500338 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500339 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500339 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500339 |  | F | Any | Class J Fuse | 200 | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500339 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500339 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500340 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500340 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500340 |  | F | Any | Class J Fuse | 200 | 70 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500340 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500340 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500341 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500341 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500341 |  | F | Any | Class J Fuse | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500341 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500341 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500342 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500342 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500342 |  | F | Any | Class J Fuse | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500342 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500342 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500343 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500343 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500343 |  | F | Any | Class J Fuse | 200 | 175 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500343 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500343 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500344 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500344 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500344 |  | F | Any | Class J Fuse | 200 | 90 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500344 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500344 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500345 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500345 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500345 |  | F | Any | Class J Fuse | 200 | 70 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500345 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500345 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500346 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500346 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500346 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500346 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500346 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500347 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500347 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500347 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500347 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500347 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500348 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500348 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500348 |  | F | Any | Class J Fuse | 200 | 110 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500348 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500348 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500349 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500349 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500349 |  | F | Any | Class J Fuse | 200 | 90 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500349 |  | STR | Telemecanique | ATS48D62Y | 10 | 62 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500349 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500350 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500350 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500350 |  | F | Any | Class J Fuse | 200 | 300 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500350 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500350 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500351 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500351 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500351 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500351 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500351 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500352 | A | DS | Square D | KHL36000M | 35 | 250 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500352 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500352 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500352 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500352 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500353 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500353 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500353 |  | F | Any | Class J Fuse | 200 | 110 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500353 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500353 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500354 | A | DS | Square D | LHL36000M | 65 | 400 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 28800 | 1, 6, 7(p) | E40610 V12 S20
SE500354 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 28800 | 1, 6, 7(p) | E40610 V12 S20
SE500354 |  | F | Any | Class J Fuse | 200 | 350 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 28800 | 1, 6, 7(p) | E40610 V12 S20
SE500354 |  | STR | Telemecanique | ATS48C25Y | 18 | 250 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 28800 | 1, 6, 7(p) | E40610 V12 S20
SE500354 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 28800 | 1, 6, 7(p) | E40610 V12 S20
SE500355 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500355 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500355 |  | F | Any | Class J Fuse | 200 | 350 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500355 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500355 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500356 | A | DS | Square D | KHL36000M | 35 | 250 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500356 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500356 |  | F | Any | Class J Fuse | 200 | 175 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500356 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500356 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500357 | A | DS | Square D | KHL36000M | 25 | 250 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500357 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500357 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500357 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500357 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500358 | A | DS | Square D | LHL36000M | 65 | 400 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500358 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500358 |  | F | Any | Class J Fuse | 200 | 450 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500358 |  | STR | Telemecanique | ATS48C32Y | 18 | 320 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500358 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500359 | A | DS | Square D | LHL36000M | 65 | 400 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500359 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500359 |  | F | Any | Class J Fuse | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500359 |  | STR | Telemecanique | ATS48C25Y | 18 | 250 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500359 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500360 | A | DS | Square D | KHL36000M | 35 | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500360 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500360 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500360 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500360 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500361 | A | DS | Square D | KHL36000M | 25 | 250 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500361 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500361 |  | F | Any | Class J Fuse | 200 | 175 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500361 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500361 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500362 | A | DS | Square D | MHL360006M | 65 | 600 | 600 | 3 | 100 | 208 | 3 | 125 | 343 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE500362 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 208 | 3 | 125 | 343 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE500362 |  | F | Any | Class J Fuse | 200 | 600 | 600 | 3 | 100 | 208 | 3 | 125 | 343 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE500362 |  | STR | Telemecanique | ATS48C41Y | 18 | 410 | 600 | 3 | 100 | 208 | 3 | 125 | 343 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE500362 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 100 | 208 | 3 | 125 | 343 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE500363 | A | DS | Square D | LHL36000M | 65 | 400 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 28800 | 1, 6, 7(i) | E40610 V12 S20
SE500363 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 28800 | 1, 6, 7(i) | E40610 V12 S20
SE500363 |  | F | Any | Class J Fuse | 200 | 500 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 28800 | 1, 6, 7(i) | E40610 V12 S20
SE500363 |  | STR | Telemecanique | ATS48C32Y | 18 | 320 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 28800 | 1, 6, 7(i) | E40610 V12 S20
SE500363 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 28800 | 1, 6, 7(i) | E40610 V12 S20
SE500364 | A | DS | Square D | KHL36000M | 35 | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500364 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500364 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500364 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500364 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500365 | A | DS | Square D | KHL36000M | 25 | 250 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500365 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500365 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500365 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500365 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500366 | A | DS | Square D | MHL360006M | 65 | 600 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500366 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500366 |  | F | Any | Class J Fuse | 200 | 600 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500366 |  | STR | Telemecanique | ATS48C41Y | 18 | 410 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500366 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500367 | A | DS | Square D | KHL36000M | 35 | 250 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500367 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500367 |  | F | Any | Class J Fuse | 200 | 300 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500367 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500367 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500368 | A | DS | Square D | KHL36000M | 25 | 250 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500368 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500368 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500368 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500368 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE500369 | A | DS | Square D | LHL36000M | 35 | 400 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500369 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500369 |  | F | Any | Class J Fuse | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500369 |  | STR | Telemecanique | ATS48C25Y | 18 | 250 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500369 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500370 | A | DS | Square D | LHL36000M | 25 | 400 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500370 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500370 |  | F | Any | Class J Fuse | 200 | 350 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500370 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500370 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE500371 | A | DS | Square D | LHL36000M | 35 | 400 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500371 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500371 |  | F | Any | Class J Fuse | 200 | 500 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500371 |  | STR | Telemecanique | ATS48C32Y | 18 | 320 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500371 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500372 | A | DS | Square D | LHL36000M | 25 | 400 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500372 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500372 |  | F | Any | Class J Fuse | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500372 |  | STR | Telemecanique | ATS48C25Y | 18 | 250 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500372 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 28800 | 1, 6, 7(h) | E40610 V12 S20
SE500373 | A | DS | Square D | MHL360006M | 65 | 600 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500373 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500373 |  | F | Any | Class J Fuse | 200 | 600 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500373 |  | STR | Telemecanique | ATS48C41Y | 18 | 410 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500373 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 50400 | 1, 6, 7(e) | E40610 V12 S20
SE500374 | A | DS | Square D | LHL36000M | 25 | 400 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500374 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500374 |  | F | Any | Class J Fuse | 200 | 500 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500374 |  | STR | Telemecanique | ATS48C32Y | 18 | 320 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500374 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 28800 | 1, 6, 7(s) | E40610 V12 S20
SE500375 | A | DS | Square D | MHL360006M | 25 | 600 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE500375 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE500375 |  | F | Any | Class J Fuse | 200 | 600 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE500375 |  | STR | Telemecanique | ATS48C41Y | 18 | 410 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE500375 |  | MC | Square D | 8502SH02 | 10 | 540 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 50400 | 1, 6, 7(i) | E40610 V12 S20
SE550045 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550045 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550045 |  | F | Any | Class J Fuse | 200 | 20 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550045 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550045 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550046 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550046 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550046 |  | F | Any | Class J Fuse | 200 | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550046 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550046 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550047 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550047 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550047 |  | F | Any | Class J Fuse | 200 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550047 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550047 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550048 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550048 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550048 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550048 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550048 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550049 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550049 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550049 |  | F | Any | Class J Fuse | 200 | 40 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550049 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550049 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550050 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550050 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550050 |  | F | Any | Class J Fuse | 200 | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550050 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550050 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550051 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550051 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550051 |  | F | Any | Class J Fuse | 200 | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550051 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550051 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550052 | A | DS | Square D | HGL36000S15 | 35 | 150 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550052 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550052 |  | F | Any | Class J Fuse | 200 | 25 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550052 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550052 |  | MC | Square D | 8502SC02 | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550053 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550053 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550053 |  | F | Any | Class J Fuse | 200 | 80 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550053 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550053 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550054 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550054 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550054 |  | F | Any | Class J Fuse | 200 | 70 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550054 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550054 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550055 | A | DS | Square D | HGL36000S15 | 35 | 150 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550055 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550055 |  | F | Any | Class J Fuse | 200 | 35 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550055 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550055 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550056 | A | DS | Square D | HGL36000S15 | 18 | 150 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550056 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550056 |  | F | Any | Class J Fuse | 200 | 30 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550056 |  | STR | Telemecanique | ATS48D17Y | 5 | 17 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550056 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550057 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550057 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550057 |  | F | Any | Class J Fuse | 200 | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550057 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550057 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550058 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550058 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550058 |  | F | Any | Class J Fuse | 200 | 90 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550058 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550058 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550059 | A | DS | Square D | HGL36000S15 | 35 | 150 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550059 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550059 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550059 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550059 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550060 | A | DS | Square D | HGL36000S15 | 18 | 150 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550060 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550060 |  | F | Any | Class J Fuse | 200 | 40 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550060 |  | STR | Telemecanique | ATS48D22Y | 5 | 22 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550060 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550061 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550061 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550061 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550061 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550061 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550062 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550062 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550062 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550062 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550062 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550063 | A | DS | Square D | HGL36000S15 | 35 | 150 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550063 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550063 |  | F | Any | Class J Fuse | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550063 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550063 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550064 | A | DS | Square D | HGL36000S15 | 18 | 150 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550064 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550064 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550064 |  | STR | Telemecanique | ATS48D32Y | 5 | 32 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550064 |  | MC | Square D | 8502SD02 | 5 | 45 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550065 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550065 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550065 |  | F | Any | Class J Fuse | 200 | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550065 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550065 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550066 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550066 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550066 |  | F | Any | Class J Fuse | 200 | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550066 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550066 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550067 | A | DS | Square D | HGL36000S15 | 35 | 150 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550067 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550067 |  | F | Any | Class J Fuse | 200 | 70 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550067 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550067 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550068 | A | DS | Square D | HGL36000S15 | 18 | 150 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550068 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550068 |  | F | Any | Class J Fuse | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550068 |  | STR | Telemecanique | ATS48D38Y | 5 | 38 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550068 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE550069 | A | DS | Square D | JLL36000S17 | 65 | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550069 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550069 |  | F | Any | Class J Fuse | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550069 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550069 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550070 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550070 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550070 |  | F | Any | Class J Fuse | 200 | 175 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550070 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550070 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550071 | A | DS | Square D | HGL36000S15 | 35 | 150 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550071 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550071 |  | F | Any | Class J Fuse | 200 | 90 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550071 |  | STR | Telemecanique | ATS48D62Y | 5 | 62 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550071 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550072 | A | DS | Square D | HGL36000S15 | 18 | 150 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550072 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550072 |  | F | Any | Class J Fuse | 200 | 70 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550072 |  | STR | Telemecanique | ATS48D47Y | 5 | 47 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550072 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE550073 | A | DS | Square D | JGL36000S25 | 65 | 250 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550073 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550073 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550073 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550073 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550074 | A | DS | Square D | JLL36000S17 | 65 | 175 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550074 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550074 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550074 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550074 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550075 | A | DS | Square D | HGL36000S15 | 35 | 150 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550075 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550075 |  | F | Any | Class J Fuse | 200 | 110 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550075 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550075 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550076 | A | DS | Square D | HGL36000S15 | 18 | 150 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550076 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550076 |  | F | Any | Class J Fuse | 200 | 90 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550076 |  | STR | Telemecanique | ATS48D62Y | 10 | 62 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550076 |  | MC | Square D | 8502SE02 | 5 | 90 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550077 | A | DS | Square D | JGL36000S25 | 65 | 250 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550077 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550077 |  | F | Any | Class J Fuse | 200 | 300 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550077 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550077 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550078 | A | DS | Square D | JGL36000S25 | 65 | 250 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550078 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550078 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550078 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550078 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550079 | A | DS | Square D | HGL36000S15 | 35 | 150 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550079 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550079 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550079 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550079 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550080 | A | DS | Square D | HGL36000S15 | 18 | 150 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550080 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550080 |  | F | Any | Class J Fuse | 200 | 110 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550080 |  | STR | Telemecanique | ATS48D75Y | 10 | 75 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550080 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE550081 | A | DS | Square D | JGL36000S25 | 65 | 250 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550081 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550081 |  | F | Any | Class J Fuse | 200 | 350 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550081 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550081 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550082 | A | DS | Square D | HGL36000S15 | 35 | 150 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550082 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550082 |  | F | Any | Class J Fuse | 200 | 175 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550082 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550082 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550083 | A | DS | Square D | HGL36000S15 | 18 | 150 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550083 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550083 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550083 |  | STR | Telemecanique | ATS48D88Y | 10 | 88 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550083 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE550084 | A | DS | Square D | JGL36000S17 | 35 | 175 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550084 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550084 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550084 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550084 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550085 | A | DS | Square D | HGL36000S15 | 18 | 150 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550085 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550085 |  | F | Any | Class J Fuse | 200 | 175 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550085 |  | STR | Telemecanique | ATS48C11Y | 10 | 110 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550085 |  | MC | Square D | 8502SF02 | 10 | 135 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE550086 | A | DS | Square D | JGL36000S25 | 35 | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550086 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550086 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550086 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550086 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550087 | A | DS | Square D | HLL36000S15 | 18 | 175 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550087 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550087 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550087 |  | STR | Telemecanique | ATS48C14Y | 10 | 140 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550087 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550088 | A | DS | Square D | JGL36000S25 | 35 | 250 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550088 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550088 |  | F | Any | Class J Fuse | 200 | 300 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550088 |  | STR | Telemecanique | ATS48C21Y | 10 | 210 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550088 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 28800 | 1, 6, 7(d) | E40610 V12 S20
SE550089 | A | DS | Square D | JLL36000S17 | 18 | 250 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550089 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550089 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550089 |  | STR | Telemecanique | ATS48C17Y | 10 | 170 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20
SE550089 |  | MC | Square D | 8502SG02 | 10 | 270 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 6409 | 1, 6, 7(c) | E40610 V12 S20

## ATS48-GSx
Issued: 2008-08-15
Last Revised: 2008-08-18
| Listed Combination Motor Controller Information |  |  | Component Description | [6 empty] | Combination Motor Controller Ratings
Database Identification Number | UL File Number | Volume / Section (Vol#).(Sec#) | Construction Type | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, ph | SCCR, kA | Full Load Current, A | Hp | Short Circuit Current Rating, kA | Horsepower Rating | Current Rating, FLA or FLA/LRA | Voltage and Number of Phases | Enclosure Volume, cubic inches | Conditions of Use | Schematic
SE502350 | E40610 | 12.20 | A | FDS | Telemecanique | GS1EU3 | 600, 3 | 200 | 30 | - | 100 | 3 | 10.6 | 208, 3 | 4620 | 1, 6, 7a, 9 | NA
|  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 20 | - | 100 | 3 | 10.6 | 208, 3 | 4620 |  | NA
|  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D17Y | 600, 3 | 5 | 10.6 | 3 | 100 | 3 | 10.6 | 208, 3 | 4620 |  | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 24.2 | 7.5 | 100 | 3 | 10.6 | 208, 3 | 4620 |  | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 24.2 | 7.5 | 100 | 3 | 10.6 | 208, 3 | 4620 |  | NA
SE502351 | E40610 | 12.20 | A | FDS | Telemecanique | GS1EU3 | 600, 3 | 200 | 30 | - | 100 | 5 | 16.7 | 208, 3 | 4620 | 1, 6, 7a, 9 | NA
|  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 30 | - | 100 | 5 | 16.7 | 208, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D22Y | 600, 3 | 5 | 16.7 | 5 | 100 | 5 | 16.7 | 208, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 24.2 | 7.5 | 100 | 5 | 16.7 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 24.2 | 7.5 | 100 | 5 | 16.7 | 208, 3 | 4620 | 1, 6, 7a | NA
SE502352 | E40610 | 12.20 | A | FDS | Telemecanique | GS1EU3 | 600, 3 | 200 | 30 | - | 100 | 5 | 15.2 | 240, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502352 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 25 | - | 100 | 5 | 15.2 | 240, 3 | 4620 | 1, 6, 7a | NA
SE502352 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D17Y | 600, 3 | 5 | 15.2 | 5 | 100 | 5 | 15.2 | 240, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 22 | 7.5 | 100 | 5 | 15.2 | 240, 3 | 0 | 1, 6, 7a | NA
SE502352 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 22 | 7.5 | 100 | 5 | 15.2 | 240, 3 | 4620 | 1, 6, 7a | NA
SE502353 | E40610 | 12.20 | A | FDS | Telemecanique | GS1GU3 | 600, 3 | 200 | 60 | - | 100 | 7.5 | 24.2 | 208, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502353 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 45 | - | 100 | 7.5 | 24.2 | 208, 3 | 4620 | 1, 6, 7a | NA
SE502353 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D32Y | 600, 3 | 5 | 24.2 | 7.5 | 100 | 7.5 | 24.2 | 208, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 30.8 | 10 | 100 | 7.5 | 24.2 | 208, 3 | 0 | 1, 6, 7a | NA
SE502353 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 24.2 | 7.5 | 100 | 7.5 | 24.2 | 208, 3 | 4620 | 1, 6, 7a | NA
SE502354 | E40610 | 12.20 | A | FDS | Telemecanique | GS1GU3 | 600, 3 | 200 | 60 | - | 100 | 7.5 | 22 | 240, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502354 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 40 | - | 100 | 7.5 | 22 | 240, 3 | 4620 | 1, 6, 7a | NA
SE502354 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D22Y | 600, 3 | 5 | 22 | 7.5 | 100 | 7.5 | 22 | 240, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 28 | 10 | 100 | 7.5 | 22 | 240, 3 | 0 | 1, 6, 7a | NA
SE502354 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 22 | 7.5 | 100 | 7.5 | 22 | 240, 3 | 4620 | 1, 6, 7a | NA
SE502355 | E40610 | 12.20 | A | FDS | Telemecanique | GS1GU3 | 600, 3 | 200 | 60 | - | 100 | 10 | 30.8 | 208, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502355 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 50 | - | 100 | 10 | 30.8 | 208, 3 | 4620 | 1, 6, 7a | NA
SE502355 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D38Y | 600, 3 | 5 | 30.8 | 10 | 100 | 10 | 30.8 | 208, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D40 (Optional) | 600, 3 | 5 | 30.8 | 10 | 100 | 10 | 30.8 | 208, 3 | 0 | 1, 6, 7a | NA
SE502355 |  |  |  | (SHORT) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 30.8 | 10 | 100 | 10 | 30.8 | 208, 3 | 4620 | 1, 6, 7a | NA
SE502356 | E40610 | 12.20 | A | FDS | Telemecanique | GS1GU3 | 600, 3 | 200 | 60 | - | 100 | 10 | 28 | 240, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502356 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 50 | - | 100 | 10 | 28 | 240, 3 | 4620 | 1, 6, 7a | NA
SE502356 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D32Y | 600, 3 | 5 | 28 | 10 | 100 | 10 | 28 | 240, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 28 | 10 | 100 | 10 | 28 | 240, 3 | 0 | 1, 6, 7a | NA
SE502356 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 22 | 7.5 | 100 | 10 | 28 | 240, 3 | 4620 | 1, 6, 7a | NA
SE502357 | E40610 | 12.20 | A | FDS | Telemecanique | GS1EU3 | 600, 3 | 200 | 30 | - | 100 | 10 | 14 | 480, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502357 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 25 | - | 100 | 10 | 14 | 480, 3 | 4620 | 1, 6, 7a | NA
SE502357 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D17Y | 600, 3 | 5 | 14 | 10 | 100 | 10 | 14 | 480, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 21 | 15 | 100 | 10 | 14 | 480, 3 | 0 | 1, 6, 7a | NA
SE502357 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 21 | 15 | 100 | 10 | 14 | 480, 3 | 4620 | 1, 6, 7a | NA
SE502358 | E40610 | 12.20 | A | FDS | Telemecanique | GS1JU3 | 600, 3 | 200 | 100 | - | 100 | 15 | 46.2 | 208, 3 | 4620 | 1, 6, 7b, 9 | NA
SE502358 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 80 | - | 100 | 15 | 46.2 | 208, 3 | 4620 | 1, 6, 7b | NA
SE502358 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D62Y | 600, 3 | 5 | 46.2 | 15 | 100 | 15 | 46.2 | 208, 3 | 4620 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D50 (Optional) | 600, 3 | 5 | 46.2 | 15 | 100 | 15 | 46.2 | 208, 3 | 0 | 1, 6, 7b | NA
SE502358 |  |  |  | (SHORT) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 30.8 | 10 | 100 | 15 | 46.2 | 208, 3 | 4620 | 1, 6, 7b | NA
SE502359 | E40610 | 12.20 | A | FDS | Telemecanique | GS1JU3 | 600, 3 | 200 | 100 | - | 100 | 15 | 42 | 240, 3 | 4620 | 1, 6, 7k, 9 | NA
SE502359 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 70 | - | 100 | 15 | 42 | 240, 3 | 4620 | 1, 6, 7k | NA
SE502359 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D47Y | 600, 3 | 5 | 42 | 15 | 100 | 15 | 42 | 240, 3 | 4620 | 1, 6, 7k | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D50 (Optional) | 600, 3 | 5 | 42 | 15 | 100 | 15 | 42 | 240, 3 | 0 | 1, 6, 7k | NA
SE502359 |  |  |  | (SHORT) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 28 | 10 | 100 | 15 | 42 | 240, 3 | 4620 | 1, 6, 7k | NA
SE502360 | E40610 | 12.20 | A | FDS | Telemecanique | GS1GU3 | 600, 3 | 200 | 60 | - | 100 | 15 | 21 | 480, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502360 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 35 | - | 100 | 15 | 21 | 480, 3 | 4620 | 1, 6, 7a | NA
SE502360 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D22Y | 600, 3 | 5 | 21 | 15 | 100 | 15 | 21 | 480, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 21 | 15 | 100 | 15 | 21 | 480, 3 | 0 | 1, 6, 7a | NA
SE502360 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 21 | 15 | 100 | 15 | 21 | 480, 3 | 4620 | 1, 6, 7a | NA
SE502361 | E40610 | 12.20 | A | FDS | Telemecanique | GS1EU3 | 600, 3 | 200 | 30 | - | 100 | 15 | 17 | 600, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502361 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 30 | - | 100 | 15 | 17 | 600, 3 | 4620 | 1, 6, 7a | NA
SE502361 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D17Y | 600, 3 | 5 | 17 | 15 | 100 | 15 | 17 | 600, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 22 | 20 | 100 | 15 | 17 | 600, 3 | 0 | 1, 6, 7a | NA
SE502361 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 22 | 20 | 100 | 15 | 17 | 600, 3 | 4620 | 1, 6, 7a | NA
SE502362 | E40610 | 12.20 | A | FDS | Telemecanique | GS1JU3 | 600, 3 | 200 | 100 | - | 100 | 20 | 59.4 | 208, 3 | 4620 | 1, 6, 7b, 9 | NA
SE502362 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 100 | - | 100 | 20 | 59.4 | 208, 3 | 4620 | 1, 6, 7b | NA
SE502362 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D75Y | 600, 3 | 10 | 59.4 | 20 | 100 | 20 | 59.4 | 208, 3 | 4620 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D65 (Optional) | 600, 3 | 5 | 59.4 | 20 | 100 | 20 | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
SE502362 |  |  |  | (SHORT) MC | Telemecanique | LC1D50 (Optional) | 600, 3 | 5 | 46.2 | 15 | 100 | 20 | 59.4 | 208, 3 | 4620 | 1, 6, 7b | NA
SE502363 | E40610 | 12.20 | A | FDS | Telemecanique | GS1JU3 | 600, 3 | 200 | 100 | - | 100 | 20 | 54 | 240, 3 | 4620 | 1, 6, 7b, 9 | NA
SE502363 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 90 | - | 100 | 20 | 54 | 240, 3 | 4620 | 1, 6, 7b | NA
SE502363 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D62Y | 600, 3 | 5 | 54 | 20 | 100 | 20 | 54 | 240, 3 | 4620 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D65 (Optional) | 600, 3 | 5 | 54 | 20 | 100 | 20 | 54 | 240, 3 | 0 | 1, 6, 7b | NA
SE502363 |  |  |  | (SHORT) MC | Telemecanique | LC1D40 (Optional) | 600, 3 | 5 | 28 | 10 | 100 | 20 | 54 | 240, 3 | 4620 | 1, 6, 7b | NA
SE502364 | E40610 | 12.20 | A | FDS | Telemecanique | GS1GU3 | 600, 3 | 200 | 60 | - | 100 | 20 | 27 | 480, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502364 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 45 | - | 100 | 20 | 27 | 480, 3 | 4620 | 1, 6, 7a | NA
SE502364 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D32Y | 600, 3 | 5 | 27 | 20 | 100 | 20 | 27 | 480, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 27 | 20 | 100 | 20 | 27 | 480, 3 | 0 | 1, 6, 7a | NA
SE502364 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 21 | 15 | 100 | 20 | 27 | 480, 3 | 4620 | 1, 6, 7a | NA
SE502365 | E40610 | 12.20 | A | FDS | Telemecanique | GS1GU3 | 600, 3 | 200 | 60 | - | 100 | 20 | 22 | 600, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502365 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 40 | - | 100 | 20 | 22 | 600, 3 | 4620 | 1, 6, 7a | NA
SE502365 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D22Y | 600, 3 | 5 | 22 | 20 | 100 | 20 | 22 | 600, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 22 | 20 | 100 | 20 | 22 | 600, 3 | 0 | 1, 6, 7a | NA
SE502365 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 22 | 20 | 100 | 20 | 22 | 600, 3 | 4620 | 1, 6, 7a | NA
SE502366 | E40610 | 12.20 | A | FDS | Telemecanique | GS1MU3 | 600, 3 | 200 | 200 | - | 100 | 25 | 74.8 | 208, 3 | 4620 | 1, 6, 7L, 9 | NA
SE502366 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 125 | - | 100 | 25 | 74.8 | 208, 3 | 4620 | 1, 6, 7L | NA
SE502366 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D88Y | 600, 3 | 10 | 74.8 | 25 | 100 | 25 | 74.8 | 208, 3 | 4620 | 1, 6, 7L | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 88 | 30 | 100 | 25 | 74.8 | 208, 3 | 0 | 1, 6, 7L | NA
SE502366 |  |  |  | (SHORT) MC | Telemecanique | LC1D50 (Optional) | 600, 3 | 5 | 46.2 | 15 | 100 | 25 | 74.8 | 208, 3 | 4620 | 1, 6, 7L | NA
SE502367 | E40610 | 12.20 | A | FDS | Telemecanique | GS1MU3 | 600, 3 | 200 | 200 | - | 100 | 25 | 68 | 240, 3 | 4620 | 1, 6, 7b, 9 | NA
SE502367 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 125 | - | 100 | 25 | 68 | 240, 3 | 4620 | 1, 6, 7b | NA
SE502367 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D75Y | 600, 3 | 10 | 68 | 25 | 100 | 25 | 68 | 240, 3 | 4620 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 80 | 30 | 100 | 25 | 68 | 240, 3 | 0 | 1, 6, 7b | NA
SE502367 |  |  |  | (SHORT) MC | Telemecanique | LC1D50 (Optional) | 600, 3 | 5 | 42 | 15 | 100 | 25 | 68 | 240, 3 | 4620 | 1, 6, 7b | NA
SE502368 | E40610 | 12.20 | A | FDS | Telemecanique | GS1GU3 | 600, 3 | 200 | 60 | - | 100 | 25 | 34 | 480, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502368 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 60 | - | 100 | 25 | 34 | 480, 3 | 4620 | 1, 6, 7a | NA
SE502368 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D38Y | 600, 3 | 5 | 34 | 25 | 100 | 25 | 34 | 480, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D40 (Optional) | 600, 3 | 5 | 40 | 30 | 100 | 25 | 34 | 480, 3 | 0 | 1, 6, 7a | NA
SE502368 |  |  |  | (SHORT) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 27 | 20 | 100 | 25 | 34 | 480, 3 | 4620 | 1, 6, 7a | NA
SE502369 | E40610 | 12.20 | A | FDS | Telemecanique | GS1GU3 | 600, 3 | 200 | 60 | - | 100 | 25 | 27 | 600, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502369 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 45 | - | 100 | 25 | 27 | 600, 3 | 4620 | 1, 6, 7a | NA
SE502369 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D32Y | 600, 3 | 5 | 27 | 25 | 100 | 25 | 27 | 600, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 32 | 30 | 100 | 25 | 27 | 600, 3 | 0 | 1, 6, 7a | NA
SE502369 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 22 | 20 | 100 | 25 | 27 | 600, 3 | 4620 | 1, 6, 7a | NA
SE502370 | E40610 | 12.20 | A | FDS | Telemecanique | GS1MU3 | 600, 3 | 200 | 200 | - | 100 | 30 | 88 | 208, 3 | 4620 | 1, 6, 7m, 9 | NA
SE502370 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 150 | - | 100 | 30 | 88 | 208, 3 | 4620 | 1, 6, 7m | NA
SE502370 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C11Y | 600, 3 | 10 | 88 | 30 | 100 | 30 | 88 | 208, 3 | 4620 | 1, 6, 7m | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 88 | 30 | 100 | 30 | 88 | 208, 3 | 0 | 1, 6, 7m | NA
SE502370 |  |  |  | (SHORT) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 74.8 | 25 | 100 | 30 | 88 | 208, 3 | 4620 | 1, 6, 7m | NA
SE502371 | E40610 | 12.20 | A | FDS | Telemecanique | GS1MU3 | 600, 3 | 200 | 200 | - | 100 | 30 | 80 | 240, 3 | 4620 | 1, 6, 7L, 9 | NA
SE502371 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 150 | - | 100 | 30 | 80 | 240, 3 | 4620 | 1, 6, 7L | NA
SE502371 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D88Y | 600, 3 | 10 | 80 | 30 | 100 | 30 | 80 | 240, 3 | 4620 | 1, 6, 7L | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 104 | 40 | 100 | 30 | 80 | 240, 3 | 0 | 1, 6, 7L | NA
SE502371 |  |  |  | (SHORT) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 80 | 30 | 100 | 30 | 80 | 240, 3 | 4620 | 1, 6, 7L | NA
SE502372 | E40610 | 12.20 | A | FDS | Telemecanique | GS1JU3 | 600, 3 | 200 | 100 | - | 100 | 30 | 40 | 480, 3 | 4620 | 1, 6, 7k, 9 | NA
SE502372 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 70 | - | 100 | 30 | 40 | 480, 3 | 4620 | 1, 6, 7k | NA
SE502372 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D47Y | 600, 3 | 5 | 40 | 30 | 100 | 30 | 40 | 480, 3 | 4620 | 1, 6, 7k | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D50 (Optional) | 600, 3 | 5 | 52 | 40 | 100 | 30 | 40 | 480, 3 | 0 | 1, 6, 7k | NA
SE502372 |  |  |  | (SHORT) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 27 | 20 | 100 | 30 | 40 | 480, 3 | 4620 | 1, 6, 7k | NA
SE502373 | E40610 | 12.20 | A | FDS | Telemecanique | GS1GU3 | 600, 3 | 200 | 60 | - | 100 | 30 | 32 | 600, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502373 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 60 | - | 100 | 30 | 32 | 600, 3 | 4620 | 1, 6, 7a | NA
SE502373 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D38Y | 600, 3 | 5 | 32 | 30 | 100 | 30 | 32 | 600, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D40 (Optional) | 600, 3 | 5 | 32 | 30 | 100 | 30 | 32 | 600, 3 | 0 | 1, 6, 7a | NA
SE502373 |  |  |  | (SHORT) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 32 | 30 | 100 | 30 | 32 | 600, 3 | 4620 | 1, 6, 7a | NA
SE502374 | E40610 | 12.20 | A | FDS | Telemecanique | GS1MU3 | 600, 3 | 200 | 200 | - | 100 | 40 | 114 | 208, 3 | 6468 | 1, 6, 7n, 9 | NA
SE502374 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 200 | - | 100 | 40 | 114 | 208, 3 | 6468 | 1, 6, 7n | NA
SE502374 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C14Y | 600, 3 | 10 | 114 | 40 | 100 | 40 | 114 | 208, 3 | 6468 | 1, 6, 7n | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 114 | 40 | 100 | 40 | 114 | 208, 3 | 0 | 1, 6, 7n | NA
SE502374 |  |  |  | (SHORT) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 74.8 | 25 | 100 | 40 | 114 | 208, 3 | 6468 | 1, 6, 7n | NA
SE502375 | E40610 | 12.20 | A | FDS | Telemecanique | GS1MU3 | 600, 3 | 200 | 200 | - | 100 | 40 | 104 | 240, 3 | 4620 | 1, 6, 7m, 9 | NA
SE502375 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 175 | - | 100 | 40 | 104 | 240, 3 | 4620 | 1, 6, 7m | NA
SE502375 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C11Y | 600, 3 | 10 | 104 | 40 | 100 | 40 | 104 | 240, 3 | 4620 | 1, 6, 7m | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 104 | 40 | 100 | 40 | 104 | 240, 3 | 0 | 1, 6, 7m | NA
SE502375 |  |  |  | (SHORT) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 80 | 30 | 100 | 40 | 104 | 240, 3 | 4620 | 1, 6, 7m | NA
SE502376 | E40610 | 12.20 | A | FDS | Telemecanique | GS1JU3 | 600, 3 | 200 | 100 | - | 100 | 40 | 52 | 480, 3 | 4620 | 1, 6, 7b, 9 | NA
SE502376 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 90 | - | 100 | 40 | 52 | 480, 3 | 4620 | 1, 6, 7b | NA
SE502376 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D62Y | 600, 3 | 5 | 52 | 40 | 100 | 40 | 52 | 480, 3 | 4620 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D65 (Optional) | 600, 3 | 5 | 65 | 50 | 100 | 40 | 52 | 480, 3 | 0 | 1, 6, 7b | NA
SE502376 |  |  |  | (SHORT) MC | Telemecanique | LC1D40 (Optional) | 600, 3 | 5 | 40 | 30 | 100 | 40 | 52 | 480, 3 | 4620 | 1, 6, 7b | NA
SE502377 | E40610 | 12.20 | A | FDS | Telemecanique | GS1JU3 | 600, 3 | 200 | 100 | - | 100 | 40 | 41 | 600, 3 | 4620 | 1, 6, 7k, 9 | NA
SE502377 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 70 | - | 100 | 40 | 41 | 600, 3 | 4620 | 1, 6, 7k | NA
SE502377 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D47Y | 600, 3 | 5 | 41 | 40 | 100 | 40 | 41 | 600, 3 | 4620 | 1, 6, 7k | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D50 (Optional) | 600, 3 | 5 | 41 | 40 | 100 | 40 | 41 | 600, 3 | 0 | 1, 6, 7k | NA
SE502377 |  |  |  | (SHORT) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 32 | 30 | 100 | 40 | 41 | 600, 3 | 4620 | 1, 6, 7k | NA
SE502378 | E40610 | 12.20 | A | FDS | Telemecanique | GS1QU3 | 600, 3 | 200 | 400 | - | 100 | 50 | 143 | 208, 3 | 8778 | 1, 6, 7c, 9 | NA
SE502378 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 250 | - | 100 | 50 | 143 | 208, 3 | 6468 | 1, 6, 7c | NA
SE502378 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C17Y | 600, 3 | 10 | 143 | 50 | 100 | 50 | 143 | 208, 3 | 6468 | 1, 6, 7c | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 143 | 50 | 100 | 50 | 143 | 208, 3 | 0 | 1, 6, 7c | NA
SE502378 |  |  |  | (SHORT) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 88 | 30 | 100 | 50 | 143 | 208, 3 | 6468 | 1, 6, 7c | NA
SE502379 | E40610 | 12.20 | A | FDS | Telemecanique | GS1QU3 | 600, 3 | 200 | 400 | - | 100 | 50 | 130 | 240, 3 | 8778 | 1, 6, 7n, 9 | NA
SE502379 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 225 | - | 100 | 50 | 130 | 240, 3 | 6468 | 1, 6, 7n | NA
SE502379 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C14Y | 600, 3 | 10 | 130 | 50 | 100 | 50 | 130 | 240, 3 | 6468 | 1, 6, 7n | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 130 | 50 | 100 | 50 | 130 | 240, 3 | 0 | 1, 6, 7n | NA
SE502379 |  |  |  | (SHORT) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 104 | 40 | 100 | 50 | 130 | 240, 3 | 6468 | 1, 6, 7n | NA
SE502380 | E40610 | 12.20 | A | FDS | Telemecanique | GS1MU3 | 600, 3 | 200 | 200 | - | 100 | 50 | 65 | 480, 3 | 4620 | 1, 6, 7b, 9 | NA
SE502380 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 110 | - | 100 | 50 | 65 | 480, 3 | 4620 | 1, 6, 7b | NA
SE502380 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D75Y | 600, 3 | 10 | 65 | 50 | 100 | 50 | 65 | 480, 3 | 4620 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 77 | 60 | 100 | 50 | 65 | 480, 3 | 0 | 1, 6, 7b | NA
SE502380 |  |  |  | (SHORT) MC | Telemecanique | LC1D50 (Optional) | 600, 3 | 5 | 52 | 40 | 100 | 50 | 65 | 480, 3 | 4620 | 1, 6, 7b | NA
SE502381 | E40610 | 12.20 | A | FDS | Telemecanique | GS1JU3 | 600, 3 | 200 | 100 | - | 100 | 50 | 52 | 600, 3 | 4620 | 1, 6, 7b, 9 | NA
SE502381 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 90 | - | 100 | 50 | 52 | 600, 3 | 4620 | 1, 6, 7b | NA
SE502381 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D62Y | 600, 3 | 5 | 52 | 50 | 100 | 50 | 52 | 600, 3 | 4620 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D65 (Optional) | 600, 3 | 5 | 52 | 50 | 100 | 50 | 52 | 600, 3 | 0 | 1, 6, 7b | NA
SE502381 |  |  |  | (SHORT) MC | Telemecanique | LC1D40 (Optional) | 600, 3 | 5 | 32 | 30 | 100 | 50 | 52 | 600, 3 | 4620 | 1, 6, 7b | NA
SE502382 | E40610 | 12.20 | A | FDS | Telemecanique | GS1QU3 | 600, 3 | 200 | 400 | - | 100 | 60 | 169 | 208, 3 | 28800 | 1, 6, 7d, 9 | NA
SE502382 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 300 | - | 100 | 60 | 169 | 208, 3 | 28800 | 1, 6, 7d | NA
SE502382 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C21Y | 600, 3 | 10 | 169 | 60 | 100 | 60 | 169 | 208, 3 | 28800 | 1, 6, 7d | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 143 | 50 | 100 | 60 | 169 | 208, 3 | 0 | 1, 6, 7d | NA
SE502382 |  |  |  | (SHORT) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 114 | 40 | 100 | 60 | 169 | 208, 3 | 28800 | 1, 6, 7d | NA
SE502383 | E40610 | 12.20 | A | FDS | Telemecanique | GS1QU3 | 600, 3 | 200 | 400 | - | 100 | 60 | 154 | 240, 3 | 8778 | 1, 6, 7c, 9 | NA
SE502383 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 250 | - | 100 | 60 | 154 | 240, 3 | 6468 | 1, 6, 7c | NA
SE502383 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C17Y | 600, 3 | 10 | 154 | 60 | 100 | 60 | 154 | 240, 3 | 6468 | 1, 6, 7c | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 154 | 60 | 100 | 60 | 154 | 240, 3 | 0 | 1, 6, 7c | NA
SE502383 |  |  |  | (SHORT) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 104 | 40 | 100 | 60 | 154 | 240, 3 | 6468 | 1, 6, 7c | NA
SE502384 | E40610 | 12.20 | A | FDS | Telemecanique | GS1MU3 | 600, 3 | 200 | 200 | - | 100 | 60 | 77 | 480, 3 | 4620 | 1, 6, 7L, 9 | NA
SE502384 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 125 | - | 100 | 60 | 77 | 480, 3 | 4620 | 1, 6, 7L | NA
SE502384 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D88Y | 600, 3 | 10 | 77 | 60 | 100 | 60 | 77 | 480, 3 | 4620 | 1, 6, 7L | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 96 | 75 | 100 | 60 | 77 | 480, 3 | 0 | 1, 6, 7L | NA
SE502384 |  |  |  | (SHORT) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 77 | 60 | 100 | 60 | 77 | 480, 3 | 4620 | 1, 6, 7L | NA
SE502385 | E40610 | 12.20 | A | FDS | Telemecanique | GS1MU3 | 600, 3 | 200 | 200 | - | 100 | 60 | 62 | 600, 3 | 4620 | 1, 6, 7b, 9 | NA
SE502385 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 110 | - | 100 | 60 | 62 | 600, 3 | 4620 | 1, 6, 7b | NA
SE502385 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D75Y | 600, 3 | 10 | 62 | 60 | 100 | 60 | 62 | 600, 3 | 4620 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 62 | 60 | 100 | 60 | 62 | 600, 3 | 0 | 1, 6, 7b | NA
SE502385 |  |  |  | (SHORT) MC | Telemecanique | LC1D50 (Optional) | 600, 3 | 5 | 41 | 40 | 100 | 60 | 62 | 600, 3 | 4620 | 1, 6, 7b | NA
SE502386 | E40610 | 12.20 | A | FDS | Telemecanique | GS1QU3 | 600, 3 | 200 | 400 | - | 100 | 75 | 211 | 208, 3 | 28800 | 1, 6, 7p, 9 | NA
SE502386 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 350 | - | 100 | 75 | 211 | 208, 3 | 28800 | 1, 6, 7p | NA
SE502386 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C25Y | 600, 3 | 18 | 211 | 75 | 100 | 75 | 211 | 208, 3 | 28800 | 1, 6, 7p | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F225 (Optional) | 600, 3 | 10 | 169 | 60 | 100 | 75 | 211 | 208, 3 | 0 | 1, 6, 7p | NA
SE502386 |  |  |  | (SHORT) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 143 | 50 | 100 | 75 | 211 | 208, 3 | 28800 | 1, 6, 7p | NA
SE502387 | E40610 | 12.20 | A | FDS | Telemecanique | GS1QU3 | 600, 3 | 200 | 400 | - | 100 | 75 | 192 | 240, 3 | 28800 | 1, 6, 7d, 9 | NA
SE502387 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 350 | - | 100 | 75 | 192 | 240, 3 | 28800 | 1, 6, 7d | NA
SE502387 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C21Y | 600, 3 | 10 | 192 | 75 | 100 | 75 | 192 | 240, 3 | 28800 | 1, 6, 7d | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F225 (Optional) | 600, 3 | 10 | 192 | 75 | 100 | 75 | 192 | 240, 3 | 0 | 1, 6, 7d | NA
SE502387 |  |  |  | (SHORT) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 130 | 50 | 100 | 75 | 192 | 240, 3 | 28800 | 1, 6, 7d | NA
SE502388 | E40610 | 12.20 | A | FDS | Telemecanique | GS1MU3 | 600, 3 | 200 | 200 | - | 100 | 75 | 96 | 480, 3 | 4620 | 1, 6, 7m, 9 | NA
SE502388 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 175 | - | 100 | 75 | 96 | 480, 3 | 4620 | 1, 6, 7m | NA
SE502388 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C11Y | 600, 3 | 10 | 96 | 75 | 100 | 75 | 96 | 480, 3 | 4620 | 1, 6, 7m | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 96 | 75 | 100 | 75 | 96 | 480, 3 | 0 | 1, 6, 7m | NA
SE502388 |  |  |  | (SHORT) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 77 | 60 | 100 | 75 | 96 | 480, 3 | 4620 | 1, 6, 7m | NA
SE502389 | E40610 | 12.20 | A | FDS | Telemecanique | GS1MU3 | 600, 3 | 200 | 200 | - | 100 | 75 | 77 | 600, 3 | 4620 | 1, 6, 7L, 9 | NA
SE502389 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 125 | - | 100 | 75 | 77 | 600, 3 | 4620 | 1, 6, 7L | NA
SE502389 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D88Y | 600, 3 | 10 | 77 | 75 | 100 | 75 | 77 | 600, 3 | 4620 | 1, 6, 7L | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 99 | 100 | 100 | 75 | 77 | 600, 3 | 0 | 1, 6, 7L | NA
SE502389 |  |  |  | (SHORT) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 62 | 60 | 100 | 75 | 77 | 600, 3 | 4620 | 1, 6, 7L | NA
SE502390 | E40610 | 12.20 | A | FDS | Telemecanique | GS1SU3 | 600, 3 | 200 | 600 | - | 100 | 100 | 273 | 208, 3 | 28800 | 1, 6, 7h, 9 | NA
SE502390 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 450 | - | 100 | 100 | 273 | 208, 3 | 28800 | 1, 6, 7h | NA
SE502390 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C32Y | 600, 3 | 18 | 273 | 100 | 100 | 100 | 273 | 208, 3 | 28800 | 1, 6, 7h | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 211 | 75 | 100 | 100 | 273 | 208, 3 | 0 | 1, 6, 7h | NA
SE502390 |  |  |  | (SHORT) MC | Telemecanique | LC1F265 (Optional) | 600, 3 | 10 | 169 | 60 | 100 | 100 | 273 | 208, 3 | 28800 | 1, 6, 7h | NA
SE502391 | E40610 | 12.20 | A | FDS | Telemecanique | GS1QU3 | 600, 3 | 200 | 400 | - | 100 | 100 | 248 | 240, 3 | 28800 | 1, 6, 7h, 9 | NA
SE502391 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 400 | - | 100 | 100 | 248 | 240, 3 | 28800 | 1, 6, 7h | NA
SE502391 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C25Y | 600, 3 | 18 | 248 | 100 | 100 | 100 | 248 | 240, 3 | 28800 | 1, 6, 7h | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F265 (Optional) | 600, 3 | 10 | 192 | 75 | 100 | 100 | 248 | 240, 3 | 0 | 1, 6, 7h | NA
SE502391 |  |  |  | (SHORT) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 154 | 60 | 100 | 100 | 248 | 240, 3 | 28800 | 1, 6, 7h | NA
SE502392 | E40610 | 12.20 | A | FDS | Telemecanique | GS1QU3 | 600, 3 | 200 | 400 | - | 100 | 100 | 124 | 480, 3 | 8778 | 1, 6, 7n, 9 | NA
SE502392 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 225 | - | 100 | 100 | 124 | 480, 3 | 6468 | 1, 6, 7n | NA
SE502392 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C14Y | 600, 3 | 10 | 124 | 100 | 100 | 100 | 124 | 480, 3 | 6468 | 1, 6, 7n | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 124 | 100 | 100 | 100 | 124 | 480, 3 | 0 | 1, 6, 7n | NA
SE502392 |  |  |  | (SHORT) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 96 | 75 | 100 | 100 | 124 | 480, 3 | 6468 | 1, 6, 7n | NA
SE502393 | E40610 | 12.20 | A | FDS | Telemecanique | GS1MU3 | 600, 3 | 200 | 200 | - | 100 | 100 | 99 | 600, 3 | 4620 | 1, 6, 7m, 9 | NA
SE502393 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 175 | - | 100 | 100 | 99 | 600, 3 | 4620 | 1, 6, 7m | NA
SE502393 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C11Y | 600, 3 | 10 | 99 | 100 | 100 | 100 | 99 | 600, 3 | 4620 | 1, 6, 7m | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 99 | 100 | 100 | 100 | 99 | 600, 3 | 0 | 1, 6, 7m | NA
SE502393 |  |  |  | (SHORT) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 62 | 60 | 100 | 100 | 99 | 600, 3 | 4620 | 1, 6, 7m | NA
SE502394 | E40610 | 12.20 | A | FDS | Telemecanique | GS1SU3 | 600, 3 | 200 | 600 | - | 100 | 125 | 343 | 208, 3 | 50400 | 1, 6, 7i, 9 | NA
SE502394 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 600 | - | 100 | 125 | 343 | 208, 3 | 50400 | 1, 6, 7i | NA
SE502394 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C41Y | 600, 3 | 18 | 343 | 125 | 100 | 125 | 343 | 208, 3 | 50400 | 1, 6, 7i | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 273 | 100 | 100 | 125 | 343 | 208, 3 | 0 | 1, 6, 7i | NA
SE502394 |  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 211 | 75 | 100 | 125 | 343 | 208, 3 | 50400 | 1, 6, 7i | NA
SE502395 | E40610 | 12.20 | A | FDS | Telemecanique | GS1SU3 | 600, 3 | 200 | 600 | - | 100 | 125 | 312 | 240, 3 | 28800 | 1, 6, 7i, 9 | NA
SE502395 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 500 | - | 100 | 125 | 312 | 240, 3 | 28800 | 1, 6, 7i | NA
SE502395 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C32Y | 600, 3 | 18 | 312 | 125 | 100 | 125 | 312 | 240, 3 | 28800 | 1, 6, 7i | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 248 | 100 | 100 | 125 | 312 | 240, 3 | 0 | 1, 6, 7i | NA
SE502395 |  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 248 | 100 | 100 | 125 | 312 | 240, 3 | 28800 | 1, 6, 7i | NA
SE502396 | E40610 | 12.20 | A | FDS | Telemecanique | GS1QU3 | 600, 3 | 200 | 400 | - | 100 | 125 | 156 | 480, 3 | 8778 | 1, 6, 7c, 9 | NA
SE502396 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 250 | - | 100 | 125 | 156 | 480, 3 | 6468 | 1, 6, 7c | NA
SE502396 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C17Y | 600, 3 | 10 | 156 | 125 | 100 | 125 | 156 | 480, 3 | 6468 | 1, 6, 7c | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 156 | 125 | 100 | 125 | 156 | 480, 3 | 0 | 1, 6, 7c | NA
SE502396 |  |  |  | (SHORT) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 96 | 75 | 100 | 125 | 156 | 480, 3 | 6468 | 1, 6, 7c | NA
SE502397 | E40610 | 12.20 | A | FDS | Telemecanique | GS1QU3 | 600, 3 | 200 | 400 | - | 100 | 125 | 125 | 600, 3 | 8778 | 1, 6, 7n, 9 | NA
SE502397 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 225 | - | 100 | 125 | 125 | 600, 3 | 6468 | 1, 6, 7n | NA
SE502397 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C14Y | 600, 3 | 10 | 125 | 125 | 100 | 125 | 125 | 600, 3 | 6468 | 1, 6, 7n | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 125 | 125 | 100 | 125 | 125 | 600, 3 | 0 | 1, 6, 7n | NA
SE502397 |  |  |  | (SHORT) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 99 | 100 | 100 | 125 | 125 | 600, 3 | 6468 | 1, 6, 7n | NA
SE502398 | E40610 | 12.20 | A | FDS | Telemecanique | GS1SU3 | 600, 3 | 200 | 600 | - | 100 | 150 | 360 | 240, 3 | 50400 | 1, 6, 7e, 9 | NA
SE502398 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 600 | - | 100 | 150 | 360 | 240, 3 | 50400 | 1, 6, 7e | NA
SE502398 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C41Y | 600, 3 | 18 | 360 | 150 | 100 | 150 | 360 | 240, 3 | 50400 | 1, 6, 7e | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 312 | 125 | 100 | 150 | 360 | 240, 3 | 0 | 1, 6, 7e | NA
SE502398 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 312 | 125 | 100 | 150 | 360 | 240, 3 | 50400 | 1, 6, 7e | NA
SE502399 | E40610 | 12.20 | A | FDS | Telemecanique | GS1QU3 | 600, 3 | 200 | 400 | - | 100 | 150 | 180 | 480, 3 | 28800 | 1, 6, 7d, 9 | NA
SE502399 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 300 | - | 100 | 150 | 180 | 480, 3 | 28800 | 1, 6, 7d | NA
SE502399 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C21Y | 600, 3 | 10 | 180 | 150 | 100 | 150 | 180 | 480, 3 | 28800 | 1, 6, 7d | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F225 (Optional) | 600, 3 | 10 | 180 | 150 | 100 | 150 | 180 | 480, 3 | 0 | 1, 6, 7d | NA
SE502399 |  |  |  | (SHORT) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 124 | 100 | 100 | 150 | 180 | 480, 3 | 28800 | 1, 6, 7d | NA
SE502400 | E40610 | 12.20 | A | FDS | Telemecanique | GS1QU3 | 600, 3 | 200 | 400 | - | 100 | 150 | 144 | 600, 3 | 8778 | 1, 6, 7c, 9 | NA
SE502400 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 250 | - | 100 | 150 | 144 | 600, 3 | 6468 | 1, 6, 7c | NA
SE502400 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C17Y | 600, 3 | 10 | 144 | 150 | 100 | 150 | 144 | 600, 3 | 6468 | 1, 6, 7c | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 144 | 150 | 100 | 150 | 144 | 600, 3 | 0 | 1, 6, 7c | NA
SE502400 |  |  |  | (SHORT) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 99 | 100 | 100 | 150 | 144 | 600, 3 | 6468 | 1, 6, 7c | NA
SE502401 | E40610 | 12.20 | A | FDS | Telemecanique | GS1QU3 | 600, 3 | 200 | 400 | - | 100 | 200 | 240 | 480, 3 | 28800 | 1, 6, 7h, 9 | NA
SE502401 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 400 | - | 100 | 200 | 240 | 480, 3 | 28800 | 1, 6, 7h | NA
SE502401 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C25Y | 600, 3 | 18 | 240 | 200 | 100 | 200 | 240 | 480, 3 | 28800 | 1, 6, 7h | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F265 (Optional) | 600, 3 | 10 | 180 | 150 | 100 | 200 | 240 | 480, 3 | 0 | 1, 6, 7h | NA
SE502401 |  |  |  | (SHORT) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 156 | 125 | 100 | 200 | 240 | 480, 3 | 28800 | 1, 6, 7h | NA
SE502402 | E40610 | 12.20 | A | FDS | Telemecanique | GS1QU3 | 600, 3 | 200 | 400 | - | 100 | 200 | 192 | 600, 3 | 28800 | 1, 6, 7d, 9 | NA
SE502402 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 350 | - | 100 | 200 | 192 | 600, 3 | 28800 | 1, 6, 7d | NA
SE502402 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C21Y | 600, 3 | 10 | 192 | 200 | 100 | 200 | 192 | 600, 3 | 28800 | 1, 6, 7d | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F225 (Optional) | 600, 3 | 10 | 192 | 200 | 100 | 200 | 192 | 600, 3 | 0 | 1, 6, 7d | NA
SE502402 |  |  |  | (SHORT) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 125 | 125 | 100 | 200 | 192 | 600, 3 | 28800 | 1, 6, 7d | NA
SE502403 | E40610 | 12.20 | A | FDS | Telemecanique | GS1SU3 | 600, 3 | 200 | 600 | - | 100 | 250 | 302 | 480, 3 | 28800 | 1, 6, 7s, 9 | NA
SE502403 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 500 | - | 100 | 250 | 302 | 480, 3 | 28800 | 1, 6, 7s | NA
SE502403 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C32Y | 600, 3 | 18 | 302 | 250 | 100 | 250 | 302 | 480, 3 | 28800 | 1, 6, 7s | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 240 | 200 | 100 | 250 | 302 | 480, 3 | 0 | 1, 6, 7s | NA
SE502403 |  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 240 | 200 | 100 | 250 | 302 | 480, 3 | 28800 | 1, 6, 7s | NA
SE502404 | E40610 | 12.20 | A | FDS | Telemecanique | GS1QU3 | 600, 3 | 200 | 400 | - | 100 | 250 | 242 | 600, 3 | 28800 | 1, 6, 7h, 9 | NA
SE502404 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 400 | - | 100 | 250 | 242 | 600, 3 | 28800 | 1, 6, 7h | NA
SE502404 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C25Y | 600, 3 | 18 | 242 | 250 | 100 | 250 | 242 | 600, 3 | 28800 | 1, 6, 7h | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F265 (Optional) | 600, 3 | 10 | 161 | 175 | 100 | 250 | 242 | 600, 3 | 0 | 1, 6, 7h | NA
SE502404 |  |  |  | (SHORT) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 144 | 150 | 100 | 250 | 242 | 600, 3 | 28800 | 1, 6, 7h | NA
SE502405 | E40610 | 12.20 | A | FDS | Telemecanique | GS1SU3 | 600, 3 | 200 | 600 | - | 100 | 300 | 361 | 480, 3 | 50400 | 1, 6, 7e, 9 | NA
SE502405 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 600 | - | 100 | 300 | 361 | 480, 3 | 50400 | 1, 6, 7e | NA
SE502405 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C41Y | 600, 3 | 18 | 361 | 300 | 100 | 300 | 361 | 480, 3 | 50400 | 1, 6, 7e | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 302 | 250 | 100 | 300 | 361 | 480, 3 | 0 | 1, 6, 7e | NA
SE502405 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 302 | 250 | 100 | 300 | 361 | 480, 3 | 50400 | 1, 6, 7e | NA
SE502406 | E40610 | 12.20 | A | FDS | Telemecanique | GS1SU3 | 600, 3 | 200 | 600 | - | 100 | 300 | 289 | 600, 3 | 28800 | 1, 6, 7s, 9 | NA
SE502406 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 500 | - | 100 | 300 | 289 | 600, 3 | 28800 | 1, 6, 7s | NA
SE502406 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C32Y | 600, 3 | 18 | 289 | 300 | 100 | 300 | 289 | 600, 3 | 28800 | 1, 6, 7s | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 242 | 250 | 100 | 300 | 289 | 600, 3 | 0 | 1, 6, 7s | NA
SE502406 |  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 242 | 250 | 100 | 300 | 289 | 600, 3 | 28800 | 1, 6, 7s | NA
SE502407 | E40610 | 12.20 | A | FDS | Telemecanique | GS1SU3 | 600, 3 | 200 | 600 | - | 100 | 350 | 336 | 600, 3 | 50400 | 1, 6, 7i, 9 | NA
SE502407 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 600 | - | 100 | 350 | 336 | 600, 3 | 50400 | 1, 6, 7i | NA
SE502407 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C41Y | 600, 3 | 18 | 336 | 350 | 100 | 350 | 336 | 600, 3 | 50400 | 1, 6, 7i | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 242 | 250 | 100 | 350 | 336 | 600, 3 | 0 | 1, 6, 7i | NA
SE502407 |  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 242 | 250 | 100 | 350 | 336 | 600, 3 | 50400 | 1, 6, 7i | NA
SE502408 | E40610 | 12.20 | A | FDS | Telemecanique | GS1TU3 | 600, 3 | 200 | 800 | - | 100 | 150 | 396 | 208, 3 | 50400 | 1, 6, 7e, 9 | NA
SE502408 |  |  |  | F | Any Listed Mfgr. | Any Class L Fuse Rated: | 600 | 200 | 700 | - | 100 | 150 | 396 | 208, 3 | 50400 | 1, 6, 7e | NA
SE502408 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C48Y | 600, 3 | 18 | 396 | 150 | 100 | 150 | 396 | 208, 3 | 50400 | 1, 6, 7e | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 396 | 150 | 100 | 150 | 396 | 208, 3 | 0 | 1, 6, 7e | NA
SE502408 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 273 | 100 | 100 | 150 | 396 | 208, 3 | 50400 | 1, 6, 7e | NA
SE502409 | E40610 | 12.20 | A | FDS | Telemecanique | GS1TU3 | 600, 3 | 200 | 800 | - | 100 | 200 | 480 | 240, 3 | 50400 | 1, 6, 7r, 9 | NA
SE502409 |  |  |  | F | Any Listed Mfgr. | Any Class L Fuse Rated: | 600 | 200 | 800 | - | 100 | 200 | 480 | 240, 3 | 50400 | 1, 6, 7r | NA
SE502409 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C59Y | 600, 3 | 30 | 480 | 200 | 100 | 200 | 480 | 240, 3 | 50400 | 1, 6, 7r | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 722 | 300 | 100 | 200 | 480 | 240, 3 | 0 | 1, 6, 7r | NA
SE502409 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 480 | 200 | 100 | 200 | 480 | 240, 3 | 50400 | 1, 6, 7r | NA
SE502410 | E40610 | 12.20 | A | FDS | Telemecanique | GS1TU3 | 600, 3 | 200 | 800 | - | 100 | 350 | 414 | 480, 3 | 50400 | 1, 6, 7f, 9 | NA
SE502410 |  |  |  | F | Any Listed Mfgr. | Any Class L Fuse Rated: | 600 | 200 | 700 | - | 100 | 350 | 414 | 480, 3 | 50400 | 1, 6, 7f | NA
SE502410 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C48Y | 600, 3 | 18 | 414 | 350 | 100 | 350 | 414 | 480, 3 | 50400 | 1, 6, 7f | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 477 | 400 | 100 | 350 | 414 | 480, 3 | 0 | 1, 6, 7f | NA
SE502410 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 302 | 250 | 100 | 350 | 414 | 480, 3 | 50400 | 1, 6, 7f | NA
SE502411 | E40610 | 12.20 | A | FDS | Telemecanique | GS1TU3 | 600, 3 | 200 | 800 | - | 100 | 400 | 477 | 480, 3 | 50400 | 1, 6, 7r, 9 | NA
SE502411 |  |  |  | F | Any Listed Mfgr. | Any Class L Fuse Rated: | 600 | 200 | 800 | - | 100 | 400 | 477 | 480, 3 | 50400 | 1, 6, 7r | NA
SE502411 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C59Y | 600, 3 | 30 | 477 | 400 | 100 | 400 | 477 | 480, 3 | 50400 | 1, 6, 7r | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 722 FLA / 4400 LRA | 600 | 100 | 400 | 477 | 480, 3 | 0 | 1, 6, 7r | NA
SE502411 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 477 | 400 | 100 | 400 | 477 | 480, 3 | 50400 | 1, 6, 7r | NA
SE502412 | E40610 | 12.20 | A | FDS | Telemecanique | GS1TU3 | 600, 3 | 200 | 800 | - | 100 | 400 | 382 | 600, 3 | 50400 | 1, 6, 7e, 9 | NA
SE502412 |  |  |  | F | Any Listed Mfgr. | Any Class L Fuse Rated: | 600 | 200 | 700 | - | 100 | 400 | 382 | 600, 3 | 50400 | 1, 6, 7f | NA
SE502412 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C48Y | 600, 3 | 18 | 382 | 400 | 100 | 400 | 382 | 600, 3 | 50400 | 1, 6, 7f | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 472 | 500 | 100 | 400 | 382 | 600, 3 | 0 | 1, 6, 7f | NA
SE502412 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 289 | 300 | 100 | 400 | 382 | 600, 3 | 50400 | 1, 6, 7f | NA
SE502413 | E40610 | 12.20 | A | FDS | Telemecanique | GS1TU3 | 600, 3 | 200 | 800 | - | 100 | 500 | 472 | 600, 3 | 50400 | 1, 6, 7q, 9 | NA
SE502413 |  |  |  | F | Any Listed Mfgr. | Any Class L Fuse Rated: | 600 | 200 | 800 | - | 100 | 500 | 472 | 600, 3 | 50400 | 1, 6, 7q | NA
SE502413 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C59Y | 600, 3 | 30 | 472 | 500 | 100 | 500 | 472 | 600, 3 | 50400 | 1, 6, 7q | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 472 | 500 | 100 | 500 | 472 | 600, 3 | 0 | 1, 6, 7q | NA
SE502413 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 472 | 500 | 100 | 500 | 472 | 600, 3 | 50400 | 1, 6, 7q | NA
SE502414 | E40610 | 12.20 | A | FDS | Telemecanique | GS2EU3 | 600, 3 | 200 | 30 | - | 100 | 3 | 10.6 | 208, 3 | 4620 | 1, 6, 7a, 9 | NA
|  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 20 | - | 100 | 3 | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D17Y | 600, 3 | 5 | 10.6 | 3 | 100 | 3 | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 24.2 | 7.5 | 100 | 3 | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 24.2 | 7.5 | 100 | 3 | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
SE502415 | E40610 | 12.20 | A | FDS | Telemecanique | GS2EU3 | 600, 3 | 200 | 30 | - | 100 | 5 | 16.7 | 208, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502415 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 30 | - | 100 | 5 | 16.7 | 208, 3 | 4620 | 1, 6, 7a | NA
SE502415 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D22Y | 600, 3 | 5 | 16.7 | 5 | 100 | 5 | 16.7 | 208, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 24.2 | 7.5 | 100 | 5 | 16.7 | 208, 3 | 0 | 1, 6, 7a | NA
SE502415 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 24.2 | 7.5 | 100 | 5 | 16.7 | 208, 3 | 4620 | 1, 6, 7a | NA
SE502416 | E40610 | 12.20 | A | FDS | Telemecanique | GS2EU3 | 600, 3 | 200 | 30 | - | 100 | 5 | 15.2 | 240, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502416 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 25 | - | 100 | 5 | 15.2 | 240, 3 | 4620 | 1, 6, 7a | NA
SE502416 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D17Y | 600, 3 | 5 | 15.2 | 5 | 100 | 5 | 15.2 | 240, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 22 | 7.5 | 100 | 5 | 15.2 | 240, 3 | 0 | 1, 6, 7a | NA
SE502416 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 22 | 7.5 | 100 | 5 | 15.2 | 240, 3 | 4620 | 1, 6, 7a | NA
SE502417 | E40610 | 12.20 | A | FDS | Telemecanique | GS2GU3 | 600, 3 | 200 | 60 | - | 100 | 7.5 | 24.2 | 208, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502417 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 45 | - | 100 | 7.5 | 24.2 | 208, 3 | 4620 | 1, 6, 7a | NA
SE502417 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D32Y | 600, 3 | 5 | 24.2 | 7.5 | 100 | 7.5 | 24.2 | 208, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 30.8 | 10 | 100 | 7.5 | 24.2 | 208, 3 | 0 | 1, 6, 7a | NA
SE502417 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 24.2 | 7.5 | 100 | 7.5 | 24.2 | 208, 3 | 4620 | 1, 6, 7a | NA
SE502418 | E40610 | 12.20 | A | FDS | Telemecanique | GS2GU3 | 600, 3 | 200 | 60 | - | 100 | 7.5 | 22 | 240, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502418 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 40 | - | 100 | 7.5 | 22 | 240, 3 | 4620 | 1, 6, 7a | NA
SE502418 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D22Y | 600, 3 | 5 | 22 | 7.5 | 100 | 7.5 | 22 | 240, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 28 | 10 | 100 | 7.5 | 22 | 240, 3 | 0 | 1, 6, 7a | NA
SE502418 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 22 | 7.5 | 100 | 7.5 | 22 | 240, 3 | 4620 | 1, 6, 7a | NA
SE502419 | E40610 | 12.20 | A | FDS | Telemecanique | GS2GU3 | 600, 3 | 200 | 60 | - | 100 | 10 | 30.8 | 208, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502419 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 50 | - | 100 | 10 | 30.8 | 208, 3 | 4620 | 1, 6, 7a | NA
SE502419 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D38Y | 600, 3 | 5 | 30.8 | 10 | 100 | 10 | 30.8 | 208, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D40 (Optional) | 600, 3 | 5 | 30.8 | 10 | 100 | 10 | 30.8 | 208, 3 | 0 | 1, 6, 7a | NA
SE502419 |  |  |  | (SHORT) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 30.8 | 10 | 100 | 10 | 30.8 | 208, 3 | 4620 | 1, 6, 7a | NA
SE502420 | E40610 | 12.20 | A | FDS | Telemecanique | GS2GU3 | 600, 3 | 200 | 60 | - | 100 | 10 | 28 | 240, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502420 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 50 | - | 100 | 10 | 28 | 240, 3 | 4620 | 1, 6, 7a | NA
SE502420 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D32Y | 600, 3 | 5 | 28 | 10 | 100 | 10 | 28 | 240, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 28 | 10 | 100 | 10 | 28 | 240, 3 | 0 | 1, 6, 7a | NA
SE502420 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 22 | 7.5 | 100 | 10 | 28 | 240, 3 | 4620 | 1, 6, 7a | NA
SE502421 | E40610 | 12.20 | A | FDS | Telemecanique | GS2EU3 | 600, 3 | 200 | 30 | - | 100 | 10 | 14 | 480, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502421 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 25 | - | 100 | 10 | 14 | 480, 3 | 4620 | 1, 6, 7a | NA
SE502421 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D17Y | 600, 3 | 5 | 14 | 10 | 100 | 10 | 14 | 480, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 21 | 15 | 100 | 10 | 14 | 480, 3 | 0 | 1, 6, 7a | NA
SE502421 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 21 | 15 | 100 | 10 | 14 | 480, 3 | 4620 | 1, 6, 7a | NA
SE502422 | E40610 | 12.20 | A | FDS | Telemecanique | GS2JU3 | 600, 3 | 200 | 100 | - | 100 | 15 | 46.2 | 208, 3 | 4620 | 1, 6, 7b, 9 | NA
SE502422 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 80 | - | 100 | 15 | 46.2 | 208, 3 | 4620 | 1, 6, 7b | NA
SE502422 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D62Y | 600, 3 | 5 | 46.2 | 15 | 100 | 15 | 46.2 | 208, 3 | 4620 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D50 (Optional) | 600, 3 | 5 | 46.2 | 15 | 100 | 15 | 46.2 | 208, 3 | 0 | 1, 6, 7b | NA
SE502422 |  |  |  | (SHORT) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 30.8 | 10 | 100 | 15 | 46.2 | 208, 3 | 4620 | 1, 6, 7b | NA
SE502423 | E40610 | 12.20 | A | FDS | Telemecanique | GS2JU3 | 600, 3 | 200 | 100 | - | 100 | 15 | 42 | 240, 3 | 4620 | 1, 6, 7k, 9 | NA
SE502423 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 70 | - | 100 | 15 | 42 | 240, 3 | 4620 | 1, 6, 7k | NA
SE502423 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D47Y | 600, 3 | 5 | 42 | 15 | 100 | 15 | 42 | 240, 3 | 4620 | 1, 6, 7k | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D50 (Optional) | 600, 3 | 5 | 42 | 15 | 100 | 15 | 42 | 240, 3 | 0 | 1, 6, 7k | NA
SE502423 |  |  |  | (SHORT) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 28 | 10 | 100 | 15 | 42 | 240, 3 | 4620 | 1, 6, 7k | NA
SE502424 | E40610 | 12.20 | A | FDS | Telemecanique | GS2GU3 | 600, 3 | 200 | 60 | - | 100 | 15 | 21 | 480, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502424 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 35 | - | 100 | 15 | 21 | 480, 3 | 4620 | 1, 6, 7a | NA
SE502424 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D22Y | 600, 3 | 5 | 21 | 15 | 100 | 15 | 21 | 480, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 21 | 15 | 100 | 15 | 21 | 480, 3 | 0 | 1, 6, 7a | NA
SE502424 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 21 | 15 | 100 | 15 | 21 | 480, 3 | 4620 | 1, 6, 7a | NA
SE502425 | E40610 | 12.20 | A | FDS | Telemecanique | GS2EU3 | 600, 3 | 200 | 30 | - | 100 | 15 | 17 | 600, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502425 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 30 | - | 100 | 15 | 17 | 600, 3 | 4620 | 1, 6, 7a | NA
SE502425 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D17Y | 600, 3 | 5 | 17 | 15 | 100 | 15 | 17 | 600, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 22 | 20 | 100 | 15 | 17 | 600, 3 | 0 | 1, 6, 7a | NA
SE502425 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 22 | 20 | 100 | 15 | 17 | 600, 3 | 4620 | 1, 6, 7a | NA
SE502426 | E40610 | 12.20 | A | FDS | Telemecanique | GS2JU3 | 600, 3 | 200 | 100 | - | 100 | 20 | 59.4 | 208, 3 | 4620 | 1, 6, 7b, 9 | NA
SE502426 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 100 | - | 100 | 20 | 59.4 | 208, 3 | 4620 | 1, 6, 7b | NA
SE502426 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D75Y | 600, 3 | 10 | 59.4 | 20 | 100 | 20 | 59.4 | 208, 3 | 4620 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D65 (Optional) | 600, 3 | 5 | 59.4 | 20 | 100 | 20 | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
SE502426 |  |  |  | (SHORT) MC | Telemecanique | LC1D50 (Optional) | 600, 3 | 5 | 46.2 | 15 | 100 | 20 | 59.4 | 208, 3 | 4620 | 1, 6, 7b | NA
SE502427 | E40610 | 12.20 | A | FDS | Telemecanique | GS2JU3 | 600, 3 | 200 | 100 | - | 100 | 20 | 54 | 240, 3 | 4620 | 1, 6, 7b, 9 | NA
SE502427 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 90 | - | 100 | 20 | 54 | 240, 3 | 4620 | 1, 6, 7b | NA
SE502427 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D62Y | 600, 3 | 5 | 54 | 20 | 100 | 20 | 54 | 240, 3 | 4620 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D65 (Optional) | 600, 3 | 5 | 54 | 20 | 100 | 20 | 54 | 240, 3 | 0 | 1, 6, 7b | NA
SE502427 |  |  |  | (SHORT) MC | Telemecanique | LC1D40 (Optional) | 600, 3 | 5 | 28 | 10 | 100 | 20 | 54 | 240, 3 | 4620 | 1, 6, 7b | NA
SE502428 | E40610 | 12.20 | A | FDS | Telemecanique | GS2GU3 | 600, 3 | 200 | 60 | - | 100 | 20 | 27 | 480, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502428 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 45 | - | 100 | 20 | 27 | 480, 3 | 4620 | 1, 6, 7a | NA
SE502428 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D32Y | 600, 3 | 5 | 27 | 20 | 100 | 20 | 27 | 480, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 27 | 20 | 100 | 20 | 27 | 480, 3 | 0 | 1, 6, 7a | NA
SE502428 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 21 | 15 | 100 | 20 | 27 | 480, 3 | 4620 | 1, 6, 7a | NA
SE502429 | E40610 | 12.20 | A | FDS | Telemecanique | GS2GU3 | 600, 3 | 200 | 60 | - | 100 | 20 | 22 | 600, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502429 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 40 | - | 100 | 20 | 22 | 600, 3 | 4620 | 1, 6, 7a | NA
SE502429 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D22Y | 600, 3 | 5 | 22 | 20 | 100 | 20 | 22 | 600, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 22 | 20 | 100 | 20 | 22 | 600, 3 | 0 | 1, 6, 7a | NA
SE502429 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 22 | 20 | 100 | 20 | 22 | 600, 3 | 4620 | 1, 6, 7a | NA
SE502430 | E40610 | 12.20 | A | FDS | Telemecanique | GS2MU3 | 600, 3 | 200 | 200 | - | 100 | 25 | 74.8 | 208, 3 | 4620 | 1, 6, 7L, 9 | NA
SE502430 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 125 | - | 100 | 25 | 74.8 | 208, 3 | 4620 | 1, 6, 7L | NA
SE502430 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D88Y | 600, 3 | 10 | 74.8 | 25 | 100 | 25 | 74.8 | 208, 3 | 4620 | 1, 6, 7L | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 88 | 30 | 100 | 25 | 74.8 | 208, 3 | 0 | 1, 6, 7L | NA
SE502430 |  |  |  | (SHORT) MC | Telemecanique | LC1D50 (Optional) | 600, 3 | 5 | 46.2 | 15 | 100 | 25 | 74.8 | 208, 3 | 4620 | 1, 6, 7L | NA
SE502431 | E40610 | 12.20 | A | FDS | Telemecanique | GS2MU3 | 600, 3 | 200 | 200 | - | 100 | 25 | 68 | 240, 3 | 4620 | 1, 6, 7b, 9 | NA
SE502431 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 125 | - | 100 | 25 | 68 | 240, 3 | 4620 | 1, 6, 7b | NA
SE502431 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D75Y | 600, 3 | 10 | 68 | 25 | 100 | 25 | 68 | 240, 3 | 4620 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 80 | 30 | 100 | 25 | 68 | 240, 3 | 0 | 1, 6, 7b | NA
SE502431 |  |  |  | (SHORT) MC | Telemecanique | LC1D50 (Optional) | 600, 3 | 5 | 42 | 15 | 100 | 25 | 68 | 240, 3 | 4620 | 1, 6, 7b | NA
SE502432 | E40610 | 12.20 | A | FDS | Telemecanique | GS2GU3 | 600, 3 | 200 | 60 | - | 100 | 25 | 34 | 480, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502432 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 60 | - | 100 | 25 | 34 | 480, 3 | 4620 | 1, 6, 7a | NA
SE502432 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D38Y | 600, 3 | 5 | 34 | 25 | 100 | 25 | 34 | 480, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D40 (Optional) | 600, 3 | 5 | 40 | 30 | 100 | 25 | 34 | 480, 3 | 0 | 1, 6, 7a | NA
SE502432 |  |  |  | (SHORT) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 27 | 20 | 100 | 25 | 34 | 480, 3 | 4620 | 1, 6, 7a | NA
SE502433 | E40610 | 12.20 | A | FDS | Telemecanique | GS2GU3 | 600, 3 | 200 | 60 | - | 100 | 25 | 27 | 600, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502433 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 45 | - | 100 | 25 | 27 | 600, 3 | 4620 | 1, 6, 7a | NA
SE502433 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D32Y | 600, 3 | 5 | 27 | 25 | 100 | 25 | 27 | 600, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 32 | 30 | 100 | 25 | 27 | 600, 3 | 0 | 1, 6, 7a | NA
SE502433 |  |  |  | (SHORT) MC | Telemecanique | LC1D25 (Optional) | 600, 3 | 5 | 22 | 20 | 100 | 25 | 27 | 600, 3 | 4620 | 1, 6, 7a | NA
SE502434 | E40610 | 12.20 | A | FDS | Telemecanique | GS2MU3 | 600, 3 | 200 | 200 | - | 100 | 30 | 88 | 208, 3 | 4620 | 1, 6, 7m, 9 | NA
SE502434 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 150 | - | 100 | 30 | 88 | 208, 3 | 4620 | 1, 6, 7m | NA
SE502434 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C11Y | 600, 3 | 10 | 88 | 30 | 100 | 30 | 88 | 208, 3 | 4620 | 1, 6, 7m | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 88 | 30 | 100 | 30 | 88 | 208, 3 | 0 | 1, 6, 7m | NA
SE502434 |  |  |  | (SHORT) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 74.8 | 25 | 100 | 30 | 88 | 208, 3 | 4620 | 1, 6, 7m | NA
SE502435 | E40610 | 12.20 | A | FDS | Telemecanique | GS2MU3 | 600, 3 | 200 | 200 | - | 100 | 30 | 80 | 240, 3 | 4620 | 1, 6, 7L, 9 | NA
SE502435 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 150 | - | 100 | 30 | 80 | 240, 3 | 4620 | 1, 6, 7L | NA
SE502435 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D88Y | 600, 3 | 10 | 80 | 30 | 100 | 30 | 80 | 240, 3 | 4620 | 1, 6, 7L | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 104 | 40 | 100 | 30 | 80 | 240, 3 | 0 | 1, 6, 7L | NA
SE502435 |  |  |  | (SHORT) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 80 | 30 | 100 | 30 | 80 | 240, 3 | 4620 | 1, 6, 7L | NA
SE502436 | E40610 | 12.20 | A | FDS | Telemecanique | GS2JU3 | 600, 3 | 200 | 100 | - | 100 | 30 | 40 | 480, 3 | 4620 | 1, 6, 7k, 9 | NA
SE502436 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 70 | - | 100 | 30 | 40 | 480, 3 | 4620 | 1, 6, 7k | NA
SE502436 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D47Y | 600, 3 | 5 | 40 | 30 | 100 | 30 | 40 | 480, 3 | 4620 | 1, 6, 7k | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D50 (Optional) | 600, 3 | 5 | 52 | 40 | 100 | 30 | 40 | 480, 3 | 0 | 1, 6, 7k | NA
SE502436 |  |  |  | (SHORT) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 27 | 20 | 100 | 30 | 40 | 480, 3 | 4620 | 1, 6, 7k | NA
SE502437 | E40610 | 12.20 | A | FDS | Telemecanique | GS2GU3 | 600, 3 | 200 | 60 | - | 100 | 30 | 32 | 600, 3 | 4620 | 1, 6, 7a, 9 | NA
SE502437 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 60 | - | 100 | 30 | 32 | 600, 3 | 4620 | 1, 6, 7a | NA
SE502437 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D38Y | 600, 3 | 5 | 32 | 30 | 100 | 30 | 32 | 600, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D40 (Optional) | 600, 3 | 5 | 32 | 30 | 100 | 30 | 32 | 600, 3 | 0 | 1, 6, 7a | NA
SE502437 |  |  |  | (SHORT) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 32 | 30 | 100 | 30 | 32 | 600, 3 | 4620 | 1, 6, 7a | NA
SE502438 | E40610 | 12.20 | A | FDS | Telemecanique | GS2MU3 | 600, 3 | 200 | 200 | - | 100 | 40 | 114 | 208, 3 | 6468 | 1, 6, 7n, 9 | NA
SE502438 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 200 | - | 100 | 40 | 114 | 208, 3 | 6468 | 1, 6, 7n | NA
SE502438 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C14Y | 600, 3 | 10 | 114 | 40 | 100 | 40 | 114 | 208, 3 | 6468 | 1, 6, 7n | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 114 | 40 | 100 | 40 | 114 | 208, 3 | 0 | 1, 6, 7n | NA
SE502438 |  |  |  | (SHORT) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 74.8 | 25 | 100 | 40 | 114 | 208, 3 | 6468 | 1, 6, 7n | NA
SE502439 | E40610 | 12.20 | A | FDS | Telemecanique | GS2MU3 | 600, 3 | 200 | 200 | - | 100 | 40 | 104 | 240, 3 | 4620 | 1, 6, 7m, 9 | NA
SE502439 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 175 | - | 100 | 40 | 104 | 240, 3 | 4620 | 1, 6, 7m | NA
SE502439 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C11Y | 600, 3 | 10 | 104 | 40 | 100 | 40 | 104 | 240, 3 | 4620 | 1, 6, 7m | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 104 | 40 | 100 | 40 | 104 | 240, 3 | 0 | 1, 6, 7m | NA
SE502439 |  |  |  | (SHORT) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 80 | 30 | 100 | 40 | 104 | 240, 3 | 4620 | 1, 6, 7m | NA
SE502440 | E40610 | 12.20 | A | FDS | Telemecanique | GS2JU3 | 600, 3 | 200 | 100 | - | 100 | 40 | 52 | 480, 3 | 4620 | 1, 6, 7b, 9 | NA
SE502440 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 90 | - | 100 | 40 | 52 | 480, 3 | 4620 | 1, 6, 7b | NA
SE502440 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D62Y | 600, 3 | 5 | 52 | 40 | 100 | 40 | 52 | 480, 3 | 4620 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D65 (Optional) | 600, 3 | 5 | 65 | 50 | 100 | 40 | 52 | 480, 3 | 0 | 1, 6, 7b | NA
SE502440 |  |  |  | (SHORT) MC | Telemecanique | LC1D40 (Optional) | 600, 3 | 5 | 40 | 30 | 100 | 40 | 52 | 480, 3 | 4620 | 1, 6, 7b | NA
SE502441 | E40610 | 12.20 | A | FDS | Telemecanique | GS2JU3 | 600, 3 | 200 | 100 | - | 100 | 40 | 41 | 600, 3 | 4620 | 1, 6, 7k, 9 | NA
SE502441 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 70 | - | 100 | 40 | 41 | 600, 3 | 4620 | 1, 6, 7k | NA
SE502441 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D47Y | 600, 3 | 5 | 41 | 40 | 100 | 40 | 41 | 600, 3 | 4620 | 1, 6, 7k | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D50 (Optional) | 600, 3 | 5 | 41 | 40 | 100 | 40 | 41 | 600, 3 | 0 | 1, 6, 7k | NA
SE502441 |  |  |  | (SHORT) MC | Telemecanique | LC1D32 (Optional) | 600, 3 | 5 | 32 | 30 | 100 | 40 | 41 | 600, 3 | 4620 | 1, 6, 7k | NA
SE502442 | E40610 | 12.20 | A | FDS | Telemecanique | GS2QU3 | 600, 3 | 200 | 400 | - | 100 | 50 | 143 | 208, 3 | 8778 | 1, 6, 7c, 9 | NA
SE502442 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 250 | - | 100 | 50 | 143 | 208, 3 | 6468 | 1, 6, 7c | NA
SE502442 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C17Y | 600, 3 | 10 | 143 | 50 | 100 | 50 | 143 | 208, 3 | 6468 | 1, 6, 7c | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 143 | 50 | 100 | 50 | 143 | 208, 3 | 0 | 1, 6, 7c | NA
SE502442 |  |  |  | (SHORT) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 88 | 30 | 100 | 50 | 143 | 208, 3 | 6468 | 1, 6, 7c | NA
SE502443 | E40610 | 12.20 | A | FDS | Telemecanique | GS2QU3 | 600, 3 | 200 | 400 | - | 100 | 50 | 130 | 240, 3 | 8778 | 1, 6, 7n, 9 | NA
SE502443 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 225 | - | 100 | 50 | 130 | 240, 3 | 6468 | 1, 6, 7n | NA
SE502443 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C14Y | 600, 3 | 10 | 130 | 50 | 100 | 50 | 130 | 240, 3 | 6468 | 1, 6, 7n | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 130 | 50 | 100 | 50 | 130 | 240, 3 | 0 | 1, 6, 7n | NA
SE502443 |  |  |  | (SHORT) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 104 | 40 | 100 | 50 | 130 | 240, 3 | 6468 | 1, 6, 7n | NA
SE502444 | E40610 | 12.20 | A | FDS | Telemecanique | GS2MU3 | 600, 3 | 200 | 200 | - | 100 | 50 | 65 | 480, 3 | 4620 | 1, 6, 7b, 9 | NA
SE502444 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 110 | - | 100 | 50 | 65 | 480, 3 | 4620 | 1, 6, 7b | NA
SE502444 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D75Y | 600, 3 | 10 | 65 | 50 | 100 | 50 | 65 | 480, 3 | 4620 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 77 | 60 | 100 | 50 | 65 | 480, 3 | 0 | 1, 6, 7b | NA
SE502444 |  |  |  | (SHORT) MC | Telemecanique | LC1D50 (Optional) | 600, 3 | 5 | 52 | 40 | 100 | 50 | 65 | 480, 3 | 4620 | 1, 6, 7b | NA
SE502445 | E40610 | 12.20 | A | FDS | Telemecanique | GS2JU3 | 600, 3 | 200 | 100 | - | 100 | 50 | 52 | 600, 3 | 4620 | 1, 6, 7b, 9 | NA
SE502445 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 90 | - | 100 | 50 | 52 | 600, 3 | 4620 | 1, 6, 7b | NA
SE502445 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D62Y | 600, 3 | 5 | 52 | 50 | 100 | 50 | 52 | 600, 3 | 4620 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D65 (Optional) | 600, 3 | 5 | 52 | 50 | 100 | 50 | 52 | 600, 3 | 0 | 1, 6, 7b | NA
SE502445 |  |  |  | (SHORT) MC | Telemecanique | LC1D40 (Optional) | 600, 3 | 5 | 32 | 30 | 100 | 50 | 52 | 600, 3 | 4620 | 1, 6, 7b | NA
SE502446 | E40610 | 12.20 | A | FDS | Telemecanique | GS2QU3 | 600, 3 | 200 | 400 | - | 100 | 60 | 169 | 208, 3 | 28800 | 1, 6, 7d, 9 | NA
SE502446 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 300 | - | 100 | 60 | 169 | 208, 3 | 28800 | 1, 6, 7d | NA
SE502446 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C21Y | 600, 3 | 10 | 169 | 60 | 100 | 60 | 169 | 208, 3 | 28800 | 1, 6, 7d | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 143 | 50 | 100 | 60 | 169 | 208, 3 | 0 | 1, 6, 7d | NA
SE502446 |  |  |  | (SHORT) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 114 | 40 | 100 | 60 | 169 | 208, 3 | 28800 | 1, 6, 7d | NA
SE502447 | E40610 | 12.20 | A | FDS | Telemecanique | GS2QU3 | 600, 3 | 200 | 400 | - | 100 | 60 | 154 | 240, 3 | 8778 | 1, 6, 7c, 9 | NA
SE502447 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 250 | - | 100 | 60 | 154 | 240, 3 | 6468 | 1, 6, 7c | NA
SE502447 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C17Y | 600, 3 | 10 | 154 | 60 | 100 | 60 | 154 | 240, 3 | 6468 | 1, 6, 7c | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 154 | 60 | 100 | 60 | 154 | 240, 3 | 0 | 1, 6, 7c | NA
SE502447 |  |  |  | (SHORT) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 104 | 40 | 100 | 60 | 154 | 240, 3 | 6468 | 1, 6, 7c | NA
SE502448 | E40610 | 12.20 | A | FDS | Telemecanique | GS2MU3 | 600, 3 | 200 | 200 | - | 100 | 60 | 77 | 480, 3 | 4620 | 1, 6, 7L, 9 | NA
SE502448 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 125 | - | 100 | 60 | 77 | 480, 3 | 4620 | 1, 6, 7L | NA
SE502448 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D88Y | 600, 3 | 10 | 77 | 60 | 100 | 60 | 77 | 480, 3 | 4620 | 1, 6, 7L | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 96 | 75 | 100 | 60 | 77 | 480, 3 | 0 | 1, 6, 7L | NA
SE502448 |  |  |  | (SHORT) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 77 | 60 | 100 | 60 | 77 | 480, 3 | 4620 | 1, 6, 7L | NA
SE502449 | E40610 | 12.20 | A | FDS | Telemecanique | GS2MU3 | 600, 3 | 200 | 200 | - | 100 | 60 | 62 | 600, 3 | 4620 | 1, 6, 7b, 9 | NA
SE502449 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 110 | - | 100 | 60 | 62 | 600, 3 | 4620 | 1, 6, 7b | NA
SE502449 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D75Y | 600, 3 | 10 | 62 | 60 | 100 | 60 | 62 | 600, 3 | 4620 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 62 | 60 | 100 | 60 | 62 | 600, 3 | 0 | 1, 6, 7b | NA
SE502449 |  |  |  | (SHORT) MC | Telemecanique | LC1D50 (Optional) | 600, 3 | 5 | 41 | 40 | 100 | 60 | 62 | 600, 3 | 4620 | 1, 6, 7b | NA
SE502450 | E40610 | 12.20 | A | FDS | Telemecanique | GS2QU3 | 600, 3 | 200 | 400 | - | 100 | 75 | 211 | 208, 3 | 28800 | 1, 6, 7p, 9 | NA
SE502450 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 350 | - | 100 | 75 | 211 | 208, 3 | 28800 | 1, 6, 7p | NA
SE502450 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C25Y | 600, 3 | 18 | 211 | 75 | 100 | 75 | 211 | 208, 3 | 28800 | 1, 6, 7p | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F225 (Optional) | 600, 3 | 10 | 169 | 60 | 100 | 75 | 211 | 208, 3 | 0 | 1, 6, 7p | NA
SE502450 |  |  |  | (SHORT) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 143 | 50 | 100 | 75 | 211 | 208, 3 | 28800 | 1, 6, 7p | NA
SE502451 | E40610 | 12.20 | A | FDS | Telemecanique | GS2QU3 | 600, 3 | 200 | 400 | - | 100 | 75 | 192 | 240, 3 | 28800 | 1, 6, 7d, 9 | NA
SE502451 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 350 | - | 100 | 75 | 192 | 240, 3 | 28800 | 1, 6, 7d | NA
SE502451 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C21Y | 600, 3 | 10 | 192 | 75 | 100 | 75 | 192 | 240, 3 | 28800 | 1, 6, 7d | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F225 (Optional) | 600, 3 | 10 | 192 | 75 | 100 | 75 | 192 | 240, 3 | 0 | 1, 6, 7d | NA
SE502451 |  |  |  | (SHORT) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 130 | 50 | 100 | 75 | 192 | 240, 3 | 28800 | 1, 6, 7d | NA
SE502452 | E40610 | 12.20 | A | FDS | Telemecanique | GS2MU3 | 600, 3 | 200 | 200 | - | 100 | 75 | 96 | 480, 3 | 4620 | 1, 6, 7m, 9 | NA
SE502452 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 175 | - | 100 | 75 | 96 | 480, 3 | 4620 | 1, 6, 7m | NA
SE502452 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C11Y | 600, 3 | 10 | 96 | 75 | 100 | 75 | 96 | 480, 3 | 4620 | 1, 6, 7m | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 96 | 75 | 100 | 75 | 96 | 480, 3 | 0 | 1, 6, 7m | NA
SE502452 |  |  |  | (SHORT) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 77 | 60 | 100 | 75 | 96 | 480, 3 | 4620 | 1, 6, 7m | NA
SE502453 | E40610 | 12.20 | A | FDS | Telemecanique | GS2MU3 | 600, 3 | 200 | 200 | - | 100 | 75 | 77 | 600, 3 | 4620 | 1, 6, 7L, 9 | NA
SE502453 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 125 | - | 100 | 75 | 77 | 600, 3 | 4620 | 1, 6, 7L | NA
SE502453 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48D88Y | 600, 3 | 10 | 77 | 75 | 100 | 75 | 77 | 600, 3 | 4620 | 1, 6, 7L | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 99 | 100 | 100 | 75 | 77 | 600, 3 | 0 | 1, 6, 7L | NA
SE502453 |  |  |  | (SHORT) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 62 | 60 | 100 | 75 | 77 | 600, 3 | 4620 | 1, 6, 7L | NA
SE502454 | E40610 | 12.20 | A | FDS | Telemecanique | GS2SU3 | 600, 3 | 200 | 600 | - | 100 | 100 | 273 | 208, 3 | 28800 | 1, 6, 7h, 9 | NA
SE502454 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 450 | - | 100 | 100 | 273 | 208, 3 | 28800 | 1, 6, 7h | NA
SE502454 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C32Y | 600, 3 | 18 | 273 | 100 | 100 | 100 | 273 | 208, 3 | 28800 | 1, 6, 7h | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 211 | 75 | 100 | 100 | 273 | 208, 3 | 0 | 1, 6, 7h | NA
SE502454 |  |  |  | (SHORT) MC | Telemecanique | LC1F265 (Optional) | 600, 3 | 10 | 169 | 60 | 100 | 100 | 273 | 208, 3 | 28800 | 1, 6, 7h | NA
SE502455 | E40610 | 12.20 | A | FDS | Telemecanique | GS2QU3 | 600, 3 | 200 | 400 | - | 100 | 100 | 248 | 240, 3 | 28800 | 1, 6, 7h, 9 | NA
SE502455 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 400 | - | 100 | 100 | 248 | 240, 3 | 28800 | 1, 6, 7h | NA
SE502455 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C25Y | 600, 3 | 18 | 248 | 100 | 100 | 100 | 248 | 240, 3 | 28800 | 1, 6, 7h | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F265 (Optional) | 600, 3 | 10 | 192 | 75 | 100 | 100 | 248 | 240, 3 | 0 | 1, 6, 7h | NA
SE502455 |  |  |  | (SHORT) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 154 | 60 | 100 | 100 | 248 | 240, 3 | 28800 | 1, 6, 7h | NA
SE502456 | E40610 | 12.20 | A | FDS | Telemecanique | GS2QU3 | 600, 3 | 200 | 400 | - | 100 | 100 | 124 | 480, 3 | 8778 | 1, 6, 7n, 9 | NA
SE502456 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 225 | - | 100 | 100 | 124 | 480, 3 | 6468 | 1, 6, 7n | NA
SE502456 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C14Y | 600, 3 | 10 | 124 | 100 | 100 | 100 | 124 | 480, 3 | 6468 | 1, 6, 7n | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 124 | 100 | 100 | 100 | 124 | 480, 3 | 0 | 1, 6, 7n | NA
SE502456 |  |  |  | (SHORT) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 96 | 75 | 100 | 100 | 124 | 480, 3 | 6468 | 1, 6, 7n | NA
SE502457 | E40610 | 12.20 | A | FDS | Telemecanique | GS2MU3 | 600, 3 | 200 | 200 | - | 100 | 100 | 99 | 600, 3 | 4620 | 1, 6, 7m, 9 | NA
SE502457 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 175 | - | 100 | 100 | 99 | 600, 3 | 4620 | 1, 6, 7m | NA
SE502457 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C11Y | 600, 3 | 10 | 99 | 100 | 100 | 100 | 99 | 600, 3 | 4620 | 1, 6, 7m | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 99 | 100 | 100 | 100 | 99 | 600, 3 | 0 | 1, 6, 7m | NA
SE502457 |  |  |  | (SHORT) MC | Telemecanique | LC1D80 (Optional) | 600, 3 | 10 | 62 | 60 | 100 | 100 | 99 | 600, 3 | 4620 | 1, 6, 7m | NA
SE502458 | E40610 | 12.20 | A | FDS | Telemecanique | GS2SU3 | 600, 3 | 200 | 600 | - | 100 | 125 | 343 | 208, 3 | 50400 | 1, 6, 7i, 9 | NA
SE502458 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 600 | - | 100 | 125 | 343 | 208, 3 | 50400 | 1, 6, 7i | NA
SE502458 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C41Y | 600, 3 | 18 | 343 | 125 | 100 | 125 | 343 | 208, 3 | 50400 | 1, 6, 7i | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 273 | 100 | 100 | 125 | 343 | 208, 3 | 0 | 1, 6, 7i | NA
SE502458 |  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 211 | 75 | 100 | 125 | 343 | 208, 3 | 50400 | 1, 6, 7i | NA
SE502459 | E40610 | 12.20 | A | FDS | Telemecanique | GS2SU3 | 600, 3 | 200 | 600 | - | 100 | 125 | 312 | 240, 3 | 28800 | 1, 6, 7i, 9 | NA
SE502459 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 500 | - | 100 | 125 | 312 | 240, 3 | 28800 | 1, 6, 7i | NA
SE502459 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C32Y | 600, 3 | 18 | 312 | 125 | 100 | 125 | 312 | 240, 3 | 28800 | 1, 6, 7i | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 248 | 100 | 100 | 125 | 312 | 240, 3 | 0 | 1, 6, 7i | NA
SE502459 |  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 248 | 100 | 100 | 125 | 312 | 240, 3 | 28800 | 1, 6, 7i | NA
SE502460 | E40610 | 12.20 | A | FDS | Telemecanique | GS2QU3 | 600, 3 | 200 | 400 | - | 100 | 125 | 156 | 480, 3 | 8778 | 1, 6, 7c, 9 | NA
SE502460 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 250 | - | 100 | 125 | 156 | 480, 3 | 6468 | 1, 6, 7c | NA
SE502460 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C17Y | 600, 3 | 10 | 156 | 125 | 100 | 125 | 156 | 480, 3 | 6468 | 1, 6, 7c | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 156 | 125 | 100 | 125 | 156 | 480, 3 | 0 | 1, 6, 7c | NA
SE502460 |  |  |  | (SHORT) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 96 | 75 | 100 | 125 | 156 | 480, 3 | 6468 | 1, 6, 7c | NA
SE502461 | E40610 | 12.20 | A | FDS | Telemecanique | GS2QU3 | 600, 3 | 200 | 400 | - | 100 | 125 | 125 | 600, 3 | 8778 | 1, 6, 7n, 9 | NA
SE502461 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 225 | - | 100 | 125 | 125 | 600, 3 | 6468 | 1, 6, 7n | NA
SE502461 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C14Y | 600, 3 | 10 | 125 | 125 | 100 | 125 | 125 | 600, 3 | 6468 | 1, 6, 7n | NA
|  |  |  | (ISO) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 125 | 125 | 100 | 125 | 125 | 600, 3 | 0 | 1, 6, 7n | NA
SE502461 |  |  |  | (SHORT) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 99 | 100 | 100 | 125 | 125 | 600, 3 | 6468 | 1, 6, 7n | NA
SE502462 | E40610 | 12.20 | A | FDS | Telemecanique | GS2SU3 | 600, 3 | 200 | 600 | - | 100 | 150 | 360 | 240, 3 | 50400 | 1, 6, 7e, 9 | NA
SE502462 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 600 | - | 100 | 150 | 360 | 240, 3 | 50400 | 1, 6, 7e | NA
SE502462 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C41Y | 600, 3 | 18 | 360 | 150 | 100 | 150 | 360 | 240, 3 | 50400 | 1, 6, 7e | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 312 | 125 | 100 | 150 | 360 | 240, 3 | 0 | 1, 6, 7e | NA
SE502462 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 312 | 125 | 100 | 150 | 360 | 240, 3 | 50400 | 1, 6, 7e | NA
SE502463 | E40610 | 12.20 | A | FDS | Telemecanique | GS2QU3 | 600, 3 | 200 | 400 | - | 100 | 150 | 180 | 480, 3 | 28800 | 1, 6, 7d, 9 | NA
SE502463 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 300 | - | 100 | 150 | 180 | 480, 3 | 28800 | 1, 6, 7d | NA
SE502463 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C21Y | 600, 3 | 10 | 180 | 150 | 100 | 150 | 180 | 480, 3 | 28800 | 1, 6, 7d | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F225 (Optional) | 600, 3 | 10 | 180 | 150 | 100 | 150 | 180 | 480, 3 | 0 | 1, 6, 7d | NA
SE502463 |  |  |  | (SHORT) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 124 | 100 | 100 | 150 | 180 | 480, 3 | 28800 | 1, 6, 7d | NA
SE502464 | E40610 | 12.20 | A | FDS | Telemecanique | GS2QU3 | 600, 3 | 200 | 400 | - | 100 | 150 | 144 | 600, 3 | 8778 | 1, 6, 7c, 9 | NA
SE502464 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 250 | - | 100 | 150 | 144 | 600, 3 | 6468 | 1, 6, 7c | NA
SE502464 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C17Y | 600, 3 | 10 | 144 | 150 | 100 | 150 | 144 | 600, 3 | 6468 | 1, 6, 7c | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 144 | 150 | 100 | 150 | 144 | 600, 3 | 0 | 1, 6, 7c | NA
SE502464 |  |  |  | (SHORT) MC | Telemecanique | LC1D115 (Optional) | 600, 3 | 10 | 99 | 100 | 100 | 150 | 144 | 600, 3 | 6468 | 1, 6, 7c | NA
SE502465 | E40610 | 12.20 | A | FDS | Telemecanique | GS2QU3 | 600, 3 | 200 | 400 | - | 100 | 200 | 240 | 480, 3 | 28800 | 1, 6, 7h, 9 | NA
SE502465 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 400 | - | 100 | 200 | 240 | 480, 3 | 28800 | 1, 6, 7h | NA
SE502465 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C25Y | 600, 3 | 18 | 240 | 200 | 100 | 200 | 240 | 480, 3 | 28800 | 1, 6, 7h | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F265 (Optional) | 600, 3 | 10 | 180 | 150 | 100 | 200 | 240 | 480, 3 | 0 | 1, 6, 7h | NA
SE502465 |  |  |  | (SHORT) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 156 | 125 | 100 | 200 | 240 | 480, 3 | 28800 | 1, 6, 7h | NA
SE502466 | E40610 | 12.20 | A | FDS | Telemecanique | GS2QU3 | 600, 3 | 200 | 400 | - | 100 | 200 | 192 | 600, 3 | 28800 | 1, 6, 7d, 9 | NA
SE502466 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 350 | - | 100 | 200 | 192 | 600, 3 | 28800 | 1, 6, 7d | NA
SE502466 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C21Y | 600, 3 | 10 | 192 | 200 | 100 | 200 | 192 | 600, 3 | 28800 | 1, 6, 7d | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F225 (Optional) | 600, 3 | 10 | 192 | 200 | 100 | 200 | 192 | 600, 3 | 0 | 1, 6, 7d | NA
SE502466 |  |  |  | (SHORT) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 125 | 125 | 100 | 200 | 192 | 600, 3 | 28800 | 1, 6, 7d | NA
SE502467 | E40610 | 12.20 | A | FDS | Telemecanique | GS2SU3 | 600, 3 | 200 | 600 | - | 100 | 250 | 302 | 480, 3 | 28800 | 1, 6, 7s, 9 | NA
SE502467 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 500 | - | 100 | 250 | 302 | 480, 3 | 28800 | 1, 6, 7s | NA
SE502467 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C32Y | 600, 3 | 18 | 302 | 250 | 100 | 250 | 302 | 480, 3 | 28800 | 1, 6, 7s | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 240 | 200 | 100 | 250 | 302 | 480, 3 | 0 | 1, 6, 7s | NA
SE502467 |  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 240 | 200 | 100 | 250 | 302 | 480, 3 | 28800 | 1, 6, 7s | NA
SE502468 | E40610 | 12.20 | A | FDS | Telemecanique | GS2QU3 | 600, 3 | 200 | 400 | - | 100 | 250 | 242 | 600, 3 | 28800 | 1, 6, 7h, 9 | NA
SE502468 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 400 | - | 100 | 250 | 242 | 600, 3 | 28800 | 1, 6, 7h | NA
SE502468 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C25Y | 600, 3 | 18 | 242 | 250 | 100 | 250 | 242 | 600, 3 | 28800 | 1, 6, 7h | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F265 (Optional) | 600, 3 | 10 | 161 | 175 | 100 | 250 | 242 | 600, 3 | 0 | 1, 6, 7h | NA
SE502468 |  |  |  | (SHORT) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 144 | 150 | 100 | 250 | 242 | 600, 3 | 28800 | 1, 6, 7h | NA
SE502469 | E40610 | 12.20 | A | FDS | Telemecanique | GS2SU3 | 600, 3 | 200 | 600 | - | 100 | 300 | 361 | 480, 3 | 50400 | 1, 6, 7e, 9 | NA
SE502469 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 600 | - | 100 | 300 | 361 | 480, 3 | 50400 | 1, 6, 7e | NA
SE502469 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C41Y | 600, 3 | 18 | 361 | 300 | 100 | 300 | 361 | 480, 3 | 50400 | 1, 6, 7e | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 302 | 250 | 100 | 300 | 361 | 480, 3 | 0 | 1, 6, 7e | NA
SE502469 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 302 | 250 | 100 | 300 | 361 | 480, 3 | 50400 | 1, 6, 7e | NA
SE502470 | E40610 | 12.20 | A | FDS | Telemecanique | GS2SU3 | 600, 3 | 200 | 600 | - | 100 | 300 | 289 | 600, 3 | 28800 | 1, 6, 7s, 9 | NA
SE502470 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 500 | - | 100 | 300 | 289 | 600, 3 | 28800 | 1, 6, 7s | NA
SE502470 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C32Y | 600, 3 | 18 | 289 | 300 | 100 | 300 | 289 | 600, 3 | 28800 | 1, 6, 7s | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 242 | 250 | 100 | 300 | 289 | 600, 3 | 0 | 1, 6, 7s | NA
SE502470 |  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 242 | 250 | 100 | 300 | 289 | 600, 3 | 28800 | 1, 6, 7s | NA
SE502471 | E40610 | 12.20 | A | FDS | Telemecanique | GS2SU3 | 600, 3 | 200 | 600 | - | 100 | 350 | 336 | 600, 3 | 50400 | 1, 6, 7i, 9 | NA
SE502471 |  |  |  | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 200 | 600 | - | 100 | 350 | 336 | 600, 3 | 50400 | 1, 6, 7i | NA
SE502471 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C41Y | 600, 3 | 18 | 336 | 350 | 100 | 350 | 336 | 600, 3 | 50400 | 1, 6, 7i | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 242 | 250 | 100 | 350 | 336 | 600, 3 | 0 | 1, 6, 7i | NA
SE502471 |  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 242 | 250 | 100 | 350 | 336 | 600, 3 | 50400 | 1, 6, 7i | NA
SE502472 | E40610 | 12.20 | A | FDS | Telemecanique | GS2TU3 | 600, 3 | 200 | 800 | - | 100 | 150 | 396 | 208, 3 | 50400 | 1, 6, 7e, 9 | NA
SE502472 |  |  |  | F | Any Listed Mfgr. | Any Class L Fuse Rated: | 600 | 200 | 700 | - | 100 | 150 | 396 | 208, 3 | 50400 | 1, 6, 7e | NA
SE502472 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C48Y | 600, 3 | 18 | 396 | 150 | 100 | 150 | 396 | 208, 3 | 50400 | 1, 6, 7e | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 396 | 150 | 100 | 150 | 396 | 208, 3 | 0 | 1, 6, 7e | NA
SE502472 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 273 | 100 | 100 | 150 | 396 | 208, 3 | 50400 | 1, 6, 7e | NA
SE502473 | E40610 | 12.20 | A | FDS | Telemecanique | GS2TU3 | 600, 3 | 200 | 800 | - | 100 | 200 | 480 | 240, 3 | 50400 | 1, 6, 7r, 9 | NA
SE502473 |  |  |  | F | Any Listed Mfgr. | Any Class L Fuse Rated: | 600 | 200 | 800 | - | 100 | 200 | 480 | 240, 3 | 50400 | 1, 6, 7r | NA
SE502473 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C59Y | 600, 3 | 30 | 480 | 200 | 100 | 200 | 480 | 240, 3 | 50400 | 1, 6, 7r | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 722 | 300 | 100 | 200 | 480 | 240, 3 | 0 | 1, 6, 7r | NA
SE502473 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 480 | 200 | 100 | 200 | 480 | 240, 3 | 50400 | 1, 6, 7r | NA
SE502474 | E40610 | 12.20 | A | FDS | Telemecanique | GS2TU3 | 600, 3 | 200 | 800 | - | 100 | 350 | 414 | 480, 3 | 50400 | 1, 6, 7f, 9 | NA
SE502474 |  |  |  | F | Any Listed Mfgr. | Any Class L Fuse Rated: | 600 | 200 | 700 | - | 100 | 350 | 414 | 480, 3 | 50400 | 1, 6, 7f | NA
SE502474 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C48Y | 600, 3 | 18 | 414 | 350 | 100 | 350 | 414 | 480, 3 | 50400 | 1, 6, 7f | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 477 | 400 | 100 | 350 | 414 | 480, 3 | 0 | 1, 6, 7f | NA
SE502474 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 302 | 250 | 100 | 350 | 414 | 480, 3 | 50400 | 1, 6, 7f | NA
SE502475 | E40610 | 12.20 | A | FDS | Telemecanique | GS2TU3 | 600, 3 | 200 | 800 | - | 100 | 400 | 477 | 480, 3 | 50400 | 1, 6, 7r, 9 | NA
SE502475 |  |  |  | F | Any Listed Mfgr. | Any Class L Fuse Rated: | 600 | 200 | 800 | - | 100 | 400 | 477 | 480, 3 | 50400 | 1, 6, 7r | NA
SE502475 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C59Y | 600, 3 | 30 | 477 | 400 | 100 | 400 | 477 | 480, 3 | 50400 | 1, 6, 7r | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 722 FLA / 4400 LRA | 600 | 100 | 400 | 477 | 480, 3 | 0 | 1, 6, 7r | NA
SE502475 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 477 | 400 | 100 | 400 | 477 | 480, 3 | 50400 | 1, 6, 7r | NA
SE502476 | E40610 | 12.20 | A | FDS | Telemecanique | GS2TU3 | 600, 3 | 200 | 800 | - | 100 | 400 | 382 | 600, 3 | 50400 | 1, 6, 7e, 9 | NA
SE502476 |  |  |  | F | Any Listed Mfgr. | Any Class L Fuse Rated: | 600 | 200 | 700 | - | 100 | 400 | 382 | 600, 3 | 50400 | 1, 6, 7f | NA
SE502476 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C48Y | 600, 3 | 18 | 382 | 400 | 100 | 400 | 382 | 600, 3 | 50400 | 1, 6, 7f | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 472 | 500 | 100 | 400 | 382 | 600, 3 | 0 | 1, 6, 7f | NA
SE502476 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 289 | 300 | 100 | 400 | 382 | 600, 3 | 50400 | 1, 6, 7f | NA
SE502477 | E40610 | 12.20 | A | FDS | Telemecanique | GS2TU3 | 600, 3 | 200 | 800 | - | 100 | 500 | 472 | 600, 3 | 50400 | 1, 6, 7q, 9 | NA
SE502477 |  |  |  | F | Any Listed Mfgr. | Any Class L Fuse Rated: | 600 | 200 | 800 | - | 100 | 500 | 472 | 600, 3 | 50400 | 1, 6, 7q | NA
SE502477 |  |  |  | STR | Schneider Toshiba Inverter Europe | ATS48C59Y | 600, 3 | 30 | 472 | 500 | 100 | 500 | 472 | 600, 3 | 50400 | 1, 6, 7q | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 472 | 500 | 100 | 500 | 472 | 600, 3 | 0 | 1, 6, 7q | NA
SE502477 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 472 | 500 | 100 | 500 | 472 | 600, 3 | 50400 | 1, 6, 7q | NA

## ATS48_Disconnect
Issued: 2011-04-15
Last Revised: 2013-10-25
| Listed Combination Motor Controller Information |  |  | Component Description | [6 empty] | Combination Motor Controller Ratings
Database Identification Number | UL File Number | Volume / Section (Vol#).(Sec#) | Construction Type | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, ph | SCCR, kA | Full Load Current, A | Hp | Short Circuit Current Rating, kA | Horsepower Rating | Current Rating, FLA or FLA/LRA | Voltage and Number of Phases | Enclosure Volume, cubic inches | Conditions of Use | Schematic
SE158000 | E40610 | 12.20 | C | CB | Square D | MJL36600 | 600, 3 | 25 | 600 | - | 65 | 125 | 343 | 208, 3 | 50400 | 1, 6, 7i | NA
|  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 10.6 | 208, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 10.6 | 208, 3 | 4620 | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 330 | 250 | 100 |  | 10.6 | 208, 3 | 4620 | 1, 6, 7a | NA
SE158001 | E40610 | 12.20 | C | CB | Square D | MGL36600 | 600, 3 | 18 | 600 | - | 35 | 125 | 343 | 208, 3 | 50400 | 1, 6, 7i | NA
|  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 330 | 250 | 100 |  | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
SE158002 | E40610 | 12.20 | C | CB | Square D | PLL34060 | 480, 3 | 100 | 600 | - | 100 | 125 | 343 | 208, 3 | 50400 | 1, 6, 7i | NA
SE158002 |  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
SE158002 |  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 330 | 250 | 100 |  | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
SE158003 | E40610 | 12.20 | C | CB | Square D | PKL36060 | 600, 3 | 50 | 600 | - | 50 | 125 | 343 | 208, 3 | 50400 | 1, 6, 7i | NA
SE158003 |  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
SE158003 |  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 330 | 250 | 100 |  | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
SE158004 | E40610 | 12.20 | C | CB | Square D | PJL36060 | 600, 3 | 25 | 600 | - | 65 | 125 | 343 | 208, 3 | 50400 | 1, 6, 7i | NA
SE158004 |  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
SE158004 |  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 330 | 250 | 100 |  | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
SE158005 | E40610 | 12.20 | C | CB | Square D | PGL36060 | 600, 3 | 18 | 600 | - | 35 | 125 | 343 | 208, 3 | 50400 | 1, 6, 7i | NA
SE158005 |  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
SE158005 |  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 330 | 250 | 100 |  | 10.6 | 208, 3 | 0 | 1, 6, 7a | NA
SE158006 | E40610 | 12.20 | C | CB | Square D | MJL36600 | 600, 3 | 25 | 600 | - | 65 | 150 | 396 | 208, 3 | 50400 | 1, 6, 7e | NA
SE158006 |  |  |  | STR | Telemecanique | ATS48C48Y | 600, 3 | 18 | 480 | 400 | 100 |  | 28 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 28 | 208, 3 | 0 | 1, 6, 7a | NA
SE158006 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 28 | 208, 3 | 0 | 1, 6, 7a | NA
SE158007 | E40610 | 12.20 | C | CB | Square D | MGL36600 | 600, 3 | 18 | 600 | - | 35 | 150 | 396 | 208, 3 | 50400 | 1, 6, 7e | NA
SE158007 |  |  |  | STR | Telemecanique | ATS48C48Y | 600, 3 | 18 | 480 | 400 | 100 |  | 28 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 28 | 208, 3 | 0 | 1, 6, 7a | NA
SE158007 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 28 | 208, 3 | 0 | 1, 6, 7a | NA
SE158008 | E40610 | 12.20 | C | CB | Square D | PLL34060 | 480, 3 | 100 | 600 | - | 100 | 150 | 396 | 208, 3 | 50400 | 1, 6, 7e | NA
SE158008 |  |  |  | STR | Telemecanique | ATS48C48Y | 600, 3 | 18 | 480 | 400 | 100 |  | 28 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 28 | 208, 3 | 0 | 1, 6, 7a | NA
SE158008 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 28 | 208, 3 | 0 | 1, 6, 7a | NA
SE158009 | E40610 | 12.20 | C | CB | Square D | PKL36060 | 600, 3 | 50 | 600 | - | 50 | 150 | 396 | 208, 3 | 50400 | 1, 6, 7e | NA
SE158009 |  |  |  | STR | Telemecanique | ATS48C48Y | 600, 3 | 18 | 480 | 400 | 100 |  | 28 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 28 | 208, 3 | 0 | 1, 6, 7a | NA
SE158009 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 28 | 208, 3 | 0 | 1, 6, 7a | NA
SE158010 | E40610 | 12.20 | C | CB | Square D | PJL36060 | 600, 3 | 25 | 600 | - | 65 | 150 | 396 | 208, 3 | 50400 | 1, 6, 7e | NA
SE158010 |  |  |  | STR | Telemecanique | ATS48C48Y | 600, 3 | 18 | 480 | 400 | 100 |  | 28 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 28 | 208, 3 | 0 | 1, 6, 7a | NA
SE158010 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 28 | 208, 3 | 0 | 1, 6, 7a | NA
SE158011 | E40610 | 12.20 | C | CB | Square D | PGL36060 | 600, 3 | 18 | 600 | - | 35 | 150 | 396 | 208, 3 | 50400 | 1, 6, 7e | NA
SE158011 |  |  |  | STR | Telemecanique | ATS48C48Y | 600, 3 | 18 | 480 | 400 | 100 |  | 28 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 28 | 208, 3 | 0 | 1, 6, 7a | NA
SE158011 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 28 | 208, 3 | 0 | 1, 6, 7a | NA
SE158012 | E40610 | 12.20 | C | CB | Square D | MJL36800 | 600, 3 | 25 | 800 | - | 65 | 200 | 528 | 208, 3 | 50400 | 1, 6, 7q | NA
SE158012 |  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
SE158012 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
SE158013 | E40610 | 12.20 | C | CB | Square D | MGL36800 | 600, 3 | 18 | 800 | - | 35 | 200 | 528 | 208, 3 | 50400 | 1, 6, 7q | NA
SE158013 |  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
SE158013 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
SE158014 | E40610 | 12.20 | C | CB | Square D | PLL34080 | 480, 3 | 100 | 800 | - | 100 | 200 | 528 | 208, 3 | 50400 | 1, 6, 7q | NA
SE158014 |  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
SE158014 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
SE158015 | E40610 | 12.20 | C | CB | Square D | PKL36080 | 600, 3 | 50 | 800 | - | 50 | 200 | 528 | 208, 3 | 50400 | 1, 6, 7q | NA
SE158015 |  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
SE158015 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
SE158016 | E40610 | 12.20 | C | CB | Square D | PJL36080 | 600, 3 | 25 | 800 | - | 65 | 200 | 528 | 208, 3 | 50400 | 1, 6, 7q | NA
SE158016 |  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
SE158016 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
SE158017 | E40610 | 12.20 | C | CB | Square D | PGL36080 | 600, 3 | 18 | 800 | - | 35 | 200 | 528 | 208, 3 | 50400 | 1, 6, 7q | NA
SE158017 |  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
SE158017 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
SE158018 | E40610 | 12.20 | C | CB | Square D | MJL36600 | 600, 3 | 25 | 600 | - | 65 | 150 | 360 | 240, 3 | 50400 | 1, 6, 7e | NA
SE158018 |  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 34 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 34 | 240, 3 | 0 | 1, 6, 7a | NA
SE158018 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 34 | 240, 3 | 0 | 1, 6, 7a | NA
SE158019 | E40610 | 12.20 | C | CB | Square D | MGL36600 | 600, 3 | 18 | 600 | - | 35 | 150 | 360 | 240, 3 | 50400 | 1, 6, 7e | NA
SE158019 |  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 34 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 34 | 240, 3 | 0 | 1, 6, 7a | NA
SE158019 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 34 | 240, 3 | 0 | 1, 6, 7a | NA
SE158020 | E40610 | 12.20 | C | CB | Square D | PLL34060 | 480, 3 | 100 | 600 | - | 100 | 150 | 360 | 240, 3 | 50400 | 1, 6, 7e | NA
SE158020 |  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 34 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 34 | 240, 3 | 0 | 1, 6, 7a | NA
SE158020 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 34 | 240, 3 | 0 | 1, 6, 7a | NA
SE158021 | E40610 | 12.20 | C | CB | Square D | PKL36060 | 600, 3 | 50 | 600 | - | 50 | 150 | 360 | 240, 3 | 50400 | 1, 6, 7e | NA
SE158021 |  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 34 |  | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 34 |  | 0 | 1, 6, 7a | NA
SE158021 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 34 |  | 0 | 1, 6, 7a | NA
SE158022 | E40610 | 12.20 | C | CB | Square D | PJL36060 | 600, 3 | 25 | 600 | - | 65 | 150 | 360 | 240, 3 | 50400 | 1, 6, 7e | NA
SE158022 |  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 34 |  | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 34 |  | 0 | 1, 6, 7a | NA
SE158022 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 34 |  | 0 | 1, 6, 7a | NA
SE158023 | E40610 | 12.20 | C | CB | Square D | PGL36060 | 600, 3 | 18 | 600 | - | 35 | 150 | 360 | 240, 3 | 50400 | 1, 6, 7e | NA
SE158023 |  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 34 |  | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 34 |  | 0 | 1, 6, 7a | NA
SE158023 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 34 |  | 0 | 1, 6, 7a | NA
SE158024 | E40610 | 12.20 | C | CB | Square D | MJL36800 | 600, 3 | 25 | 800 | - | 65 | 200 | 480 | 240, 3 | 50400 | 1, 6, 7r | NA
SE158024 |  |  |  | STR | Telemecanique | ATS48C59Y | 600, 3 | 30 | 590 | 500 | 100 |  | 114 | 240, 3 | 0 | 1, 6, 7n | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 114 | 240, 3 | 0 | 1, 6, 7n | NA
SE158024 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 114 | 240, 3 | 0 | 1, 6, 7n | NA
SE158025 | E40610 | 12.20 | C | CB | Square D | MGL36800 | 600, 3 | 18 | 800 | - | 35 | 200 | 480 | 240, 3 | 50400 | 1, 6, 7r | NA
SE158025 |  |  |  | STR | Telemecanique | ATS48C59Y | 600, 3 | 30 | 590 | 500 | 100 |  | 114 | 240, 3 | 0 | 1, 6, 7n | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 114 | 240, 3 | 0 | 1, 6, 7n | NA
SE158025 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 114 | 240, 3 | 0 | 1, 6, 7n | NA
SE158026 | E40610 | 12.20 | C | CB | Square D | PLL34080 | 480, 3 | 100 | 800 | - | 100 | 200 | 480 | 240, 3 | 50400 | 1, 6, 7r | NA
SE158026 |  |  |  | STR | Telemecanique | ATS48C59Y | 600, 3 | 30 | 590 | 500 | 100 |  | 114 | 240, 3 | 0 | 1, 6, 7n | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 114 | 240, 3 | 0 | 1, 6, 7n | NA
SE158026 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 114 | 240, 3 | 0 | 1, 6, 7n | NA
SE158027 | E40610 | 12.20 | C | CB | Square D | PKL36080 | 600, 3 | 50 | 800 | - | 50 | 200 | 480 | 240, 3 | 50400 | 1, 6, 7r | NA
SE158027 |  |  |  | STR | Telemecanique | ATS48C59Y | 600, 3 | 30 | 590 | 500 | 100 |  | 114 |  | 0 | 1, 6, 7n | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 114 |  | 0 | 1, 6, 7n | NA
SE158027 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 114 |  | 0 | 1, 6, 7n | NA
SE158028 | E40610 | 12.20 | C | CB | Square D | PJL36080 | 600, 3 | 25 | 800 | - | 65 | 200 | 480 | 240, 3 | 50400 | 1, 6, 7r | NA
SE158028 |  |  |  | STR | Telemecanique | ATS48C59Y | 600, 3 | 30 | 590 | 500 | 100 |  | 114 |  | 0 | 1, 6, 7n | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 114 |  | 0 | 1, 6, 7n | NA
SE158028 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 114 |  | 0 | 1, 6, 7n | NA
SE158029 | E40610 | 12.20 | C | CB | Square D | PGL36080 | 600, 3 | 18 | 800 | - | 35 | 200 | 480 | 240, 3 | 50400 | 1, 6, 7r | NA
SE158029 |  |  |  | STR | Telemecanique | ATS48C59Y | 600, 3 | 30 | 590 | 500 | 100 |  | 114 |  | 0 | 1, 6, 7n | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 114 |  | 0 | 1, 6, 7n | NA
SE158029 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 114 |  | 0 | 1, 6, 7n | NA
SE158030 | E40610 | 12.20 | C | CB | Square D | PLL34100 | 480, 3 | 100 | 1000 | - | 100 | 250 | 604 | 240, 3 | 50400 | 1, 6, 7q | NA
SE158030 |  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  | 65 | 240, 3 | 0 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 65 | 240, 3 | 0 | 1, 6, 7b | NA
SE158030 |  |  |  | (SHORT) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 65 | 240, 3 | 0 | 1, 6, 7b | NA
SE158031 | E40610 | 12.20 | C | CB | Square D | PKL36100 | 600, 3 | 50 | 1000 | - | 50 | 250 | 604 | 240, 3 | 50400 | 1, 6, 7q | NA
SE158031 |  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  | 65 | 240, 3 | 0 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 65 | 240, 3 | 0 | 1, 6, 7b | NA
SE158031 |  |  |  | (SHORT) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 65 | 240, 3 | 0 | 1, 6, 7b | NA
SE158032 | E40610 | 12.20 | C | CB | Square D | PJL36100 | 600, 3 | 25 | 1000 | - | 65 | 250 | 604 | 240, 3 | 50400 | 1, 6, 7q | NA
SE158032 |  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  | 65 | 240, 3 | 0 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 65 | 240, 3 | 0 | 1, 6, 7b | NA
SE158032 |  |  |  | (SHORT) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 65 | 240, 3 | 0 | 1, 6, 7b | NA
SE158033 | E40610 | 12.20 | C | CB | Square D | PGL36100 | 600, 3 | 18 | 1000 | - | 35 | 250 | 604 | 240, 3 | 50400 | 1, 6, 7q | NA
SE158033 |  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  | 65 |  | 0 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 65 |  | 0 | 1, 6, 7b | NA
SE158033 |  |  |  | (SHORT) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 65 |  | 0 | 1, 6, 7b | NA
SE158034 | E40610 | 12.20 | C | CB | Square D | MJL36600 | 600, 3 | 25 | 600 | - | 65 | 300 | 361 | 480, 3 | 50400 | 1, 6, 7e | NA
SE158034 |  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 65 |  | 0 | 1, 6, 7L | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 65 |  | 0 | 1, 6, 7L | NA
SE158034 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 65 |  | 0 | 1, 6, 7L | NA
SE158035 | E40610 | 12.20 | C | CB | Square D | MGL36600 | 600, 3 | 18 | 600 | - | 35 | 300 | 361 | 480, 3 | 50400 | 1, 6, 7e | NA
SE158035 |  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 65 |  | 0 | 1, 6, 7L | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 65 |  | 0 | 1, 6, 7L | NA
SE158035 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 65 |  | 0 | 1, 6, 7L | NA
SE158036 | E40610 | 12.20 | C | CB | Square D | PLL34060 | 480, 3 | 100 | 600 | - | 100 | 300 | 361 | 480, 3 | 50400 | 1, 6, 7e | NA
SE158036 |  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 65 |  | 0 | 1, 6, 7L | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 65 |  | 0 | 1, 6, 7L | NA
SE158036 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 65 |  | 0 | 1, 6, 7L | NA
SE158037 | E40610 | 12.20 | C | CB | Square D | PKL36060 | 600, 3 | 50 | 600 | - | 50 | 300 | 361 | 480, 3 | 50400 | 1, 6, 7e | NA
SE158037 |  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 65 |  | 0 | 1, 6, 7L | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 65 |  | 0 | 1, 6, 7L | NA
SE158037 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 65 |  | 0 | 1, 6, 7L | NA
SE158038 | E40610 | 12.20 | C | CB | Square D | PJL36060 | 600, 3 | 25 | 600 | - | 65 | 300 | 361 | 480, 3 | 50400 | 1, 6, 7e | NA
SE158038 |  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 65 |  | 0 | 1, 6, 7L | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 65 |  | 0 | 1, 6, 7L | NA
SE158038 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 65 |  | 0 | 1, 6, 7L | NA
SE158039 | E40610 | 12.20 | C | CB | Square D | PGL36060 | 600, 3 | 18 | 600 | - | 35 | 300 | 361 | 480, 3 | 50400 | 1, 6, 7e | NA
SE158039 |  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 65 |  | 0 | 1, 6, 7L | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 65 |  | 0 | 1, 6, 7L | NA
SE158039 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 65 |  | 0 | 1, 6, 7L | NA
SE158040 | E40610 | 12.20 | C | CB | Square D | MJL36600 | 600, 3 | 25 | 600 | - | 65 | 350 | 414 | 480, 3 | 50400 | 1, 6, 7f | NA
SE158040 |  |  |  | STR | Telemecanique | ATS48C48Y | 600, 3 | 18 | 480 | 400 | 100 |  | 248 |  | 0 | 1, 6, 7h | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 248 |  | 0 | 1, 6, 7h | NA
SE158040 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 248 |  | 0 | 1, 6, 7h | NA
SE158041 | E40610 | 12.20 | C | CB | Square D | MGL36600 | 600, 3 | 18 | 600 | - | 35 | 350 | 414 | 480, 3 | 50400 | 1, 6, 7f | NA
SE158041 |  |  |  | STR | Telemecanique | ATS48C48Y | 600, 3 | 18 | 480 | 400 | 100 |  | 248 |  | 0 | 1, 6, 7h | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 248 |  | 0 | 1, 6, 7h | NA
SE158041 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 248 |  | 0 | 1, 6, 7h | NA
SE158042 | E40610 | 12.20 | C | CB | Square D | PLL34060 | 480, 3 | 100 | 600 | - | 100 | 350 | 414 | 480, 3 | 50400 | 1, 6, 7f | NA
SE158042 |  |  |  | STR | Telemecanique | ATS48C48Y | 600, 3 | 18 | 480 | 400 | 100 |  | 248 |  | 0 | 1, 6, 7h | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 248 |  | 0 | 1, 6, 7h | NA
SE158042 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 248 |  | 0 | 1, 6, 7h | NA
SE158043 | E40610 | 12.20 | C | CB | Square D | PKL36060 | 600, 3 | 50 | 600 | - | 50 | 350 | 414 | 480, 3 | 50400 | 1, 6, 7f | NA
SE158043 |  |  |  | STR | Telemecanique | ATS48C48Y | 600, 3 | 18 | 480 | 400 | 100 |  | 248 |  | 0 | 1, 6, 7h | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 248 |  | 0 | 1, 6, 7h | NA
SE158043 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 248 |  | 0 | 1, 6, 7h | NA
SE158044 | E40610 | 12.20 | C | CB | Square D | PJL36060 | 600, 3 | 25 | 600 | - | 65 | 350 | 414 | 480, 3 | 50400 | 1, 6, 7f | NA
SE158044 |  |  |  | STR | Telemecanique | ATS48C48Y | 600, 3 | 18 | 480 | 400 | 100 |  | 248 |  | 0 | 1, 6, 7h | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 248 |  | 0 | 1, 6, 7h | NA
SE158044 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 248 |  | 0 | 1, 6, 7h | NA
SE158045 | E40610 | 12.20 | C | CB | Square D | PGL36060 | 600, 3 | 18 | 600 | - | 35 | 350 | 414 | 480, 3 | 50400 | 1, 6, 7f | NA
SE158045 |  |  |  | STR | Telemecanique | ATS48C48Y | 600, 3 | 18 | 480 | 400 | 100 |  | 248 |  | 0 | 1, 6, 7h | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 248 |  | 0 | 1, 6, 7h | NA
SE158045 |  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 248 |  | 0 | 1, 6, 7h | NA
SE158046 | E40610 | 12.20 | C | CB | Square D | MJL36800 | 600, 3 | 25 | 800 | - | 65 | 400 | 477 | 480, 3 | 50400 | 1, 6, 7r | NA
SE158046 |  |  |  | STR | Telemecanique | ATS48C59Y | 600, 3 | 30 | 590 | 500 | 100 |  |  |  | 0 | 1, 6, 7c | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  |  |  | 0 | 1, 6, 7c | NA
SE158046 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  |  |  | 0 | 1, 6, 7c | NA
SE158047 | E40610 | 12.20 | C | CB | Square D | MGL36800 | 600, 3 | 18 | 800 | - | 35 | 400 | 477 | 480, 3 | 50400 | 1, 6, 7r | NA
SE158047 |  |  |  | STR | Telemecanique | ATS48C59Y | 600, 3 | 30 | 590 | 500 | 100 |  |  |  | 0 | 1, 6, 7c | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  |  |  | 0 | 1, 6, 7c | NA
SE158047 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  |  |  | 0 | 1, 6, 7c | NA
SE158048 | E40610 | 12.20 | C | CB | Square D | PLL34080 | 480, 3 | 100 | 800 | - | 100 | 400 | 477 | 480, 3 | 50400 | 1, 6, 7r | NA
SE158048 |  |  |  | STR | Telemecanique | ATS48C59Y | 600, 3 | 30 | 590 | 500 | 100 |  | 360 |  | 0 | 1, 6, 7c | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 360 |  | 0 | 1, 6, 7c | NA
SE158048 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 360 |  | 0 | 1, 6, 7c | NA
SE158049 | E40610 | 12.20 | C | CB | Square D | PKL36080 | 600, 3 | 50 | 800 | - | 50 | 400 | 477 | 480, 3 | 50400 | 1, 6, 7r | NA
SE158049 |  |  |  | STR | Telemecanique | ATS48C59Y | 600, 3 | 30 | 590 | 500 | 100 |  | 360 |  | 0 | 1, 6, 7c | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 360 |  | 0 | 1, 6, 7c | NA
SE158049 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 360 |  | 0 | 1, 6, 7c | NA
SE158050 | E40610 | 12.20 | C | CB | Square D | PJL36080 | 600, 3 | 25 | 800 | - | 65 | 400 | 477 | 480, 3 | 50400 | 1, 6, 7r | NA
SE158050 |  |  |  | STR | Telemecanique | ATS48C59Y | 600, 3 | 30 | 590 | 500 | 100 |  | 360 |  | 0 | 1, 6, 7c | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 360 |  | 0 | 1, 6, 7c | NA
SE158050 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 360 |  | 0 | 1, 6, 7c | NA
SE158051 | E40610 | 12.20 | C | CB | Square D | PGL36080 | 600, 3 | 18 | 800 | - | 35 | 400 | 477 | 480, 3 | 50400 | 1, 6, 7r | NA
SE158051 |  |  |  | STR | Telemecanique | ATS48C59Y | 600, 3 | 30 | 590 | 500 | 100 |  | 360 |  | 0 | 1, 6, 7c | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 360 |  | 0 | 1, 6, 7c | NA
SE158051 |  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 360 |  | 0 | 1, 6, 7c | NA
SE158052 | E40610 | 12.20 | A | DS | Square D | PLL34000S60 | 480, 3 | 100 | 600 | - | 100 | 125 | 343 | 208, 3 | 50400 | 1, 6, 7i | NA
|  |  |  | FH | Any | Listed Class J Fuse Holder | 600, 3 | 200 | 600 | -
|  |  |  | F | Any | Class J Fuse | 600, 1 | 200 | 600 | - | 100 |  | 289 | 600, 3 | 0 | 1, 6, 7s | NA
|  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 289 | 600, 3 | 0 | 1, 6, 7s | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 289 | 600, 3 | 0 | 1, 6, 7s | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 330 | 250 | 100 |  | 289 | 600, 3 | 0 | 1, 6, 7s | NA
SE158053 | E40610 | 12.20 | A | DS | Square D | PJL36000S60 | 600, 3 | 25 | 600 | - | 100 | 125 | 343 | 208, 3 | 50400 | 1, 6, 7i | NA
|  |  |  | FH | Any | Listed Class J Fuse Holder | 600, 3 | 200 | 600 | -
|  |  |  | F | Any | Class J Fuse | 600, 1 | 200 | 600 | - | 100 |  | 289 | 600, 3 | 0 | 1, 6, 7s | NA
|  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 289 | 600, 3 | 0 | 1, 6, 7s | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 289 | 600, 3 | 0 | 1, 6, 7s | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 330 | 250 | 100 |  | 289 | 600, 3 | 0 | 1, 6, 7s | NA
SE158054 | E40610 | 12.20 | A | DS | Square D | PLL34000S60 | 480, 3 | 100 | 600 | - | 100 | 150 | 396 | 208, 3 | 50400 | 1, 6, 7e | NA
|  |  |  | FH | Any | Listed Class L Fuse Holder | 600, 3 | 200 | 800 | -
|  |  |  | F | Any | Class L Fuse | 600, 1 | 200 | 700 | - | 100 |  | 396 | 600, 3 | 0 | 1, 6, 7e | NA
|  |  |  | STR | Telemecanique | ATS48C48Y | 600, 3 | 18 | 480 | 400 | 100 |  | 396 | 600, 3 | 0 | 1, 6, 7e | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 396 | 600, 3 | 0 | 1, 6, 7e | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 396 | 600, 3 | 0 | 1, 6, 7e | NA
SE158055 | E40610 | 12.20 | A | DS | Square D | PJL36000S60 | 600, 3 | 25 | 600 | - | 100 | 150 | 396 | 208, 3 | 50400 | 1, 6, 7e | NA
|  |  |  | FH | Any | Listed Class L Fuse Holder | 600, 3 | 200 | 800 | -
|  |  |  | F | Any | Class L Fuse | 600, 1 | 200 | 700 | - | 100 |  | 396 | 600, 3 | 0 | 1, 6, 7e | NA
|  |  |  | STR | Telemecanique | ATS48C48Y | 600, 3 | 18 | 480 | 400 | 100 |  | 396 | 600, 3 | 0 | 1, 6, 7e | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 396 | 600, 3 | 0 | 1, 6, 7e | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 396 | 600, 3 | 0 | 1, 6, 7e | NA
SE158056 | E40610 | 12.20 | A | DS | Square D | PLL34000S80 | 480, 3 | 100 | 800 | - | 100 | 200 | 528 | 208, 3 | 50400 | 1, 6, 7q | NA
|  |  |  | FH | Any | Listed Class L Fuse Holder | 600, 3 | 200 | 1200 | -
|  |  |  | F | Any | Class L Fuse | 600, 1 | 200 | 900 | - | 100 |  | 414 | 600, 3 | 0 | 1, 6, 7f | NA
|  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  | 414 | 600, 3 | 0 | 1, 6, 7f | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 414 | 600, 3 | 0 | 1, 6, 7f | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 414 | 600, 3 | 0 | 1, 6, 7f | NA
SE158057 | E40610 | 12.20 | A | DS | Square D | PJL36000S80 | 600, 3 | 25 | 800 | - | 100 | 200 | 528 | 208, 3 | 50400 | 1, 6, 7q | NA
|  |  |  | FH | Any | Listed Class L Fuse Holder | 600, 3 | 200 | 1200 | -
|  |  |  | F | Any | Class L Fuse | 600, 1 | 200 | 900 | - | 100 |  | 414 | 600, 3 | 0 | 1, 6, 7f | NA
|  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  | 414 | 600, 3 | 0 | 1, 6, 7f | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 414 | 600, 3 | 0 | 1, 6, 7f | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 414 | 600, 3 | 0 | 1, 6, 7f | NA
SE158058 | E40610 | 12.20 | A | DS | Square D | PLL34000S60 | 480, 3 | 100 | 600 | - | 100 | 150 | 360 | 240, 3 | 50400 | 1, 6, 7e | NA
|  |  |  | FH | Any | Listed Class J Fuse Holder | 600, 3 | 200 | 600 | -
|  |  |  | F | Any | Class J Fuse | 600, 1 | 200 | 600 | - | 100 |  | 382 | 600, 3 | 0 | 1, 6, 7f | NA
|  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 382 | 600, 3 | 0 | 1, 6, 7f | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 382 | 600, 3 | 0 | 1, 6, 7f | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 382 | 600, 3 | 0 | 1, 6, 7f | NA
SE158059 | E40610 | 12.20 | A | DS | Square D | PJL36000S60 | 600, 3 | 25 | 600 | - | 100 | 150 | 360 | 240, 3 | 50400 | 1, 6, 7e | NA
|  |  |  | FH | Any | Listed Class J Fuse Holder | 600, 3 | 200 | 600 | -
|  |  |  | F | Any | Class J Fuse | 600, 1 | 200 | 600 | - | 100 |  | 472 | 600, 3 | 0 | 1, 6, 7f | NA
|  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 472 | 600, 3 | 0 | 1, 6, 7f | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 472 | 600, 3 | 0 | 1, 6, 7f | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 472 | 600, 3 | 0 | 1, 6, 7f | NA
SE158060 | E40610 | 12.20 | A | DS | Square D | PLL34000S60 | 480, 3 | 100 | 600 | - | 100 | 200 | 480 | 240, 3 | 50400 | 1, 6, 7r | NA
|  |  |  | FH | Any | Listed Class L Fuse Holder | 600, 3 | 200 | 800 | -
|  |  |  | F | Any | Class L Fuse | 600, 1 | 200 | 800 | - | 100 |  | 10.6 | 600, 3 | 0 | 1, 6, 7a | NA
|  |  |  | STR | Telemecanique | ATS48C59Y | 600, 3 | 30 | 590 | 500 | 100 |  | 10.6 | 600, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 10.6 | 600, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 10.6 | 600, 3 | 0 | 1, 6, 7a | NA
SE158061 | E40610 | 12.20 | A | DS | Square D | PJL36000S60 | 600, 3 | 25 | 600 | - | 100 | 200 | 480 | 240, 3 | 50400 | 1, 6, 7r | NA
|  |  |  | FH | Any | Listed Class L Fuse Holder | 600, 3 | 200 | 800 | -
|  |  |  | F | Any | Class L Fuse | 600, 1 | 200 | 800 | - | 100 |  | 16.7 | 600, 3 | 0 | 1, 6, 7a | NA
|  |  |  | STR | Telemecanique | ATS48C59Y | 600, 3 | 30 | 590 | 500 | 100 |  | 16.7 | 600, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 16.7 | 600, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 16.7 | 600, 3 | 0 | 1, 6, 7a | NA
SE158062 | E40610 | 12.20 | A | DS | Square D | PLL34000S80 | 480, 3 | 100 | 800 | - | 100 | 250 | 604 | 240, 3 | 50400 | 1, 6, 7q | NA
|  |  |  | FH | Any | Listed Class L Fuse Holder | 600, 3 | 200 | 1200 | -
|  |  |  | F | Any | Class L Fuse | 600, 1 | 200 | 1000 | - | 100 |  | 15.2 | 600, 3 | 0 | 1, 6, 7a | NA
|  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  | 15.2 | 600, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 15.2 | 600, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 15.2 | 600, 3 | 0 | 1, 6, 7a | NA
SE158063 | E40610 | 12.20 | A | DS | Square D | PJL36000S80 | 600, 3 | 25 | 800 | - | 100 | 250 | 604 | 240, 3 | 50400 | 1, 6, 7q | NA
|  |  |  | FH | Any | Listed Class L Fuse Holder | 600, 3 | 200 | 1200 | -
|  |  |  | F | Any | Class L Fuse | 600, 1 | 200 | 1000 | - | 100 |  | 24.2 | 600, 3 | 0 | 1, 6, 7a | NA
|  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  | 24.2 | 600, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 24.2 | 600, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 24.2 | 600, 3 | 0 | 1, 6, 7a | NA
SE158064 | E40610 | 12.20 | A | DS | Square D | PLL34000S60 | 480, 3 | 100 | 600 | - | 100 | 300 | 361 | 480, 3 | 50400 | 1, 6, 7e | NA
|  |  |  | FH | Any | Listed Class J Fuse Holder | 600, 3 | 200 | 600 | -
|  |  |  | F | Any | Class J Fuse | 600, 1 | 200 | 600 | - | 100 |  | 22 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 22 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 22 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 22 | 240, 3 | 0 | 1, 6, 7a | NA
SE158065 | E40610 | 12.20 | A | DS | Square D | PJL36000S60 | 600, 3 | 25 | 600 | - | 100 | 300 | 361 | 480, 3 | 50400 | 1, 6, 7e | NA
|  |  |  | FH | Any | Listed Class J Fuse Holder | 600, 3 | 200 | 600 | -
|  |  |  | F | Any | Class J Fuse | 600, 1 | 200 | 600 | - | 100 |  | 30.8 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 30.8 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 30.8 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 30.8 | 240, 3 | 0 | 1, 6, 7a | NA
SE158066 | E40610 | 12.20 | A | DS | Square D | PLL34000S60 | 480, 3 | 100 | 600 | - | 100 | 350 | 414 | 480, 3 | 50400 | 1, 6, 7f | NA
|  |  |  | FH | Any | Listed Class L Fuse Holder | 600, 3 | 200 | 800 | -
|  |  |  | F | Any | Class L Fuse | 600, 1 | 200 | 700 | - | 100 |  | 28 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | STR | Telemecanique | ATS48C48Y | 600, 3 | 18 | 480 | 400 | 100 |  | 28 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 28 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 28 | 240, 3 | 0 | 1, 6, 7a | NA
SE158067 | E40610 | 12.20 | A | DS | Square D | PJL36000S60 | 600, 3 | 25 | 600 | - | 100 | 350 | 414 | 480, 3 | 50400 | 1, 6, 7f | NA
|  |  |  | FH | Any | Listed Class L Fuse Holder | 600, 3 | 200 | 800 | -
|  |  |  | F | Any | Class L Fuse | 600, 1 | 200 | 700 | - | 100 |  | 14 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | STR | Telemecanique | ATS48C48Y | 600, 3 | 18 | 480 | 400 | 100 |  | 14 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 14 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 14 | 240, 3 | 0 | 1, 6, 7a | NA
SE158068 | E40610 | 12.20 | A | DS | Square D | PLL34000S60 | 480, 3 | 100 | 600 | - | 100 | 400 | 477 | 480, 3 | 50400 | 1, 6, 7r | NA
|  |  |  | FH | Any | Listed Class L Fuse Holder | 600, 3 | 200 | 800 | -
|  |  |  | F | Any | Class L Fuse | 600, 1 | 200 | 800 | - | 100 |  | 46.2 | 240, 3 | 0 | 1, 6, 7b | NA
|  |  |  | STR | Telemecanique | ATS48C59Y | 600, 3 | 30 | 590 | 500 | 100 |  | 46.2 | 240, 3 | 0 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 46.2 | 240, 3 | 0 | 1, 6, 7b | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 46.2 | 240, 3 | 0 | 1, 6, 7b | NA
SE158069 | E40610 | 12.20 | A | DS | Square D | PJL36000S60 | 600, 3 | 25 | 600 | - | 100 | 400 | 477 | 480, 3 | 50400 | 1, 6, 7r | NA
|  |  |  | FH | Any | Listed Class L Fuse Holder | 600, 3 | 200 | 800 | -
|  |  |  | F | Any | Class L Fuse | 600, 1 | 200 | 800 | - | 100 |  | 42 | 240, 3 | 0 | 1, 6, 7b | NA
|  |  |  | STR | Telemecanique | ATS48C59Y | 600, 3 | 30 | 590 | 500 | 100 |  | 42 | 240, 3 | 0 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 42 | 240, 3 | 0 | 1, 6, 7b | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 42 | 240, 3 | 0 | 1, 6, 7b | NA
SE158070 | E40610 | 12.20 | A | DS | Square D | PLL34000S80 | 480, 3 | 100 | 800 | - | 100 | 500 | 590 | 480, 3 | 50400 | 1, 6, 7q | NA
|  |  |  | FH | Any | Listed Class L Fuse Holder | 600, 3 | 200 | 1200 | -
|  |  |  | F | Any | Class L Fuse | 600, 1 | 200 | 1000 | - | 100 |  | 21 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  | 21 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 21 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 21 | 240, 3 | 0 | 1, 6, 7a | NA
SE158071 | E40610 | 12.20 | A | DS | Square D | PJL36000S80 | 600, 3 | 25 | 800 | - | 100 | 500 | 590 | 480, 3 | 50400 | 1, 6, 7q | NA
|  |  |  | FH | Any | Listed Class L Fuse Holder | 600, 3 | 200 | 1200 | -
|  |  |  | F | Any | Class L Fuse | 600, 1 | 200 | 1000 | - | 100 |  | 17 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  | 17 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 17 | 240, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 17 | 240, 3 | 0 | 1, 6, 7a | NA
SE158072 | E40610 | 12.20 | A | DS | Square D | PKL36000S60 | 600, 3 | 50 | 600 | - | 100 | 350 | 336 | 600, 3 | 50400 | 1, 6, 7i | NA
|  |  |  | FH | Any | Listed Class J Fuse Holder | 600, 3 | 200 | 600 | -
|  |  |  | F | Any | Class J Fuse | 600, 1 | 200 | 600 | - | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
|  |  |  | STR | Telemecanique | ATS48C41Y | 600, 3 | 18 | 410 | 350 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 330 | 250 | 100 |  | 59.4 | 208, 3 | 0 | 1, 6, 7b | NA
SE158073 | E40610 | 12.20 | A | DS | Square D | PKL36000S60 | 600, 3 | 50 | 600 | - | 100 | 400 | 382 | 600, 3 | 50400 | 1, 6, 7e | NA
|  |  |  | FH | Any | Listed Class L Fuse Holder | 600, 3 | 200 | 800 | -
|  |  |  | F | Any | Class L Fuse | 600, 1 | 200 | 700 | - | 100 |  | 54 | 208, 3 | 0 | 1, 6, 7b | NA
|  |  |  | STR | Telemecanique | ATS48C48Y | 600, 3 | 18 | 480 | 400 | 100 |  | 54 | 208, 3 | 0 | 1, 6, 7b | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 54 | 208, 3 | 0 | 1, 6, 7b | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F400 (Optional) | 600, 3 | 18 | 400 | 300 | 100 |  | 54 | 208, 3 | 0 | 1, 6, 7b | NA
SE158074 | E40610 | 12.20 | A | DS | Square D | PKL36000S60 | 600, 3 | 50 | 600 | - | 100 | 500 | 472 | 600, 3 | 50400 | 1, 6, 7r | NA
|  |  |  | FH | Any | Listed Class L Fuse Holder | 600, 3 | 200 | 800 | -
|  |  |  | F | Any | Class L Fuse | 600, 1 | 200 | 800 | - | 100 |  | 27 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | STR | Telemecanique | ATS48C59Y | 600, 3 | 30 | 590 | 500 | 100 |  | 27 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 27 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 27 | 208, 3 | 0 | 1, 6, 7a | NA
SE158075 | E40610 | 12.20 | A | DS | Square D | PKL36000S80 | 600, 3 | 50 | 800 | - | 65 | 600 | 578 | 600, 3 | 50400 | 1, 6, 7q | NA
|  |  |  | FH | Any | Listed Class L Fuse Holder | 600, 3 | 200 | 1200 | -
|  |  |  | F | Any | Class L Fuse | 600, 1 | 200 | 1000 | - | 100 |  | 22 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  | 22 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  | 22 | 208, 3 | 0 | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F500 (Optional) | 600, 3 | 30 | 500 | 500 | 100 |  | 22 | 208, 3 | 0 | 1, 6, 7a | NA
SE158076 | E40610 | 12.20 | C | CB | Square D | PLL34100 | 480, 3 | 100 | 1000 | - | 100 | 500 | 590 | 480, 3 | 50400 | 1, 6, 7q | NA
|  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  |  |  |  | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  |  |  |  | 1, 6, 7a | NA
SE158077 | E40610 | 12.20 | C | CB | Square D | PKL36100 | 600, 3 | 50 | 1000 | - | 50 | 500 | 590 | 480, 3 | 50400 | 1, 6, 7a | NA
|  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  |  |  |  | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  |  |  |  | 1, 6, 7q | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100
SE158078 | E40610 | 12.20 | C | CB | Square D | PJL36100 | 600, 3 | 25 | 1000 | - | 65 | 500 | 590 | 480, 3 | 50400 | 1, 6, 7a | NA
|  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100 |  |  |  |  | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  |  |  |  | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100 |  |  |  |  | 1, 6, 7a | NA
SE158079 | E40610 | 12.20 | C | CB | Square D | PGL36100 | 600, 3 | 18 | 1000 | - | 35 | 500 | 590 | 480, 3 | 50400 | 1, 6, 7q | NA
|  |  |  | STR | Telemecanique | ATS48C66Y | 600, 3 | 30 | 660 | 600 | 100
|  |  |  | (ISO) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100
|  |  |  | (SHORT) MC | Telemecanique | LC1F630 (Optional) | 600, 3 | 30 | 630 | 800 | 100
SE158080 | E40610 | 12.20 | C | CB | Square D | LLL36400 | 600, 3 | 50 | 400 | - | 100 | 60 | 169 | 208, 3 | 28800 | 1, 6, 7d | NA
|  |  |  | STR | Telemecanique | ATS48C21Y | 600, 3 | 10 | 210 | 200 | [5 empty] | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 185 | 150 | [5 empty] | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 150 | 125 | [5 empty] | 1, 6, 7a | NA
SE158081 | E40610 | 12.20 | C | CB | Square D | LLL36400 | 600, 3 | 50 | 400 | - | 100 | 75 | 211 | 208, 3 | 28800 | 1, 6, 7p | NA
|  |  |  | STR | Telemecanique | ATS48C25Y | 600, 3 | 18 | 250 | 250 | [5 empty] | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F265 (Optional) | 600, 3 | 10 | 265 | 175 | [5 empty] | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 185 | 150 | [5 empty] | 1, 6, 7a | NA
SE158082 | E40610 | 12.20 | C | CB | Square D | LLL36600 | 600, 3 | 50 | 600 | - | 100 | 100 | 273 | 208, 3 | 28800 | 1, 6, 7h | NA
|  |  |  | STR | Telemecanique | ATS48C32Y | 600, 3 | 18 | 320 | 300 | [5 empty] | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 330 | 250 | [5 empty] | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F265 (Optional) | 600, 3 | 10 | 265 | 175 | [5 empty] | 1, 6, 7a | NA
SE158083 | E40610 | 12.20 | C | CB | Square D | LLL36400 | 600, 3 | 50 | 400 | - | 100 | 75 | 192 | 240, 3 | 28800 | 1, 6, 7d | NA
|  |  |  | STR | Telemecanique | ATS48C21Y | 600, 3 | 10 | 210 | 200 | 100 |  |  | 240, 3 |  | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F265 (Optional) | 600, 3 | 10 | 265 | 175 | 100 |  |  | 240, 3 |  | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 150 | 125 | 100 |  |  | 240, 3 |  | 1, 6, 7a | NA
SE158084 | E40610 | 12.20 | C | CB | Square D | LLL36600 | 600, 3 | 50 | 600 | - | 100 | 100 | 248 | 240, 3 | 28800 | 1, 6, 7h | NA
|  |  |  | STR | Telemecanique | ATS48C25Y | 600, 3 | 18 | 250 | 250 | 100 |  |  | 240, 3 |  | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F265 (Optional) | 600, 3 | 10 | 265 | 175 | 100 |  |  | 240, 3 |  | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 185 | 150 | 100 |  |  | 240, 3 |  | 1, 6, 7a | NA
SE158085 | E40610 | 12.20 | C | CB | Square D | MJL36600 | 600, 3 | 25 | 600 | - | 65 | 125 | 312 | 240, 3 | 28800 | 1, 6, 7i | NA
|  |  |  | STR | Telemecanique | ATS48C32Y | 600, 3 | 18 | 320 | 300 | 100 |  |  | 240, 3 |  | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 330 | 250 | 100 |  |  | 240, 3 |  | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 330 | 250 | 100 |  |  | 240, 3 |  | 1, 6, 7a | NA
SE158086 | E40610 | 12.20 | C | CB | Square D | PLL34060 | 480, 3 | 100 | 600 | - | 100 | 125 | 312 | 240, 3 | 28800 | 1, 6, 7i | NA
|  |  |  | STR | Telemecanique | ATS48C32Y | 600, 3 | 18 | 320 | 300 | 100 |  |  | 240, 3 |  | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 330 | 250 | 100 |  |  | 240, 3 |  | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 330 | 250 | 100 |  |  | 240, 3 |  | 1, 6, 7a | NA
SE158087 | E40610 | 12.20 | C | CB | Square D | LLL36400 | 600, 3 | 50 | 400 | - | 100 | 150 | 180 | 480, 3 | 28800 | 1, 6, 7d | NA
|  |  |  | STR | Telemecanique | ATS48C21Y | 600, 3 | 10 | 210 | 200 | 100 |  |  | 208, 3 |  | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F265 (Optional) | 600, 3 | 10 | 265 | 175 | 100 |  |  | 208, 3 |  | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 150 | 125 | 100 |  |  | 208, 3 |  | 1, 6, 7a | NA
SE158088 | E40610 | 12.20 | C | CB | Square D | LLL36600 | 600, 3 | 50 | 600 | - | 100 | 200 | 240 | 480, 3 | 28800 | 1, 6, 7h | NA
|  |  |  | STR | Telemecanique | ATS48C25Y | 600, 3 | 18 | 250 | 250 | 100 |  |  | 208, 3 |  | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F265 (Optional) | 600, 3 | 10 | 265 | 175 | 100 |  |  | 208, 3 |  | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 185 | 150 | 100 |  |  | 208, 3 |  | 1, 6, 7a | NA
SE158089 | E40610 | 12.20 | C | CB | Square D | LLL36600 | 600, 3 | 50 | 600 | - | 100 | 250 | 302 | 480, 3 | 28800 | 1, 6, 7s | NA
|  |  |  | STR | Telemecanique | ATS48C32Y | 600, 3 | 18 | 320 | 300 | 100 |  |  | 208, 3 |  | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 330 | 250 | 100 |  |  | 208, 3 |  | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 330 | 250 | 100 |  |  | 208, 3 |  | 1, 6, 7a | NA
SE158090 | E40610 | 12.20 | C | CB | Square D | LLL36400 | 600, 3 | 50 | 400 | - | 50 | 200 | 192 | 600, 3 | 28800 | 1, 6, 7d | NA
|  |  |  | STR | Telemecanique | ATS48C21Y | 600, 3 | 10 | 210 | 200 | 100 |  |  | 208, 3 |  | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F265 (Optional) | 600, 3 | 10 | 265 | 175 | 100 |  |  | 208, 3 |  | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1D150 (Optional) | 600, 3 | 10 | 150 | 125 | 100 |  |  | 208, 3 |  | 1, 6, 7a | NA
SE158091 | E40610 | 12.20 | C | CB | Square D | LLL36600 | 600, 3 | 50 | 600 | - | 50 | 250 | 242 | 600, 3 | 28800 | 1, 6, 7h | NA
|  |  |  | STR | Telemecanique | ATS48C25Y | 600, 3 | 18 | 250 | 250 | 100 |  |  | 208, 3 |  | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F265 (Optional) | 600, 3 | 10 | 265 | 175 | 100 |  |  | 208, 3 |  | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F185 (Optional) | 600, 3 | 10 | 185 | 150 | 100 |  |  | 208, 3 |  | 1, 6, 7a | NA
SE158092 | E40610 | 12.20 | C | CB | Square D | LLL36600 | 600, 3 | 50 | 600 | - | 50 | 300 | 289 | 600, 3 | 28800 | 1, 6, 7s | NA
|  |  |  | STR | Telemecanique | ATS48C32Y | 600, 3 | 18 | 320 | 300 | 100 |  |  | 208, 3 |  | 1, 6, 7a | NA
|  |  |  | (ISO) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 330 | 250 | 100 |  |  | 208, 3 |  | 1, 6, 7a | NA
|  |  |  | (SHORT) MC | Telemecanique | LC1F330 (Optional) | 600, 3 | 18 | 330 | 250 | 100 |  |  | 208, 3 |  | 1, 6, 7a | NA

## ATS480-Type A-IEC
Issued: 2023-01-14
Last Revised: 2023-01-14
Database Identification Number | Listed Combination Motor Controller Information | [7 empty] | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | Conditions of Use | Schematic | Other References
| Listing Report Information |  |  |  |  | Enclosure or Unit Dimensions
| UL File Number | Report Issue Date YYYY-MM-DD | Volume / Section (Vol#).(Sec#) | Model Number or Product Style/ Designation | Product Description on Page/Figure/Ill. | Enclosure or Unit Height, inches | Width, inches | Depth, inches |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of phases | SCCR, kA | Full Load Current, A | HP Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | HP Rating
SE105000 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2EU3N | 600 | 3 | 100 | 30 | - | 208 | 3 | 100 | 10.6 | 3 | 4620 | 1,6,7a,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 20 | -
[10 empty] | STR | Schneider Toshiba | ATS480D17Y | 600 | 3 | 100 | 10.6 | 3
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 24.2 | 7.5
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 24.2 | 7.5
SE105001 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2EU3N | 600 | 3 | 100 | 30 | - | 208 | 3 | 100 | 16.7 | 5 | 4620 | 1,6,7a,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 30 | -
[10 empty] | STR | Schneider Toshiba | ATS480D22Y | 600 | 3 | 100 | 16.7 | 5
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 24.2 | 7.5
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 24.2 | 7.5
SE105002 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2EU3N | 600 | 3 | 100 | 30 | - | 240 | 3 | 100 | 15.2 | 5 | 4620 | 1,6,7a,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 25 | -
[10 empty] | STR | Schneider Toshiba | ATS480D17Y | 600 | 3 | 100 | 15.2 | 5
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 22 | 7.5
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 22 | 7.5
SE105003 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2GU3N | 600 | 3 | 100 | 60 | - | 208 | 3 | 100 | 24.2 | 7.5 | 4620 | 1,6,7a,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 45 | -
[10 empty] | STR | Schneider Toshiba | ATS480D32Y | 600 | 3 | 100 | 24.2 | 7.5
[10 empty] | (ISO) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 100 | 30.8 | 10
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 24.2 | 7.5
SE105004 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2GU3N | 600 | 3 | 100 | 60 | - | 240 | 3 | 100 | 22 | 7.5 | 4620 | 1,6,7a,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 40 | -
[10 empty] | STR | Schneider Toshiba | ATS480D22Y | 600 | 3 | 100 | 22 | 7.5
[10 empty] | (ISO) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 100 | 28 | 10
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 22 | 7.5
SE105005 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2GU3N | 600 | 3 | 100 | 60 | - | 208 | 3 | 100 | 30.8 | 10 | 4620 | 1,6,7a,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 50 | -
[10 empty] | STR | Schneider Toshiba | ATS480D38Y | 600 | 3 | 100 | 30.8 | 10
[10 empty] | (ISO) MC | Schneider Electric | LC1D40 (Optional) | 600 | 3 | 100 | 30.8 | 10
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 100 | 30.8 | 10
SE105006 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2GU3N | 600 | 3 | 100 | 60 | - | 240 | 3 | 100 | 28 | 10 | 4620 | 1,6,7a,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 50 | -
[10 empty] | STR | Schneider Toshiba | ATS480D32Y | 600 | 3 | 100 | 28 | 10
[10 empty] | (ISO) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 100 | 28 | 10
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 22 | 7.5
SE105007 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2EU3N | 600 | 3 | 100 | 30 | - | 480 | 3 | 100 | 14 | 10 | 4620 | 1,6,7a,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 25 | -
[10 empty] | STR | Schneider Toshiba | ATS480D17Y | 600 | 3 | 100 | 14 | 10
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 21 | 15
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 21 | 15
SE105008 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2JU3N | 600 | 3 | 200 | 100 | - | 208 | 3 | 100 | 46.2 | 15 | 4620 | 1,6,7b,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 80 | -
[10 empty] | STR | Schneider Toshiba | ATS480D62Y | 600 | 3 | 100 | 46.2 | 15
[10 empty] | (ISO) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 100 | 46.2 | 15
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 100 | 30.8 | 10
SE105009 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2JU3N | 600 | 3 | 200 | 100 | - | 240 | 3 | 100 | 42 | 15 | 4620 | 1,6,7k,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 70 | -
[10 empty] | STR | Schneider Toshiba | ATS480D47Y | 600 | 3 | 100 | 42 | 15
[10 empty] | (ISO) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 100 | 42 | 15
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 100 | 28 | 10
SE105010 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2GU3N | 600 | 3 | 100 | 60 | - | 480 | 3 | 100 | 21 | 15 | 4620 | 1,6,7a,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 35 | -
[10 empty] | STR | Schneider Toshiba | ATS480D22Y | 600 | 3 | 100 | 21 | 15
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 21 | 15
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 21 | 15
SE105011 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2EU3N | 600 | 3 | 100 | 30 | - | 600 | 3 | 100 | 17 | 15 | 4620 | 1,6,7a,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 30 | -
[10 empty] | STR | Schneider Toshiba | ATS480D17Y | 600 | 3 | 100 | 17 | 15
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 22 | 20
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 22 | 20
SE105012 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2JU3N | 600 | 3 | 200 | 100 | - | 208 | 3 | 100 | 59.4 | 20 | 4620 | 1,6,7b,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 100 | -
[10 empty] | STR | Schneider Toshiba | ATS480D75Y | 600 | 3 | 100 | 59.4 | 20
[10 empty] | (ISO) MC | Schneider Electric | LC1D65 (Optional) | 600 | 3 | 100 | 59.4 | 20
[10 empty] | (SHORT) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 100 | 46.2 | 15
SE105013 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2JU3N | 600 | 3 | 200 | 100 | - | 240 | 3 | 100 | 54 | 20 | 4620 | 1,6,7b,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 90 | -
[10 empty] | STR | Schneider Toshiba | ATS480D62Y | 600 | 3 | 100 | 54 | 20
[10 empty] | (ISO) MC | Schneider Electric | LC1D65 (Optional) | 600 | 3 | 100 | 54 | 20
[10 empty] | (SHORT) MC | Schneider Electric | LC1D40 (Optional) | 600 | 3 | 100 | 28 | 10
SE105014 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2GU3N | 600 | 3 | 100 | 60 | - | 480 | 3 | 100 | 27 | 20 | 4620 | 1,6,7a,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 45 | -
[10 empty] | STR | Schneider Toshiba | ATS480D32Y | 600 | 3 | 100 | 27 | 20
[10 empty] | (ISO) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 100 | 27 | 20
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 21 | 15
SE105015 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2GU3N | 600 | 3 | 100 | 60 | - | 600 | 3 | 100 | 22 | 20 | 4620 | 1,6,7a,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 40 | -
[10 empty] | STR | Schneider Toshiba | ATS480D22Y | 600 | 3 | 100 | 22 | 20
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 22 | 20
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 22 | 20
SE105016 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2MU3N | 600 | 3 | 200 | 200 | - | 208 | 3 | 100 | 74.8 | 25 | 4620 | 1,6,7l,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 125 | -
[10 empty] | STR | Schneider Toshiba | ATS480D88Y | 600 | 3 | 100 | 74.8 | 25
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 88 | 30
[10 empty] | (SHORT) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 5 | 46.2 | 15
SE105017 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2MU3N | 600 | 3 | 200 | 200 | - | 240 | 3 | 100 | 68 | 25 | 4620 | 1,6,7b,8,9,10 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 125 | -
[10 empty] | STR | Schneider Toshiba | ATS480D75Y | 600 | 3 | 100 | 68 | 25
[10 empty] | (ISO) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 100 | 80 | 30
[10 empty] | (SHORT) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 5 | 42 | 15
SE105018 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2GU3N | 600 | 3 | 100 | 60 | - | 480 | 3 | 100 | 34 | 25 | 4620 | 1,6,7a,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 60 | -
[10 empty] | STR | Schneider Toshiba | ATS480D38Y | 600 | 3 | 100 | 34 | 25
[10 empty] | (ISO) MC | Schneider Electric | LC1D40 (Optional) | 600 | 3 | 100 | 40 | 30
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 100 | 27 | 20
SE105019 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2GU3N | 600 | 3 | 100 | 60 | - | 600 | 3 | 100 | 27 | 25 | 4620 | 1,6,7a,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 45 | -
[10 empty] | STR | Schneider Toshiba | ATS480D32Y | 600 | 3 | 100 | 27 | 25
[10 empty] | (ISO) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 100 | 27 | 25
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 100 | 22 | 20
SE105020 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2MU3N | 600 | 3 | 200 | 200 | - | 208 | 3 | 100 | 88 | 30 | 4620 | 1,6,7m,8,9,10 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 150 | -
[10 empty] | STR | Schneider Toshiba | ATS480C11Y | 600 | 3 | 100 | 88 | 30
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 88 | 30
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 100 | 74.8 | 25
SE105021 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2MU3N | 600 | 3 | 200 | 200 | - | 240 | 3 | 100 | 80 | 30 | 4620 | 1,6,7l,8,9,10 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 150 | -
[10 empty] | STR | Schneider Toshiba | ATS480D88Y | 600 | 3 | 100 | 80 | 30
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 104 | 40
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 100 | 80 | 30
SE105022 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2JU3N | 600 | 3 | 200 | 100 | - | 480 | 3 | 100 | 40 | 30 | 4620 | 1,6,7k,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 70 | -
[10 empty] | STR | Schneider Toshiba | ATS480D47Y | 600 | 3 | 100 | 40 | 30
[10 empty] | (ISO) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 100 | 52 | 40
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 100 | 27 | 20
SE105023 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2GU3N | 600 | 3 | 100 | 60 | - | 600 | 3 | 100 | 32 | 30 | 4620 | 1,6,7a,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 60 | -
[10 empty] | STR | Schneider Toshiba | ATS480D38Y | 600 | 3 | 100 | 32 | 30
[10 empty] | (ISO) MC | Schneider Electric | LC1D40 (Optional) | 600 | 3 | 100 | 32 | 30
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 100 | 32 | 30
SE105024 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 42 | 14 | 11 | A | FDS | Schneider Electric | GS2MU3N | 600 | 3 | 200 | 200 | - | 208 | 3 | 100 | 114 | 40 | 6468 | 1,6,7n,8,9,10 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 200 | -
[10 empty] | STR | Schneider Toshiba | ATS480C14Y | 600 | 3 | 100 | 114 | 40
[10 empty] | (ISO) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 100 | 114 | 40
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 10 | 74.8 | 25
SE105025 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2MU3N | 600 | 3 | 200 | 200 | - | 240 | 3 | 100 | 104 | 40 | 4620 | 1,6,7m,8,9,10 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 175 | -
[10 empty] | STR | Schneider Toshiba | ATS480C11Y | 600 | 3 | 100 | 104 | 40
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 104 | 40
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 100 | 80 | 30
SE105026 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2JU3N | 600 | 3 | 200 | 100 | - | 480 | 3 | 100 | 52 | 40 | 4620 | 1,6,7b,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 90 | -
[10 empty] | STR | Schneider Toshiba | ATS480D62Y | 600 | 3 | 100 | 52 | 40
[10 empty] | (ISO) MC | Schneider Electric | LC1D65 (Optional) | 600 | 3 | 100 | 52 | 40
[10 empty] | (SHORT) MC | Schneider Electric | LC1D40 (Optional) | 600 | 3 | 100 | 40 | 30
SE105027 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2JU3N | 600 | 3 | 200 | 100 | - | 600 | 3 | 100 | 41 | 40 | 4620 | 1,6,7k,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 70 | -
[10 empty] | STR | Schneider Toshiba | ATS480D47Y | 600 | 3 | 100 | 41 | 40
[10 empty] | (ISO) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 100 | 41 | 40
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 100 | 27 | 25
SE105028 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 57 | 14 | 11 | A | FDS | Schneider Electric | GS2QU3N | 600 | 3 | 200 | 400 | - | 208 | 3 | 100 | 143 | 50 | 8778 | 1,6,7c,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 250 | -
[10 empty] | STR | Schneider Toshiba | ATS480C17Y | 600 | 3 | 100 | 143 | 50
[10 empty] | (ISO) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 100 | 143 | 50
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 88 | 30
SE105029 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 57 | 14 | 11 | A | FDS | Schneider Electric | GS2QU3N | 600 | 3 | 200 | 400 | - | 240 | 3 | 100 | 130 | 50 | 8778 | 1,6,7n,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 225 | -
[10 empty] | STR | Schneider Toshiba | ATS480C14Y | 600 | 3 | 100 | 130 | 50
[10 empty] | (ISO) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 100 | 130 | 50
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 104 | 40
SE105030 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2MU3N | 600 | 3 | 200 | 200 | - | 480 | 3 | 100 | 65 | 50 | 4620 | 1,6,7b,8,9,10 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 110 | -
[10 empty] | STR | Schneider Toshiba | ATS480D75Y | 600 | 3 | 100 | 65 | 50
[10 empty] | (ISO) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 100 | 77 | 60
[10 empty] | (SHORT) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 100 | 52 | 40
SE105031 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2JU3N | 600 | 3 | 200 | 100 | - | 600 | 3 | 100 | 52 | 50 | 4620 | 1,6,7b,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 90 | -
[10 empty] | STR | Schneider Toshiba | ATS480D62Y | 600 | 3 | 100 | 52 | 50
[10 empty] | (ISO) MC | Schneider Electric | LC1D65 (Optional) | 600 | 3 | 100 | 52 | 50
[10 empty] | (SHORT) MC | Schneider Electric | LC1D40 (Optional) | 600 | 3 | 100 | 32 | 30
SE105032 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 20 | 20 | A | FDS | Schneider Electric | GS2QU3N | 600 | 3 | 200 | 400 | - | 208 | 3 | 100 | 169 | 60 | 28800 | 1,6,7d,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 300 | -
[10 empty] | STR | Schneider Toshiba | ATS480C21Y | 600 | 3 | 100 | 169 | 60
[10 empty] | (ISO) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 100 | 143 | 50
[10 empty] | (SHORT) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 100 | 114 | 40
SE105033 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 57 | 14 | 11 | A | FDS | Schneider Electric | GS2QU3N | 600 | 3 | 200 | 400 | - | 240 | 3 | 100 | 154 | 60 | 8778 | 1,6,7c,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 250 | -
[10 empty] | STR | Schneider Toshiba | ATS480C17Y | 600 | 3 | 100 | 154 | 60
[10 empty] | (ISO) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 100 | 154 | 60
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 104 | 40
SE105034 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2MU3N | 600 | 3 | 200 | 200 | - | 480 | 3 | 100 | 77 | 60 | 4620 | 1,6,7l,8,9,10 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 125 | -
[10 empty] | STR | Schneider Toshiba | ATS480D88Y | 600 | 3 | 100 | 77 | 60
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 96 | 75
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 100 | 77 | 60
SE105035 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2MU3N | 600 | 3 | 200 | 200 | - | 600 | 3 | 100 | 62 | 60 | 4620 | 1,6,7b,8,9,10 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 110 | -
[10 empty] | STR | Schneider Toshiba | ATS480D75Y | 600 | 3 | 100 | 62 | 60
[10 empty] | (ISO) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 100 | 62 | 60
[10 empty] | (SHORT) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 100 | 41 | 40
SE105036 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 20 | 20 | A | FDS | Schneider Electric | GS2QU3N | 600 | 3 | 200 | 400 | - | 208 | 3 | 100 | 211 | 75 | 28800 | 1,6,7p,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 350 | -
[10 empty] | STR | Schneider Toshiba | ATS480C25Y | 600 | 3 | 100 | 211 | 75
[10 empty] | (ISO) MC | Schneider Electric | LC1F225 (Optional) | 600 | 3 | 10 | 169 | 60
[10 empty] | (SHORT) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 100 | 143 | 50
SE105037 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 20 | 20 | A | FDS | Schneider Electric | GS2QU3N | 600 | 3 | 200 | 400 | - | 240 | 3 | 100 | 192 | 75 | 28800 | 1,6,7d,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 350 | -
[10 empty] | STR | Schneider Toshiba | ATS480C21Y | 600 | 3 | 100 | 192 | 75
[10 empty] | (ISO) MC | Schneider Electric | LC1F225 (Optional) | 600 | 3 | 10 | 192 | 75
[10 empty] | (SHORT) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 10 | 130 | 50
SE105038 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2MU3N | 600 | 3 | 200 | 200 | - | 480 | 3 | 100 | 96 | 75 | 4620 | 1,6,7m,8,9,10 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 175 | -
[10 empty] | STR | Schneider Toshiba | ATS480C11Y | 600 | 3 | 100 | 96 | 75
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 96 | 75
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 100 | 77 | 60
SE105039 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2MU3N | 600 | 3 | 200 | 200 | - | 600 | 3 | 100 | 77 | 75 | 4620 | 1,6,7l,8,9,10 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 125 | -
[10 empty] | STR | Schneider Toshiba | ATS480D88Y | 600 | 3 | 100 | 77 | 75
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 99 | 100
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 100 | 62 | 60
SE105040 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 20 | 20 | A | FDS | Schneider Electric | GS2SU3 | 600 | 3 | 200 | 600 | - | 208 | 3 | 100 | 273 | 100 | 28800 | 1,6,7h,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 450 | -
[10 empty] | STR | Schneider Toshiba | ATS480C32Y | 600 | 3 | 100 | 273 | 100
[10 empty] | (ISO) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 100 | 211 | 75
[10 empty] | (SHORT) MC | Schneider Electric | LC1F265 (Optional) | 600 | 3 | 100 | 169 | 60
SE105041 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 20 | 20 | A | FDS | Schneider Electric | GS2QU3N | 600 | 3 | 200 | 400 | - | 240 | 3 | 100 | 248 | 100 | 28800 | 1,6,7h,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 400 | -
[10 empty] | STR | Schneider Toshiba | ATS480C25Y | 600 | 3 | 100 | 248 | 100
[10 empty] | (ISO) MC | Schneider Electric | LC1F265 (Optional) | 600 | 3 | 100 | 192 | 75
[10 empty] | (SHORT) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 100 | 154 | 60
SE105042 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 57 | 14 | 11 | A | FDS | Schneider Electric | GS2QU3N | 600 | 3 | 200 | 400 | - | 480 | 3 | 100 | 124 | 100 | 8778 | 1,6,7n,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 225 | -
[10 empty] | STR | Schneider Toshiba | ATS480C14Y | 600 | 3 | 100 | 124 | 100
[10 empty] | (ISO) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 100 | 124 | 100
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 96 | 75
SE105043 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 30 | 14 | 11 | A | FDS | Schneider Electric | GS2MU3N | 600 | 3 | 200 | 200 | - | 600 | 3 | 100 | 99 | 100 | 4620 | 1,6,7m,8,9,10 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 175 | -
[10 empty] | STR | Schneider Toshiba | ATS480C11Y | 600 | 3 | 100 | 99 | 100
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 99 | 100
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 100 | 62 | 60
SE105044 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 35 | 20 | A | FDS | Schneider Electric | GS2SU3 | 600 | 3 | 200 | 600 | - | 208 | 3 | 100 | 343 | 125 | 50400 | 1,6,7i,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 600 | -
[10 empty] | STR | Schneider Toshiba | ATS480C41Y | 600 | 3 | 100 | 343 | 125
[10 empty] | (ISO) MC | Schneider Electric | LC1F400 (Optional) | 600 | 3 | 18 | 273 | 100
[10 empty] | (SHORT) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 100 | 211 | 75
SE105045 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 20 | 20 | A | FDS | Schneider Electric | GS2SU3 | 600 | 3 | 200 | 600 | - | 240 | 3 | 100 | 312 | 125 | 28800 | 1,6,7i,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 500 | -
[10 empty] | STR | Schneider Toshiba | ATS480C32Y | 600 | 3 | 100 | 312 | 125
[10 empty] | (ISO) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 100 | 248 | 100
[10 empty] | (SHORT) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 100 | 248 | 100
SE105046 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 57 | 14 | 11 | A | FDS | Schneider Electric | GS2QU3N | 600 | 3 | 200 | 400 | - | 480 | 3 | 100 | 156 | 125 | 8778 | 1,6,7c,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 250 | -
[10 empty] | STR | Schneider Toshiba | ATS480C17Y | 600 | 3 | 100 | 156 | 125
[10 empty] | (ISO) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 100 | 156 | 125
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 96 | 75
SE105047 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 57 | 14 | 11 | A | FDS | Schneider Electric | GS2QU3N | 600 | 3 | 200 | 400 | - | 600 | 3 | 100 | 125 | 125 | 8778 | 1,6,7n,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 225 | -
[10 empty] | STR | Schneider Toshiba | ATS480C14Y | 600 | 3 | 100 | 125 | 125
[10 empty] | (ISO) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 100 | 125 | 125
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 99 | 100
SE105048 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 35 | 20 | A | FDS | Schneider Electric | GS2TU3 | 600 | 3 | 200 | 800 | - | 208 | 3 | 100 | 396 | 150 | 50400 | 1,6,7e,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class L Fuse Rated: | 600 | 3 | 200 | 700 | -
[10 empty] | STR | Schneider Toshiba | ATS480C48Y | 600 | 3 | 100 | 396 | 150
[10 empty] | (ISO) MC | Schneider Electric | LC1F500 (Optional) | 600 | 3 | 30 | 396 | 150
[10 empty] | (SHORT) MC | Schneider Electric | LC1F400 (Optional) | 600 | 3 | 18 | 273 | 100
SE105049 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 35 | 20 | A | FDS | Schneider Electric | GS2SU3 | 600 | 3 | 200 | 600 | - | 240 | 3 | 100 | 360 | 150 | 50400 | 1,6,7i,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 600 | -
[10 empty] | STR | Schneider Toshiba | ATS480C41Y | 600 | 3 | 100 | 360 | 150
[10 empty] | (ISO) MC | Schneider Electric | LC1F400 (Optional) | 600 | 3 | 18 | 312 | 125
[10 empty] | (SHORT) MC | Schneider Electric | LC1F400 (Optional) | 600 | 3 | 18 | 312 | 125
SE105050 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 20 | 20 | A | FDS | Schneider Electric | GS2QU3N | 600 | 3 | 200 | 400 | - | 480 | 3 | 100 | 180 | 150 | 28800 | 1,6,7d,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 300 | -
[10 empty] | STR | Schneider Toshiba | ATS480C21Y | 600 | 3 | 100 | 180 | 150
[10 empty] | (ISO) MC | Schneider Electric | LC1F225 (Optional) | 600 | 3 | 10 | 180 | 150
[10 empty] | (SHORT) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 100 | 124 | 100
SE105051 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 57 | 14 | 11 | A | FDS | Schneider Electric | GS2QU3N | 600 | 3 | 200 | 400 | - | 600 | 3 | 100 | 144 | 150 | 8778 | 1,6,7c,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 250 | -
[10 empty] | STR | Schneider Toshiba | ATS480C17Y | 600 | 3 | 100 | 144 | 150
[10 empty] | (ISO) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 100 | 144 | 150
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 99 | 100
SE105052 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 35 | 20 | A | FDS | Schneider Electric | GS2TU3 | 600 | 3 | 200 | 800 | - | 240 | 3 | 100 | 480 | 200 | 50400 | 1,6,7r,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class L Fuse Rated: | 600 | 3 | 200 | 800 | -
[10 empty] | STR | Schneider Toshiba | ATS480C59Y | 600 | 3 | 100 | 480 | 200
[10 empty] | (ISO) MC | Schneider Electric | LC1F630 (Optional) | 600 | 3 | 42 | 722 | 300
[10 empty] | (SHORT) MC | Schneider Electric | LC1F500 (Optional) | 600 | 3 | 30 | 480 | 200
SE105053 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 20 | 20 | A | FDS | Schneider Electric | GS2QU3N | 600 | 3 | 200 | 400 | - | 480 | 3 | 100 | 240 | 200 | 28800 | 1,6,7h,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 400 | -
[10 empty] | STR | Schneider Toshiba | ATS480C25Y | 600 | 3 | 100 | 240 | 200
[10 empty] | (ISO) MC | Schneider Electric | LC1F265 (Optional) | 600 | 3 | 100 | 180 | 150
[10 empty] | (SHORT) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 100 | 156 | 125
SE105054 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 20 | 20 | A | FDS | Schneider Electric | GS2QU3N | 600 | 3 | 200 | 400 | - | 600 | 3 | 100 | 192 | 200 | 28800 | 1,6,7d,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 350 | -
[10 empty] | STR | Schneider Toshiba | ATS480C21Y | 600 | 3 | 100 | 192 | 200
[10 empty] | (ISO) MC | Schneider Electric | LC1F225 (Optional) | 600 | 3 | 10 | 144 | 150
[10 empty] | (SHORT) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 10 | 125 | 125
SE105055 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 20 | 20 | A | FDS | Schneider Electric | GS2SU3 | 600 | 3 | 200 | 600 | - | 480 | 3 | 100 | 302 | 250 | 28800 | 1,6,7s,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 500 | -
[10 empty] | STR | Schneider Toshiba | ATS480C32Y | 600 | 3 | 100 | 302 | 250
[10 empty] | (ISO) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 100 | 240 | 200
[10 empty] | (SHORT) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 100 | 240 | 200
SE105056 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 20 | 20 | A | FDS | Schneider Electric | GS2QU3N | 600 | 3 | 200 | 400 | - | 600 | 3 | 100 | 242 | 250 | 28800 | 1,6,7h,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 400 | -
[10 empty] | STR | Schneider Toshiba | ATS480C25Y | 600 | 3 | 100 | 242 | 250
[10 empty] | (ISO) MC | Schneider Electric | LC1F265 (Optional) | 600 | 3 | 100 | 192 | 200
[10 empty] | (SHORT) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 100 | 144 | 150
SE105057 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 35 | 20 | A | FDS | Schneider Electric | GS2SU3 | 600 | 3 | 200 | 600 | - | 480 | 3 | 100 | 361 | 300 | 50400 | 1,6,7e,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 600 | -
[10 empty] | STR | Schneider Toshiba | ATS480C41Y | 600 | 3 | 100 | 361 | 300
[10 empty] | (ISO) MC | Schneider Electric | LC1F400 (Optional) | 600 | 3 | 18 | 302 | 250
[10 empty] | (SHORT) MC | Schneider Electric | LC1F400 (Optional) | 600 | 3 | 18 | 302 | 250
SE105058 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 20 | 20 | A | FDS | Schneider Electric | GS2SU3 | 600 | 3 | 200 | 600 | - | 600 | 3 | 100 | 289 | 300 | 28800 | 1,6,7s,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 500 | -
[10 empty] | STR | Schneider Toshiba | ATS480C32Y | 600 | 3 | 100 | 289 | 300
[10 empty] | (ISO) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 100 | 242 | 250
[10 empty] | (SHORT) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 100 | 242 | 250
SE105059 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 35 | 20 | A | FDS | Schneider Electric | GS2TU3 | 600 | 3 | 200 | 800 | - | 480 | 3 | 100 | 414 | 350 | 50400 | 1,6,7f,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class L Fuse Rated: | 600 | 3 | 200 | 700 | -
[10 empty] | STR | Schneider Toshiba | ATS480C48Y | 600 | 3 | 100 | 414 | 350
[10 empty] | (ISO) MC | Schneider Electric | LC1F500 (Optional) | 600 | 3 | 30 | 477 | 400
[10 empty] | (SHORT) MC | Schneider Electric | LC1F400 (Optional) | 600 | 3 | 18 | 302 | 250
SE105060 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 35 | 20 | A | FDS | Schneider Electric | GS2SU3 | 600 | 3 | 200 | 600 | - | 600 | 3 | 100 | 336 | 350 | 50400 | 1,6,7i,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class J Fuse Rated: | 600 | 3 | 200 | 600 | -
[10 empty] | STR | Schneider Toshiba | ATS480C41Y | 600 | 3 | 100 | 336 | 350
[10 empty] | (ISO) MC | Schneider Electric | LC1F400 (Optional) | 600 | 3 | 18 | 286 | 300
[10 empty] | (SHORT) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 100 | 242 | 250
SE105061 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 35 | 20 | A | FDS | Schneider Electric | GS2TU3 | 600 | 3 | 200 | 800 | - | 480 | 3 | 100 | 477 | 400 | 50400 | 1,6,7r,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class L Fuse Rated: | 600 | 3 | 200 | 800 | -
[10 empty] | STR | Schneider Toshiba | ATS480C59Y | 600 | 3 | 100 | 477 | 400
[10 empty] | (ISO) MC | Schneider Electric | LC1F630 (Optional) | 600 | 3 | 42 | 722 | 600
[10 empty] | (SHORT) MC | Schneider Electric | LC1F500 (Optional) | 600 | 3 | 30 | 477 | 400
SE105062 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 35 | 20 | A | FDS | Schneider Electric | GS2TU3 | 600 | 3 | 200 | 800 | - | 600 | 3 | 100 | 382 | 400 | 50400 | 1,6,7e,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class L Fuse Rated: | 600 | 3 | 200 | 700 | -
[10 empty] | STR | Schneider Toshiba | ATS480C48Y | 600 | 3 | 100 | 382 | 400
[10 empty] | (ISO) MC | Schneider Electric | LC1F500 (Optional) | 600 | 3 | 30 | 472 | 500
[10 empty] | (SHORT) MC | Schneider Electric | LC1F400 (Optional) | 600 | 3 | 18 | 289 | 300
SE105063 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1B, 2, 3, 4, 5, 8 | 72 | 35 | 20 | A | FDS | Schneider Electric | GS2TU3 | 600 | 3 | 200 | 800 | - | 600 | 3 | 100 | 472 | 500 | 50400 | 1,6,7q,8,9 | N/A
[10 empty] | F | Any Listed Mfgr. | Any Class L Fuse Rated: | 600 | 3 | 200 | 800 | -
[10 empty] | STR | Schneider Toshiba | ATS480C59Y | 600 | 3 | 100 | 472 | 500
[10 empty] | (ISO) MC | Schneider Electric | LC1F500 (Optional) | 600 | 3 | 30 | 472 | 500
[10 empty] | (SHORT) MC | Schneider Electric | LC1F500 (Optional) | 600 | 3 | 30 | 472 | 500

## ATS480-Type C-NEMA
Issued: 2023-01-14
Last Revised: 2023-01-14
Database Identification Number | Listed Combination Motor Controller Information | [7 empty] | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | Conditions of Use | Schematic | Other References
| Listing Report Information |  |  |  |  | Enclosure or Unit Dimensions
| UL File Number | Report Issue Date YYYY-MM-DD | Volume / Section (Vol#).(Sec#) | Model Number or Product Style/ Designation | Product Description on Page/Figure/Ill. | Enclosure or Unit Height, inches | Width, inches | Depth, inches |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | HP Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | HP Rating
SE105070 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36020 | 600 | 3 | 125 | 20 | - | 208 | 3 | 100 | 10.6 | 3 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba | ATS480D17Y | 600 | 3 | - | 10.6 | 3
[10 empty] | (ISO) MC | Square D | 8502SC02 (Optional) | 600 | 3 | 100 | 24.2 | 7.5
[10 empty] | (SHORT) MC | Square D | 8502SC02 (Optional) | 600 | 3 | 100 | 24.2 | 7.5
SE105071 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36030 | 600 | 3 | 125 | 30 | - | 208 | 3 | 100 | 16.7 | 5 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D22Y | 600 | 3 | - | 16.7 | 5 | 208, 3 | 208, 3 | 100 | 16.7 | 5 | 4620
[10 empty] | (ISO) MC | Square D | 8502SC02 (Optional) | 600 | 3 | 100 | 24.2 | 7.5 | 208, 3 | 208, 3 | 100 | 16.7 | 5 | 4620
[10 empty] | (SHORT) MC | Square D | 8502SC02 (Optional) | 600 | 3 | 100 | 24.2 | 7.5 | 208, 3 | 208, 3 | 100 | 16.7 | 5 | 4620
SE105072 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36030 | 600 | 3 | 125 | 30 | - | 240 | 3 | 100 | 15.2 | 5 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D17Y | 600 | 3 | - | 15.2 | 5 | 240, 3 | 240, 3 | 100 | 15.2 | 5 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Square D | 8502SC02 (Optional) | 600 | 3 | 100 | 24.2 | 7.5 | 240, 3 | 240, 3 | 100 | 15.2 | 5 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Square D | 8502SC02 (Optional) | 600 | 3 | 100 | 24.2 | 7.5 | 240, 3 | 240, 3 | 100 | 15.2 | 5 | 4620 | 1, 6, 7a
SE105073 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36045 | 600 | 3 | 125 | 45 | - | 208 | 3 | 100 | 24.2 | 7.5 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D32Y | 600 | 3 | - | 24.2 | 7.5 | 208, 3 | 208, 3 | 100 | 24.2 | 7.5 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Square D | 8502SC02 (Optional) | 600 | 3 | 100 | 24.2 | 7.5 | 208, 3 | 208, 3 | 100 | 24.2 | 7.5 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Square D | 8502SC02 (Optional) | 600 | 3 | 100 | 24.2 | 7.5 | 208, 3 | 208, 3 | 100 | 24.2 | 7.5 | 4620 | 1, 6, 7a
SE105074 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36045 | 600 | 3 | 125 | 45 | - | 240 | 3 | 100 | 22 | 7.5 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D22Y | 600 | 3 | - | 22 | 7.5 | 240, 3 | 240, 3 | 100 | 22 | 7.5 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Square D | 8502SC02 (Optional) | 600 | 3 | 100 | 24.2 | 7.5 | 240, 3 | 240, 3 | 100 | 22 | 7.5 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Square D | 8502SC02 (Optional) | 600 | 3 | 100 | 24.2 | 7.5 | 240, 3 | 240, 3 | 100 | 22 | 7.5 | 4620 | 1, 6, 7a
SE105075 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36060 | 600 | 3 | 125 | 60 | - | 208 | 3 | 100 | 30.8 | 10 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D38Y | 600 | 3 | - | 30.8 | 10 | 208, 3 | 208, 3 | 100 | 30.8 | 10 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Square D | 8502SD02 (Optional) | 600 | 3 | 100 | 30.8 | 10 | 208, 3 | 208, 3 | 100 | 30.8 | 10 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Square D | 8502SD02 (Optional) | 600 | 3 | 100 | 30.8 | 10 | 208, 3 | 208, 3 | 100 | 30.8 | 10 | 4620 | 1, 6, 7a
SE105076 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36050 | 600 | 3 | 125 | 50 | - | 240 | 3 | 100 | 28 | 10 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D32Y | 600 | 3 | - | 28 | 10 | 240, 3 | 240, 3 | 100 | 28 | 10 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Square D | 8502SD02 (Optional) | 600 | 3 | 100 | 42 | 15 | 240, 3 | 240, 3 | 100 | 28 | 10 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Square D | 8502SD02 (Optional) | 600 | 3 | 100 | 42 | 15 | 240, 3 | 240, 3 | 100 | 28 | 10 | 4620 | 1, 6, 7a
SE105077 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36025 | 600 | 3 | 100 | 25 | - | 480 | 3 | 100 | 14 | 10 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D17Y | 600 | 3 | - | 14 | 10 | 480, 3 | 480, 3 | 100 | 14 | 10 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Square D | 8502SC02 (Optional) | 600 | 3 | 100 | 14 | 10 | 480, 3 | 480, 3 | 100 | 14 | 10 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Square D | 8502SC02 (Optional) | 600 | 3 | 100 | 14 | 10 | 480, 3 | 480, 3 | 100 | 14 | 10 | 4620 | 1, 6, 7a
SE105078 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36110 | 600 | 3 | 125 | 110 | - | 208 | 3 | 100 | 46.2 | 15 | 4620 | 1, 6, 7b, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D62Y | 600 | 3 | - | 46.2 | 15 | 208, 3 | 208, 3 | 100 | 46.2 | 15 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Square D | 8502SE02 (Optional) | 600 | 3 | 100 | 74.8 | 25 | 208, 3 | 208, 3 | 100 | 46.2 | 15 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Square D | 8502SE02 (Optional) | 600 | 3 | 100 | 74.8 | 25 | 208, 3 | 208, 3 | 100 | 46.2 | 15 | 4620 | 1, 6, 7b
SE105079 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36080 | 600 | 3 | 125 | 80 | - | 240 | 3 | 100 | 42 | 15 | 4620 | 1, 6, 7k, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D47Y | 600 | 3 | - | 42 | 15 | 240, 3 | 240, 3 | 100 | 42 | 15 | 4620 | 1, 6, 7k
[10 empty] | (ISO) MC | Square D | 8502SD02 (Optional) | 600 | 3 | 100 | 42 | 15 | 240, 3 | 240, 3 | 100 | 42 | 15 | 4620 | 1, 6, 7k
[10 empty] | (SHORT) MC | Square D | 8502SD02 (Optional) | 600 | 3 | 100 | 42 | 15 | 240, 3 | 240, 3 | 100 | 42 | 15 | 4620 | 1, 6, 7k
SE105080 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36040 | 600 | 3 | 100 | 40 | - | 480 | 3 | 100 | 21 | 15 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D22Y | 600 | 3 | - | 21 | 15 | 480, 3 | 480, 3 | 100 | 21 | 15 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Square D | 8502SD02 (Optional) | 600 | 3 | 100 | 34 | 25 | 480, 3 | 480, 3 | 100 | 21 | 15 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Square D | 8502SD02 (Optional) | 600 | 3 | 100 | 34 | 25 | 480, 3 | 480, 3 | 100 | 21 | 15 | 4620 | 1, 6, 7a
SE105081 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36110 | 600 | 3 | 125 | 110 | - | 208 | 3 | 100 | 59.4 | 20 | 4620 | 1, 6, 7b, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D75Y | 600 | 3 | - | 59.4 | 20 | 208, 3 | 208, 3 | 100 | 59.4 | 20 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Square D | 8502SE02 (Optional) | 600 | 3 | 100 | 74.8 | 25 | 208, 3 | 208, 3 | 100 | 59.4 | 20 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Square D | 8502SE02 (Optional) | 600 | 3 | 100 | 74.8 | 25 | 208, 3 | 208, 3 | 100 | 59.4 | 20 | 4620 | 1, 6, 7b
SE105082 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36110 | 600 | 3 | 125 | 110 | - | 240 | 3 | 100 | 54 | 20 | 4620 | 1, 6, 7b, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D62Y | 600 | 3 | - | 54 | 20 | 240, 3 | 240, 3 | 100 | 54 | 20 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Square D | 8502SE02 (Optional) | 600 | 3 | 100 | 80 | 30 | 240, 3 | 240, 3 | 100 | 54 | 20 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Square D | 8502SE02 (Optional) | 600 | 3 | 100 | 80 | 30 | 240, 3 | 240, 3 | 100 | 54 | 20 | 4620 | 1, 6, 7b
SE105083 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36050 | 600 | 3 | 100 | 50 | - | 480 | 3 | 100 | 27 | 20 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D32Y | 600 | 3 | - | 27 | 20 | 480, 3 | 480, 3 | 100 | 27 | 20 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Square D | 8502SD02 (Optional) | 600 | 3 | 100 | 34 | 25 | 480, 3 | 480, 3 | 100 | 27 | 20 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Square D | 8502SD02 (Optional) | 600 | 3 | 100 | 34 | 25 | 480, 3 | 480, 3 | 100 | 27 | 20 | 4620 | 1, 6, 7a
SE105084 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36110 | 600 | 3 | 125 | 110 | - | 208 | 3 | 100 | 74.8 | 25 | 4620 | 1, 6, 7l, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D88Y | 600 | 3 | - | 74.8 | 25 | 208, 3 | 208, 3 | 100 | 74.8 | 25 | 4620 | 1, 6, 7L
[10 empty] | (ISO) MC | Square D | 8502SE02 (Optional) | 600 | 3 | 100 | 74.08 | 25 | 208, 3 | 208, 3 | 100 | 74.8 | 25 | 4620 | 1, 6, 7L
[10 empty] | (SHORT) MC | Square D | 8502SE02 (Optional) | 600 | 3 | 100 | 74.8 | 25 | 208, 3 | 208, 3 | 100 | 74.8 | 25 | 4620 | 1, 6, 7L
SE105085 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36110 | 600 | 3 | 125 | 110 | - | 240 | 3 | 100 | 68 | 25 | 4620 | 1, 6, 7b, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D75Y | 600 | 3 | - | 68 | 25 | 240, 3 | 240, 3 | 100 | 68 | 25 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Square D | 8502SE02 (Optional) | 600 | 3 | 100 | 80 | 30 | 240, 3 | 240, 3 | 100 | 68 | 25 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Square D | 8502SE02 (Optional) | 600 | 3 | 100 | 80 | 30 | 240, 3 | 240, 3 | 100 | 68 | 25 | 4620 | 1, 6, 7b
SE105086 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36060 | 600 | 3 | 100 | 60 | - | 480 | 3 | 100 | 34 | 25 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D38Y | 600 | 3 | - | 34 | 25 | 480, 3 | 480, 3 | 100 | 34 | 25 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Square D | 8502SD02 (Optional) | 600 | 3 | 100 | 34 | 25 | 480, 3 | 480, 3 | 100 | 34 | 25 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Square D | 8502SD02 (Optional) | 600 | 3 | 100 | 34 | 25 | 480, 3 | 480, 3 | 100 | 34 | 25 | 4620 | 1, 6, 7a
SE105087 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36125 | 600 | 3 | 125 | 125 | - | 208 | 3 | 100 | 88 | 30 | 4620 | 1, 6, 7m, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C11Y | 600 | 3 | - | 88 | 30 | 208, 3 | 208, 3 | 100 | 88 | 30 | 4620 | 1, 6, 7m
[10 empty] | (ISO) MC | Square D | 8502SF02 (Optional) | 600 | 3 | 100 | 114 | 40 | 208, 3 | 208, 3 | 100 | 88 | 30 | 4620 | 1, 6, 7m
[10 empty] | (SHORT) MC | Square D | 8502SF02 (Optional) | 600 | 3 | 100 | 114 | 40 | 208, 3 | 208, 3 | 100 | 88 | 30 | 4620 | 1, 6, 7m
SE105088 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36110 | 600 | 3 | 125 | 110 | - | 240 | 3 | 100 | 80 | 30 | 4620 | 1, 6, 7l, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D88Y | 600 | 3 | - | 80 | 30 | 240, 3 | 240, 3 | 100 | 80 | 30 | 4620 | 1, 6, 7L
[10 empty] | (ISO) MC | Square D | 8502SE02 (Optional) | 600 | 3 | 100 | 80 | 30 | 240, 3 | 240, 3 | 100 | 80 | 30 | 4620 | 1, 6, 7L
[10 empty] | (SHORT) MC | Square D | 8502SE02 (Optional) | 600 | 3 | 100 | 80 | 30 | 240, 3 | 240, 3 | 100 | 80 | 30 | 4620 | 1, 6, 7L
SE105089 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36080 | 600 | 3 | 100 | 80 | - | 480 | 3 | 100 | 40 | 30 | 4620 | 1, 6, 7k, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D47Y | 600 | 3 | - | 40 | 30 | 480, 3 | 480, 3 | 100 | 40 | 30 | 4620 | 1, 6, 7k
[10 empty] | (ISO) MC | Square D | 8502SE02 (Optional) | 600 | 3 | 100 | 65 | 50 | 480, 3 | 480, 3 | 100 | 40 | 30 | 4620 | 1, 6, 7k
[10 empty] | (SHORT) MC | Square D | 8502SE02 (Optional) | 600 | 3 | 100 | 65 | 50 | 480, 3 | 480, 3 | 100 | 40 | 30 | 4620 | 1, 6, 7k
SE105090 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | C | CB | Square D | JLx36175 | 600 | 3 | 125 | 175 | - | 208 | 3 | 100 | 114 | 40 | 6468 | 1, 6, 7n, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C14Y | 600 | 3 | - | 114 | 40 | 208, 3 | 208, 3 | 100 | 114 | 40 | 4620 | 1, 6, 7n
[10 empty] | (ISO) MC | Square D | 8502SF02 (Optional) | 600 | 3 | 100 | 114 | 40 | 208, 3 | 208, 3 | 100 | 114 | 40 | 4620 | 1, 6, 7n
[10 empty] | (SHORT) MC | Square D | 8502SF02 (Optional) | 600 | 3 | 100 | 114 | 40 | 208, 3 | 208, 3 | 100 | 114 | 40 | 4620 | 1, 6, 7n
SE105091 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36150 | 600 | 3 | 125 | 150 | - | 240 | 3 | 100 | 104 | 40 | 4620 | 1, 6, 7m, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C11Y | 600 | 3 | - | 104 | 40 | 240, 3 | 240, 3 | 100 | 104 | 40 | 4620 | 1, 6, 7m
[10 empty] | (ISO) MC | Square D | 8502SF02 (Optional) | 600 | 3 | 100 | 130 | 50 | 240, 3 | 240, 3 | 100 | 104 | 40 | 4620 | 1, 6, 7m
[10 empty] | (SHORT) MC | Square D | 8502SF02 (Optional) | 600 | 3 | 100 | 130 | 50 | 240, 3 | 240, 3 | 100 | 104 | 40 | 4620 | 1, 6, 7m
SE105092 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36110 | 600 | 3 | 100 | 110 | - | 480 | 3 | 100 | 52 | 40 | 4620 | 1, 6, 7b, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D62Y | 600 | 3 | - | 52 | 40 | 480, 3 | 480, 3 | 100 | 52 | 40 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Square D | 8502SE02 (Optional) | 600 | 3 | 100 | 65 | 50 | 480, 3 | 480, 3 | 100 | 52 | 40 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Square D | 8502SE02 (Optional) | 600 | 3 | 100 | 65 | 50 | 480, 3 | 480, 3 | 100 | 52 | 40 | 4620 | 1, 6, 7b
SE105093 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | C | CB | Square D | JLx36200 | 600 | 3 | 125 | 200 | - | 208 | 3 | 100 | 143 | 50 | 6468 | 1, 6, 7c, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C17Y | 600 | 3 | - | 143 | 50 | 208, 3 | 208, 3 | 100 | 143 | 50 | 4620 | 1, 6, 7c
[10 empty] | (ISO) MC | Square D | 8502SG02 (Optional) | 600 | 3 | 100 | 211 | 75 | 208, 3 | 208, 3 | 100 | 143 | 50 | 4620 | 1, 6, 7c
[10 empty] | (SHORT) MC | Square D | 8502SG02 (Optional) | 600 | 3 | 100 | 211 | 75 | 208, 3 | 208, 3 | 100 | 143 | 50 | 4620 | 1, 6, 7c
SE105094 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | C | CB | Square D | JLx36200 | 600 | 3 | 125 | 200 | - | 240 | 3 | 100 | 130 | 50 | 6468 | 1, 6, 7n, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C14Y | 600 | 3 | - | 130 | 50 | 240, 3 | 240, 3 | 100 | 130 | 50 | 4620 | 1, 6, 7n
[10 empty] | (ISO) MC | Square D | 8502SF02 (Optional) | 600 | 3 | 100 | 130 | 50 | 240, 3 | 240, 3 | 100 | 130 | 50 | 4620 | 1, 6, 7n
[10 empty] | (SHORT) MC | Square D | 8502SF02 (Optional) | 600 | 3 | 100 | 130 | 50 | 240, 3 | 240, 3 | 100 | 130 | 50 | 4620 | 1, 6, 7n
SE105095 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36110 | 600 | 3 | 100 | 110 | - | 480 | 3 | 100 | 65 | 50 | 4620 | 1, 6, 7b, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D75Y | 600 | 3 | - | 65 | 50 | 480, 3 | 480, 3 | 100 | 65 | 50 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Square D | 8502SE02 (Optional) | 600 | 3 | 100 | 65 | 50 | 480, 3 | 480, 3 | 100 | 65 | 50 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Square D | 8502SE02 (Optional) | 600 | 3 | 100 | 65 | 50 | 480, 3 | 480, 3 | 100 | 65 | 50 | 4620 | 1, 6, 7b
SE105096 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36400 | 600 | 3 | 125 | 400 | - | 208 | 3 | 100 | 169 | 60 | 28800 | 1, 6, 7d, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C21Y | 600 | 3 | - | 169 | 60 | 208, 3 | 208, 3 | 100 | 169 | 60 | 4620 | 1, 6, 7d
[10 empty] | (ISO) MC | Square D | 8502SG02 (Optional) | 600 | 3 | 100 | 211 | 75 | 208, 3 | 208, 3 | 100 | 169 | 60 | 4620 | 1, 6, 7d
[10 empty] | (SHORT) MC | Square D | 8502SG02 (Optional) | 600 | 3 | 100 | 211 | 75 | 208, 3 | 208, 3 | 100 | 169 | 60 | 4620 | 1, 6, 7d
SE105097 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | C | CB | Square D | JLx36225 | 600 | 3 | 125 | 225 | - | 240 | 3 | 100 | 154 | 60 | 6468 | 1, 6, 7c, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C17Y | 600 | 3 | - | 154 | 60 | 240, 3 | 240, 3 | 100 | 154 | 60 | 4620 | 1, 6, 7c
[10 empty] | (ISO) MC | Square D | 8502SG02 (Optional) | 600 | 3 | 100 | 248 | 100 | 240, 3 | 240, 3 | 100 | 154 | 60 | 4620 | 1, 6, 7c
[10 empty] | (SHORT) MC | Square D | 8502SG02 (Optional) | 600 | 3 | 100 | 248 | 100 | 240, 3 | 240, 3 | 100 | 154 | 60 | 4620 | 1, 6, 7c
SE105098 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36110 | 600 | 3 | 100 | 110 | - | 480 | 3 | 100 | 77 | 60 | 4620 | 1, 6, 7l, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D88Y | 600 | 3 | - | 77 | 60 | 480, 3 | 480, 3 | 100 | 77 | 60 | 4620 | 1, 6, 7L
[10 empty] | (ISO) MC | Square D | 8502SF02 (Optional) | 600 | 3 | 100 | 124 | 100 | 480, 3 | 480, 3 | 100 | 77 | 60 | 4620 | 1, 6, 7L
[10 empty] | (SHORT) MC | Square D | 8502SF02 (Optional) | 600 | 3 | 100 | 124 | 100 | 480, 3 | 480, 3 | 100 | 77 | 60 | 4620 | 1, 6, 7L
SE105099 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36400 | 600 | 3 | 125 | 400 | - | 208 | 3 | 100 | 211 | 75 | 28800 | 1, 6, 7p, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C25Y | 600 | 3 | - | 211 | 75 | 208, 3 | 208, 3 | 100 | 211 | 75 | 4620 | 1, 6, 7p
[10 empty] | (ISO) MC | Square D | 8502SG02 (Optional) | 600 | 3 | 100 | 211 | 75 | 208, 3 | 208, 3 | 100 | 211 | 75 | 4620 | 1, 6, 7p
[10 empty] | (SHORT) MC | Square D | 8502SG02 (Optional) | 600 | 3 | 100 | 211 | 75 | 208, 3 | 208, 3 | 100 | 211 | 75 | 4620 | 1, 6, 7p
SE105100 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36400 | 600 | 3 | 125 | 400 | - | 240 | 3 | 100 | 192 | 75 | 28800 | 1, 6, 7d, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C21Y | 600 | 3 | - | 192 | 75 | 240, 3 | 240, 3 | 100 | 192 | 75 | 4620 | 1, 6, 7d
[10 empty] | (ISO) MC | Square D | 8502SG02 (Optional) | 600 | 3 | 100 | 248 | 100 | 240, 3 | 240, 3 | 100 | 192 | 75 | 4620 | 1, 6, 7d
[10 empty] | (SHORT) MC | Square D | 8502SG02 (Optional) | 600 | 3 | 100 | 248 | 100 | 240, 3 | 240, 3 | 100 | 192 | 75 | 4620 | 1, 6, 7d
SE105101 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36125 | 600 | 3 | 100 | 125 | - | 480 | 3 | 100 | 96 | 75 | 4620 | 1, 6, 7m, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C11Y | 600 | 3 | - | 96 | 75 | 480, 3 | 480, 3 | 100 | 96 | 75 | 4620 | 1, 6, 7m
[10 empty] | (ISO) MC | Square D | 8502SF02 (Optional) | 600 | 3 | 100 | 124 | 100 | 480, 3 | 480, 3 | 100 | 96 | 75 | 4620 | 1, 6, 7m
[10 empty] | (SHORT) MC | Square D | 8502SF02 (Optional) | 600 | 3 | 100 | 124 | 100 | 480, 3 | 480, 3 | 100 | 96 | 75 | 4620 | 1, 6, 7m
SE105102 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36600 | 600 | 3 | 125 | 600 | - | 208 | 3 | 100 | 273 | 100 | 28800 | 1, 6, 7h, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C32Y | 600 | 3 | - | 273 | 100 | 208, 3 | 208, 3 | 100 | 273 | 100 | 4620 | 1, 6, 7h
[10 empty] | (ISO) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 396 | 150 | 208, 3 | 208, 3 | 100 | 273 | 100 | 4620 | 1, 6, 7h
[10 empty] | (SHORT) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 396 | 150 | 208, 3 | 208, 3 | 100 | 273 | 100 | 4620 | 1, 6, 7h
SE105103 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36600 | 600 | 3 | 125 | 600 | - | 240 | 3 | 100 | 248 | 100 | 28800 | 1, 6, 7h, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C25Y | 600 | 3 | - | 248 | 100 | 240, 3 | 240, 3 | 100 | 248 | 100 | 4620 | 1, 6, 7h
[10 empty] | (ISO) MC | Square D | 8502SG02 (Optional) | 600 | 3 | 100 | 248 | 100 | 240, 3 | 240, 3 | 100 | 248 | 100 | 4620 | 1, 6, 7h
[10 empty] | (SHORT) MC | Square D | 8502SG02 (Optional) | 600 | 3 | 100 | 248 | 100 | 240, 3 | 240, 3 | 100 | 248 | 100 | 4620 | 1, 6, 7h
SE105104 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | C | CB | Square D | JLx36200 | 600 | 3 | 100 | 200 | - | 480 | 3 | 100 | 124 | 100 | 6468 | 1, 6, 7n, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C14Y | 600 | 3 | - | 124 | 100 | 480, 3 | 480, 3 | 100 | 124 | 100 | 4620 | 1, 6, 7n
[10 empty] | (ISO) MC | Square D | 8502SF02 (Optional) | 600 | 3 | 100 | 124 | 100 | 480, 3 | 480, 3 | 100 | 124 | 100 | 4620 | 1, 6, 7n
[10 empty] | (SHORT) MC | Square D | 8502SF02 (Optional) | 600 | 3 | 100 | 124 | 100 | 480, 3 | 480, 3 | 100 | 124 | 100 | 4620 | 1, 6, 7n
SE105105 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 35 | 20 | C | CB | Square D | PLx34060 | 480 | 3 | 125 | 600 | - | 208 | 3 | 100 | 343 | 125 | 50400 | 1, 6, 7i, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C41Y | 600 | 3 | - | 343 | 125 | 208, 3 | 208, 3 | 100 | 343 | 125 | 4620 | 1, 6, 7i
[10 empty] | (ISO) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 396 | 150 | 208, 3 | 208, 3 | 100 | 343 | 125 | 4620 | 1, 6, 7i
[10 empty] | (SHORT) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 396 | 150 | 208, 3 | 208, 3 | 100 | 343 | 125 | 4620 | 1, 6, 7i
SE105106 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | PLx34060 | 480 | 3 | 125 | 600 | - | 240 | 3 | 100 | 312 | 125 | 28800 | 1, 6, 7i, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C32Y | 600 | 3 | - | 312 | 125 | 240, 3 | 240, 3 | 100 | 312 | 125 | 4620 | 1, 6, 7i
[10 empty] | (ISO) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 480 | 200 | 240, 3 | 240, 3 | 100 | 312 | 125 | 4620 | 1, 6, 7i
[10 empty] | (SHORT) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 480 | 200 | 240, 3 | 240, 3 | 100 | 312 | 125 | 4620 | 1, 6, 7i
SE105107 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | C | CB | Square D | JLx36225 | 600 | 3 | 100 | 225 | - | 480 | 3 | 100 | 156 | 125 | 6468 | 1, 6, 7c, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C17Y | 600 | 3 | - | 156 | 125 | 480, 3 | 480, 3 | 100 | 156 | 125 | 4620 | 1, 6, 7c
[10 empty] | (ISO) MC | Square D | 8502SG02 (Optional) | 600 | 3 | 100 | 240 | 200 | 480, 3 | 480, 3 | 100 | 156 | 125 | 4620 | 1, 6, 7c
[10 empty] | (SHORT) MC | Square D | 8502SG02 (Optional) | 600 | 3 | 100 | 240 | 200 | 480, 3 | 480, 3 | 100 | 156 | 125 | 4620 | 1, 6, 7c
SE105108 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 35 | 20 | C | CB | Square D | PLx34060 | 480 | 3 | 125 | 600 | - | 208 | 3 | 100 | 396 | 150 | 50400 | 1, 6, 7e, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C48Y | 600 | 3 | - | 396 | 150 | 208, 3 | 208, 3 | 100 | 396 | 150 | 4620 | 1, 6, 7e
[10 empty] | (ISO) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 396 | 150 | 208, 3 | 208, 3 | 100 | 396 | 150 | 4620 | 1, 6, 7e
[10 empty] | (SHORT) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 396 | 150 | 208, 3 | 208, 3 | 100 | 396 | 150 | 4620 | 1, 6, 7e
SE105109 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 35 | 20 | C | CB | Square D | PLx34060 | 480 | 3 | 125 | 600 | - | 240 | 3 | 100 | 360 | 150 | 50400 | 1, 6, 7e, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C41Y | 600 | 3 | - | 360 | 150 | 240, 3 | 240, 3 | 100 | 360 | 150 | 4620 | 1, 6, 7e
[10 empty] | (ISO) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 480 | 200 | 240, 3 | 240, 3 | 100 | 360 | 150 | 4620 | 1, 6, 7e
[10 empty] | (SHORT) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 480 | 200 | 240, 3 | 240, 3 | 100 | 360 | 150 | 4620 | 1, 6, 7e
SE105110 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36400 | 600 | 3 | 100 | 400 | - | 480 | 3 | 100 | 180 | 150 | 28800 | 1, 6, 7d, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C21Y | 600 | 3 | - | 180 | 150 | 480, 3 | 480, 3 | 100 | 180 | 150 | 4620 | 1, 6, 7d
[10 empty] | (ISO) MC | Square D | 8502SG02 (Optional) | 600 | 3 | 100 | 240 | 200 | 480, 3 | 480, 3 | 100 | 180 | 150 | 4620 | 1, 6, 7d
[10 empty] | (SHORT) MC | Square D | 8502SG02 (Optional) | 600 | 3 | 100 | 240 | 200 | 480, 3 | 480, 3 | 100 | 180 | 150 | 4620 | 1, 6, 7d
SE105111 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 35 | 20 | C | CB | Square D | PLx34080 | 480 | 3 | 125 | 800 | - | 208 | 3 | 100 | 528 | 200 | 50400 | 1, 6, 7q, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C66Y | 600 | 3 | - | 528 | 200 | 208, 3 | 208, 3 | 100 | 10.6 | 3 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 396 | 150 | 208, 3 | 208, 3 | 100 | 10.6 | 3 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 396 | 150 | 208, 3 | 208, 3 | 100 | 10.6 | 3 | 4620 | 1, 6, 7a
SE105112 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 35 | 20 | C | CB | Square D | PLx34080 | 480 | 3 | 125 | 800 | - | 240 | 3 | 100 | 480 | 200 | 50400 | 1, 6, 7r, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C59Y | 600 | 3 | - | 480 | 200 | 240, 3 | 240, 3 | 100 | 480 | 200 | 4620 | 1, 6, 7r
[10 empty] | (ISO) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 480 | 200 | 240, 3 | 240, 3 | 100 | 480 | 200 | 4620 | 1, 6, 7r
[10 empty] | (SHORT) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 480 | 200 | 240, 3 | 240, 3 | 100 | 480 | 200 | 4620 | 1, 6, 7r
SE105113 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36600 | 600 | 3 | 100 | 600 | - | 480 | 3 | 100 | 240 | 200 | 28800 | 1, 6, 7h, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C25Y | 600 | 3 | - | 240 | 200 | 480, 3 | 480, 3 | 100 | 240 | 200 | 4620 | 1, 6, 7h
[10 empty] | (ISO) MC | Square D | 8502SG02 (Optional) | 600 | 3 | 100 | 240 | 200 | 480, 3 | 480, 3 | 100 | 240 | 200 | 4620 | 1, 6, 7h
[10 empty] | (SHORT) MC | Square D | 8502SG02 (Optional) | 600 | 3 | 100 | 240 | 200 | 480, 3 | 480, 3 | 100 | 240 | 200 | 4620 | 1, 6, 7h
SE105114 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36600 | 600 | 3 | 100 | 600 | - | 480 | 3 | 100 | 302 | 250 | 28800 | 1, 6, 7s, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C32Y | 600 | 3 | - | 302 | 250 | 480, 3 | 480, 3 | 100 | 302 | 250 | 4620 | 1, 6, 7s
[10 empty] | (ISO) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 477 | 400 | 480, 3 | 480, 3 | 100 | 302 | 250 | 4620 | 1, 6, 7s
[10 empty] | (SHORT) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 477 | 400 | 480, 3 | 480, 3 | 100 | 302 | 250 | 4620 | 1, 6, 7s
SE105115 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 35 | 20 | C | CB | Square D | PLx34060 | 480 | 3 | 100 | 600 | - | 480 | 3 | 100 | 361 | 300 | 50400 | 1, 6, 7e, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C41Y | 600 | 3 | - | 361 | 300 | 480, 3 | 480, 3 | 100 | 361 | 300 | 4620 | 1, 6, 7e
[10 empty] | (ISO) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 477 | 400 | 480, 3 | 480, 3 | 100 | 361 | 300 | 4620 | 1, 6, 7e
[10 empty] | (SHORT) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 477 | 400 | 480, 3 | 480, 3 | 100 | 361 | 300 | 4620 | 1, 6, 7e
SE105116 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 35 | 20 | C | CB | Square D | PLx36060 | 480 | 3 | 100 | 600 | - | 480 | 3 | 100 | 414 | 350 | 50400 | 1, 6, 7f, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C48Y | 600 | 3 | - | 414 | 350 | 480, 3 | 480, 3 | 100 | 414 | 350 | 4620 | 1, 6, 7f
[10 empty] | (ISO) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 477 | 400 | 480, 3 | 480, 3 | 100 | 414 | 350 | 4620 | 1, 6, 7f
[10 empty] | (SHORT) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 477 | 400 | 480, 3 | 480, 3 | 100 | 414 | 350 | 4620 | 1, 6, 7f
SE105117 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 35 | 20 | C | CB | Square D | PLx34080 | 480 | 3 | 100 | 800 | - | 480 | 3 | 100 | 477 | 400 | 50400 | 1, 6, 7r, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C59Y | 600 | 3 | - | 477 | 400 | 480, 3 | 480, 3 | 100 | 477 | 400 | 4620 | 1, 6, 7r
[10 empty] | (ISO) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 477 | 400 | 480, 3 | 480, 3 | 100 | 477 | 400 | 4620 | 1, 6, 7r
[10 empty] | (SHORT) MC | Square D | 8502SH02 (Optional) | 600 | 3 | 65 | 477 | 400 | 480, 3 | 480, 3 | 100 | 477 | 400 | 4620 | 1, 6, 7r

## ATS480-Type C-IEC
Issued: 2023-01-14
Last Revised: 2023-01-14
Database Identification Number | Listed Combination Motor Controller Information | [7 empty] | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | Conditions of Use | Schematic | Other References
| Listing Report Information |  |  |  |  | Enclosure or Unit Dimensions
| UL File Number | Report Issue Date YYYY-MM-DD | Volume / Section (Vol#).(Sec#) | Model Number or Product Style/ Designation | Product Description on Page/Figure/Ill. | Enclosure or Unit Height, inches | Width, inches | Depth, inches |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | HP Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | HP Rating
SE105120 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36020 | 600 | 3 | 125 | 20 | - | 208 | 3 | 100 | 10.6 | 3 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba | ATS480D17Y | 600 | 3 | - | 10.6 | 3
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 85 | 24.2 | 7.5
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 85 | 24.2 | 7.5
SE105121 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36030 | 600 | 3 | 125 | 30 | - | 208 | 3 | 100 | 16.7 | 5 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D22Y | 600 | 3 | - | 16.7 | 5 | 208, 3 | 208, 3 | 100 | 16.7 | 5 | 4620
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 85 | 24.2 | 7.5 | 208, 3 | 208, 3 | 100 | 16.7 | 5 | 4620
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 85 | 24.2 | 7.5 | 208, 3 | 208, 3 | 100 | 16.7 | 5 | 4620
SE105122 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36030 | 600 | 3 | 125 | 30 | - | 240 | 3 | 100 | 15.2 | 5 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D17Y | 600 | 3 | - | 15.2 | 5 | 240, 3 | 240, 3 | 100 | 15.2 | 5 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 85 | 22 | 7.5 | 240, 3 | 240, 3 | 100 | 15.2 | 5 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 85 | 22 | 7.5 | 240, 3 | 240, 3 | 100 | 15.2 | 5 | 4620 | 1, 6, 7a
SE105123 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36045 | 600 | 3 | 125 | 45 | - | 208 | 3 | 100 | 24.2 | 7.5 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D32Y | 600 | 3 | - | 24.2 | 7.5 | 208, 3 | 208, 3 | 100 | 24.2 | 7.5 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 85 | 30.8 | 10 | 208, 3 | 208, 3 | 100 | 24.2 | 7.5 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 85 | 24.2 | 7.5 | 208, 3 | 208, 3 | 100 | 24.2 | 7.5 | 4620 | 1, 6, 7a
SE105124 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36045 | 600 | 3 | 125 | 45 | - | 240 | 3 | 100 | 22 | 7.5 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D22Y | 600 | 3 | - | 22 | 7.5 | 240, 3 | 240, 3 | 100 | 22 | 7.5 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 85 | 28 | 10 | 240, 3 | 240, 3 | 100 | 22 | 7.5 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 85 | 22 | 7.5 | 240, 3 | 240, 3 | 100 | 22 | 7.5 | 4620 | 1, 6, 7a
SE105125 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36060 | 600 | 3 | 125 | 60 | - | 208 | 3 | 100 | 30.8 | 10 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D38Y | 600 | 3 | - | 30.8 | 10 | 208, 3 | 208, 3 | 100 | 30.8 | 10 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D40 (Optional) | 600 | 3 | 100 | 30.8 | 10 | 208, 3 | 208, 3 | 100 | 30.8 | 10 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 85 | 30.8 | 10 | 208, 3 | 208, 3 | 100 | 30.8 | 10 | 4620 | 1, 6, 7a
SE105126 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36050 | 600 | 3 | 125 | 50 | - | 240 | 3 | 100 | 28 | 10 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D32Y | 600 | 3 | - | 28 | 10 | 240, 3 | 240, 3 | 100 | 28 | 10 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 85 | 28 | 10 | 240, 3 | 240, 3 | 100 | 28 | 10 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 85 | 22 | 7.5 | 240, 3 | 240, 3 | 100 | 28 | 10 | 4620 | 1, 6, 7a
SE105127 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36025 | 600 | 3 | 100 | 25 | - | 480 | 3 | 100 | 14 | 10 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D17Y | 600 | 3 | - | 14 | 10 | 480, 3 | 480, 3 | 100 | 14 | 10 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 85 | 21 | 15 | 480, 3 | 480, 3 | 100 | 14 | 10 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 85 | 21 | 15 | 480, 3 | 480, 3 | 100 | 14 | 10 | 4620 | 1, 6, 7a
SE105128 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36110 | 600 | 3 | 125 | 110 | - | 208 | 3 | 100 | 46.2 | 15 | 4620 | 1, 6, 7b, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D62Y | 600 | 3 | - | 46.2 | 15 | 208, 3 | 208, 3 | 100 | 46.2 | 15 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 100 | 46.2 | 15 | 208, 3 | 208, 3 | 100 | 46.2 | 15 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 5 | 46.2 | 15 | 208, 3 | 208, 3 | 100 | 46.2 | 15 | 4620 | 1, 6, 7b
SE105129 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36080 | 600 | 3 | 125 | 80 | - | 240 | 3 | 100 | 42 | 15 | 4620 | 1, 6, 7k, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D47Y | 600 | 3 | - | 42 | 15 | 240, 3 | 240, 3 | 100 | 42 | 15 | 4620 | 1, 6, 7k
[10 empty] | (ISO) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 100 | 42 | 15 | 240, 3 | 240, 3 | 100 | 42 | 15 | 4620 | 1, 6, 7k
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 5 | 42 | 15 | 240, 3 | 240, 3 | 100 | 42 | 15 | 4620 | 1, 6, 7k
SE105130 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36040 | 600 | 3 | 100 | 40 | - | 480 | 3 | 100 | 21 | 15 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D22Y | 600 | 3 | - | 21 | 15 | 480, 3 | 480, 3 | 100 | 21 | 15 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 85 | 21 | 15 | 480, 3 | 480, 3 | 100 | 21 | 15 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 85 | 21 | 15 | 480, 3 | 480, 3 | 100 | 21 | 15 | 4620 | 1, 6, 7a
SE105131 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36060& | 600 | 3 | 50 | 60 | - | 600 | 3 | 50 | 17 | 15 | 4620 | 1, 6, 7a, 8, 9, 11, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba | ATS480D17Y | 600 | 3 | - | 17 | 15
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 50 | 22 | 20
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 50 | 22 | 20
SE105132 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36110 | 600 | 3 | 125 | 110 | - | 208 | 3 | 100 | 59.4 | 20 | 4620 | 1, 6, 7b, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D75Y | 600 | 3 | - | 59.4 | 20 | 208, 3 | 208, 3 | 100 | 59.4 | 20 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Schneider Electric | LC1D65 (Optional) | 600 | 3 | 100 | 59.4 | 20 | 208, 3 | 208, 3 | 100 | 59.4 | 20 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 100 | 46.2 | 15 | 208, 3 | 208, 3 | 100 | 59.4 | 20 | 4620 | 1, 6, 7b
SE105133 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36110 | 600 | 3 | 125 | 110 | - | 240 | 3 | 100 | 54 | 20 | 4620 | 1, 6, 7b, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D62Y | 600 | 3 | - | 54 | 20 | 240, 3 | 240, 3 | 100 | 54 | 20 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Schneider Electric | LC1D65 (Optional) | 600 | 3 | 100 | 54 | 20 | 240, 3 | 240, 3 | 100 | 54 | 20 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Schneider Electric | LC1D40 (Optional) | 600 | 3 | 100 | 28 | 10 | 240, 3 | 240, 3 | 100 | 54 | 20 | 4620 | 1, 6, 7b
SE105134 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36050 | 600 | 3 | 100 | 50 | - | 480 | 3 | 100 | 27 | 20 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D32Y | 600 | 3 | - | 27 | 20 | 480, 3 | 480, 3 | 100 | 27 | 20 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 85 | 27 | 20 | 480, 3 | 480, 3 | 100 | 27 | 20 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 85 | 21 | 15 | 480, 3 | 480, 3 | 100 | 27 | 20 | 4620 | 1, 6, 7a
SE105135 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36060& | 600 | 3 | 50 | 60 | - | 600 | 3 | 50 | 22 | 20 | 4620 | 1, 6, 7a, 8, 9, 11, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D22Y | 600 | 3 | - | 22 | 20 | 480, 3 | 480, 3 | 100 | 21 | 15 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 50 | 22 | 20 | 480, 3 | 480, 3 | 100 | 21 | 15 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 50 | 22 | 20 | 480, 3 | 480, 3 | 100 | 21 | 15 | 4620 | 1, 6, 7a
SE105136 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36110 | 600 | 3 | 125 | 110 | - | 208 | 3 | 100 | 74.8 | 25 | 4620 | 1, 6, 7l, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D88Y | 600 | 3 | - | 74.8 | 25 | 208, 3 | 208, 3 | 100 | 74.8 | 25 | 4620 | 1, 6, 7L
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 88 | 30 | 208, 3 | 208, 3 | 100 | 74.8 | 25 | 4620 | 1, 6, 7L
[10 empty] | (SHORT) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 100 | 46.2 | 15 | 208, 3 | 208, 3 | 100 | 74.8 | 25 | 4620 | 1, 6, 7L
SE105137 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36110 | 600 | 3 | 125 | 110 | - | 240 | 3 | 100 | 68 | 25 | 4620 | 1, 6, 7b, 8, 9, 10, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D75Y | 600 | 3 | - | 68 | 25 | 240, 3 | 240, 3 | 100 | 68 | 25 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 100 | 80 | 30 | 240, 3 | 240, 3 | 100 | 68 | 25 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 100 | 42 | 15 | 240, 3 | 240, 3 | 100 | 68 | 25 | 4620 | 1, 6, 7b
SE105138 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36060 | 600 | 3 | 100 | 60 | - | 480 | 3 | 100 | 34 | 25 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D38Y | 600 | 3 | - | 34 | 25 | 480, 3 | 480, 3 | 100 | 34 | 25 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D40 (Optional) | 600 | 3 | 100 | 40 | 30 | 480, 3 | 480, 3 | 100 | 34 | 25 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 85 | 27 | 20 | 480, 3 | 480, 3 | 100 | 34 | 25 | 4620 | 1, 6, 7a
SE105139 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36060& | 600 | 3 | 50 | 60 | - | 600 | 3 | 50 | 27 | 25 | 4620 | 1, 6, 7a, 8, 9, 11, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D32Y | 600 | 3 | - | 27 | 25 | 480, 3 | 480, 3 | 100 | 27 | 20 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 50 | 27 | 25 | 480, 3 | 480, 3 | 100 | 27 | 20 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 50 | 22 | 20 | 480, 3 | 480, 3 | 100 | 27 | 20 | 4620 | 1, 6, 7a
SE105140 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36125 | 600 | 3 | 125 | 125 | - | 208 | 3 | 100 | 88 | 30 | 4620 | 1, 6, 7m, 8, 9, 10, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C11Y | 600 | 3 | - | 88 | 30 | 208, 3 | 208, 3 | 100 | 88 | 30 | 4620 | 1, 6, 7m
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 88 | 30 | 208, 3 | 208, 3 | 100 | 88 | 30 | 4620 | 1, 6, 7m
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 100 | 74.8 | 25 | 208, 3 | 208, 3 | 100 | 88 | 30 | 4620 | 1, 6, 7m
SE105141 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36110 | 600 | 3 | 125 | 110 | - | 240 | 3 | 100 | 80 | 30 | 4620 | 1, 6, 7l, 8, 9, 10, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D88Y | 600 | 3 | - | 80 | 30 | 240, 3 | 240, 3 | 100 | 80 | 30 | 4620 | 1, 6, 7L
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 104 | 40 | 240, 3 | 240, 3 | 100 | 80 | 30 | 4620 | 1, 6, 7L
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 100 | 80 | 30 | 240, 3 | 240, 3 | 100 | 80 | 30 | 4620 | 1, 6, 7L
SE105142 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36080 | 600 | 3 | 100 | 80 | - | 480 | 3 | 100 | 40 | 30 | 4620 | 1, 6, 7k, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D47Y | 600 | 3 | - | 40 | 30 | 480, 3 | 480, 3 | 100 | 40 | 30 | 4620 | 1, 6, 7k
[10 empty] | (ISO) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 100 | 52 | 40 | 480, 3 | 480, 3 | 100 | 40 | 30 | 4620 | 1, 6, 7k
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 5 | 27 | 20 | 480, 3 | 480, 3 | 100 | 40 | 30 | 4620 | 1, 6, 7k
SE105143 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36080 | 600 | 3 | 50 | 80 | - | 600 | 3 | 50 | 32 | 30 | 4620 | 1, 6, 7a, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D38Y | 600 | 3 | - | 32 | 30 | 480, 3 | 480, 3 | 100 | 34 | 25 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D40 (Optional) | 600 | 3 | 50 | 32 | 30 | 480, 3 | 480, 3 | 100 | 34 | 25 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 5 | 27 | 25 | 480, 3 | 480, 3 | 100 | 34 | 25 | 4620 | 1, 6, 7a
SE105144 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | C | CB | Square D | JLx36175 | 600 | 3 | 125 | 175 | - | 208 | 3 | 100 | 114 | 40 | 6468 | 1, 6, 7n, 8, 9, 10, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C14Y | 600 | 3 | - | 114 | 40 | 208, 3 | 208, 3 | 100 | 114 | 40 | 4620 | 1, 6, 7n
[10 empty] | (ISO) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 100 | 114 | 40 | 208, 3 | 208, 3 | 100 | 114 | 40 | 4620 | 1, 6, 7n
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 5 | 74.8 | 25 | 208, 3 | 208, 3 | 100 | 114 | 40 | 4620 | 1, 6, 7n
SE105145 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36150 | 600 | 3 | 125 | 150 | - | 240 | 3 | 100 | 104 | 40 | 4620 | 1, 6, 7m, 8, 9, 10, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C11Y | 600 | 3 | - | 104 | 40 | 240, 3 | 240, 3 | 100 | 104 | 40 | 4620 | 1, 6, 7m
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 104 | 40 | 240, 3 | 240, 3 | 100 | 104 | 40 | 4620 | 1, 6, 7m
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 100 | 80 | 30 | 240, 3 | 240, 3 | 100 | 104 | 40 | 4620 | 1, 6, 7m
SE105146 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36110 | 600 | 3 | 100 | 110 | - | 480 | 3 | 100 | 52 | 40 | 4620 | 1, 6, 7b, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D62Y | 600 | 3 | - | 52 | 40 | 480, 3 | 480, 3 | 100 | 52 | 40 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Schneider Electric | LC1D65 (Optional) | 600 | 3 | 100 | 52 | 40 | 480, 3 | 480, 3 | 100 | 52 | 40 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Schneider Electric | LC1D40 (Optional) | 600 | 3 | 100 | 40 | 30 | 480, 3 | 480, 3 | 100 | 52 | 40 | 4620 | 1, 6, 7b
SE105147 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36100 | 600 | 3 | 50 | 100 | - | 600 | 3 | 50 | 41 | 40 | 4620 | 1, 6, 7k, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D47Y | 600 | 3 | - | 41 | 40 | 480, 3 | 480, 3 | 100 | 40 | 30 | 4620 | 1, 6, 7k
[10 empty] | (ISO) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 50 | 41 | 40 | 480, 3 | 480, 3 | 100 | 40 | 30 | 4620 | 1, 6, 7k
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 5 | 27 | 25 | 480, 3 | 480, 3 | 100 | 40 | 30 | 4620 | 1, 6, 7k
SE105148 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | C | CB | Square D | JLx36200 | 600 | 3 | 125 | 200 | - | 208 | 3 | 100 | 143 | 50 | 6468 | 1, 6, 7c, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C17Y | 600 | 3 | - | 143 | 50 | 208, 3 | 208, 3 | 100 | 143 | 50 | 4620 | 1, 6, 7c
[10 empty] | (ISO) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 65 | 143 | 50 | 208, 3 | 208, 3 | 100 | 143 | 50 | 4620 | 1, 6, 7c
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 88 | 30 | 208, 3 | 208, 3 | 100 | 143 | 50 | 4620 | 1, 6, 7c
SE105149 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | C | CB | Square D | JLx36200 | 600 | 3 | 125 | 200 | - | 240 | 3 | 100 | 130 | 50 | 6468 | 1, 6, 7n, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C14Y | 600 | 3 | - | 130 | 50 | 240, 3 | 240, 3 | 100 | 130 | 50 | 4620 | 1, 6, 7n
[10 empty] | (ISO) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 100 | 130 | 50 | 240, 3 | 240, 3 | 100 | 130 | 50 | 4620 | 1, 6, 7n
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 104 | 40 | 240, 3 | 240, 3 | 100 | 130 | 50 | 4620 | 1, 6, 7n
SE105150 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36110 | 600 | 3 | 100 | 110 | - | 480 | 3 | 100 | 65 | 50 | 4620 | 1, 6, 7b, 8, 9, 10, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D75Y | 600 | 3 | - | 65 | 50 | 480, 3 | 480, 3 | 100 | 65 | 50 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 100 | 52 | 40 | 480, 3 | 480, 3 | 100 | 65 | 50 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 100 | 52 | 40 | 480, 3 | 480, 3 | 100 | 65 | 50 | 4620 | 1, 6, 7b
SE105151 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36100 | 600 | 3 | 50 | 100 | - | 600 | 3 | 50 | 52 | 50 | 4620 | 1, 6, 7b, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D62Y | 600 | 3 | - | 52 | 50 | 480, 3 | 480, 3 | 100 | 52 | 40 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Schneider Electric | LC1D65 (Optional) | 600 | 3 | 50 | 52 | 50 | 480, 3 | 480, 3 | 100 | 52 | 40 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Schneider Electric | LC1D40 (Optional) | 600 | 3 | 50 | 32 | 30 | 480, 3 | 480, 3 | 100 | 52 | 40 | 4620 | 1, 6, 7b
SE105152 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36400 | 600 | 3 | 125 | 400 | - | 208 | 3 | 100 | 169 | 60 | 28800 | 1, 6, 7d, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C21Y | 600 | 3 | - | 169 | 60 | 208, 3 | 208, 3 | 100 | 169 | 60 | 4620 | 1, 6, 7d
[10 empty] | (ISO) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 65 | 143 | 50 | 208, 3 | 208, 3 | 100 | 169 | 60 | 4620 | 1, 6, 7d
[10 empty] | (SHORT) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 10 | 114 | 40 | 208, 3 | 208, 3 | 100 | 169 | 60 | 4620 | 1, 6, 7d
SE105153 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | C | CB | Square D | JLx36225 | 600 | 3 | 125 | 225 | - | 240 | 3 | 100 | 154 | 60 | 6468 | 1, 6, 7c, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C17Y | 600 | 3 | - | 154 | 60 | 240, 3 | 240, 3 | 100 | 154 | 60 | 4620 | 1, 6, 7c
[10 empty] | (ISO) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 65 | 154 | 60 | 240, 3 | 240, 3 | 100 | 154 | 60 | 4620 | 1, 6, 7c
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 104 | 40 | 240, 3 | 240, 3 | 100 | 154 | 60 | 4620 | 1, 6, 7c
SE105154 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36110 | 600 | 3 | 100 | 110 | - | 480 | 3 | 100 | 77 | 60 | 4620 | 1, 6, 7l, 8, 9, 10, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D88Y | 600 | 3 | - | 77 | 60 | 480, 3 | 480, 3 | 100 | 77 | 60 | 4620 | 1, 6, 7L
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 96 | 75 | 480, 3 | 480, 3 | 100 | 77 | 60 | 4620 | 1, 6, 7L
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 100 | 77 | 60 | 480, 3 | 480, 3 | 100 | 77 | 60 | 4620 | 1, 6, 7L
SE105155 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36150 | 600 | 3 | 50 | 150 | - | 600 | 3 | 50 | 62 | 60 | 4620 | 1, 6, 7b, 8, 9, 10, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D75Y | 600 | 3 | - | 62 | 60 | 480, 3 | 480, 3 | 100 | 65 | 50 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 50 | 62 | 60 | 480, 3 | 480, 3 | 100 | 65 | 50 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 5 | 41 | 40 | 480, 3 | 480, 3 | 100 | 65 | 50 | 4620 | 1, 6, 7b
SE105156 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36400 | 600 | 3 | 125 | 400 | - | 208 | 3 | 100 | 211 | 75 | 28800 | 1, 6, 7p, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C25Y | 600 | 3 | - | 211 | 75 | 208, 3 | 208, 3 | 100 | 211 | 75 | 4620 | 1, 6, 7p
[10 empty] | (ISO) MC | Schneider Electric | LC1F225 (Optional) | 600 | 3 | 10 | 169 | 60 | 208, 3 | 208, 3 | 100 | 211 | 75 | 4620 | 1, 6, 7p
[10 empty] | (SHORT) MC | Schneider Electric | LC1F225 (Optional) | 600 | 3 | 10 | 169 | 60 | 208, 3 | 208, 3 | 100 | 211 | 75 | 4620 | 1, 6, 7p
SE105157 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36400 | 600 | 3 | 125 | 400 | - | 240 | 3 | 100 | 192 | 75 | 28800 | 1, 6, 7d, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C21Y | 600 | 3 | - | 192 | 75 | 240, 3 | 240, 3 | 100 | 192 | 75 | 4620 | 1, 6, 7d
[10 empty] | (ISO) MC | Schneider Electric | LC1F225 (Optional) | 600 | 3 | 10 | 192 | 75 | 240, 3 | 240, 3 | 100 | 192 | 75 | 4620 | 1, 6, 7d
[10 empty] | (SHORT) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 10 | 130 | 50 | 240, 3 | 240, 3 | 100 | 192 | 75 | 4620 | 1, 6, 7d
SE105158 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36125 | 600 | 3 | 100 | 125 | - | 480 | 3 | 100 | 96 | 75 | 4620 | 1, 6, 7m, 8, 9, 10, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C11Y | 600 | 3 | - | 96 | 75 | 480, 3 | 480, 3 | 100 | 96 | 75 | 4620 | 1, 6, 7m
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 96 | 75 | 480, 3 | 480, 3 | 100 | 96 | 75 | 4620 | 1, 6, 7m
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 100 | 77 | 60 | 480, 3 | 480, 3 | 100 | 96 | 75 | 4620 | 1, 6, 7m
SE105159 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36150 | 600 | 3 | 50 | 150 | - | 600 | 3 | 50 | 77 | 75 | 4620 | 1, 6, 7l, 8, 9, 10, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D88Y | 600 | 3 | - | 77 | 75 | 480, 3 | 480, 3 | 100 | 77 | 60 | 4620 | 1, 6, 7L
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 50 | 99 | 100 | 480, 3 | 480, 3 | 100 | 77 | 60 | 4620 | 1, 6, 7L
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 50 | 62 | 60 | 480, 3 | 480, 3 | 100 | 77 | 60 | 4620 | 1, 6, 7L
SE105160 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36600 | 600 | 3 | 125 | 600 | - | 208 | 3 | 100 | 273 | 100 | 28800 | 1, 6, 7h, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C32Y | 600 | 3 | - | 273 | 100 | 208, 3 | 208, 3 | 100 | 273 | 100 | 4620 | 1, 6, 7h
[10 empty] | (ISO) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 18 | 211 | 75 | 208, 3 | 208, 3 | 100 | 273 | 100 | 4620 | 1, 6, 7h
[10 empty] | (SHORT) MC | Schneider Electric | LC1F265 (Optional) | 600 | 3 | 10 | 169 | 60 | 208, 3 | 208, 3 | 100 | 273 | 100 | 4620 | 1, 6, 7h
SE105161 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36600 | 600 | 3 | 125 | 600 | - | 240 | 3 | 100 | 248 | 100 | 28800 | 1, 6, 7h, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C25Y | 600 | 3 | - | 248 | 100 | 240, 3 | 240, 3 | 100 | 248 | 100 | 4620 | 1, 6, 7h
[10 empty] | (ISO) MC | Schneider Electric | LC1F265 (Optional) | 600 | 3 | 10 | 192 | 75 | 240, 3 | 240, 3 | 100 | 248 | 100 | 4620 | 1, 6, 7h
[10 empty] | (SHORT) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 10 | 154 | 60 | 240, 3 | 240, 3 | 100 | 248 | 100 | 4620 | 1, 6, 7h
SE105162 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | C | CB | Square D | JLx36200 | 600 | 3 | 100 | 200 | - | 480 | 3 | 100 | 124 | 100 | 6468 | 1, 6, 7n, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C14Y | 600 | 3 | - | 124 | 100 | 480, 3 | 480, 3 | 100 | 124 | 100 | 4620 | 1, 6, 7n
[10 empty] | (ISO) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 100 | 124 | 100 | 480, 3 | 480, 3 | 100 | 124 | 100 | 4620 | 1, 6, 7n
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 96 | 75 | 480, 3 | 480, 3 | 100 | 124 | 100 | 4620 | 1, 6, 7n
SE105163 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | C | CB | Square D | HLx36150 | 600 | 3 | 50 | 150 | - | 600 | 3 | 50 | 99 | 100 | 4620 | 1, 6, 7m, 8, 9, 10, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C11Y | 600 | 3 | - | 99 | 100 | 480, 3 | 480, 3 | 100 | 96 | 75 | 4620 | 1, 6, 7m
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 50 | 99 | 100 | 480, 3 | 480, 3 | 100 | 96 | 75 | 4620 | 1, 6, 7m
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 50 | 62 | 60 | 480, 3 | 480, 3 | 100 | 96 | 75 | 4620 | 1, 6, 7m
SE105164 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 35 | 20 | C | CB | Square D | PLx34060 | 480 | 3 | 125 | 600 | - | 208 | 3 | 100 | 343 | 125 | 50400 | 1, 6, 7i, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C41Y | 600 | 3 | - | 343 | 125 | 208, 3 | 208, 3 | 100 | 343 | 125 | 4620 | 1, 6, 7i
[10 empty] | (ISO) MC | Schneider Electric | LC1F400 (Optional) | 600 | 3 | 18 | 273 | 100 | 208, 3 | 208, 3 | 100 | 343 | 125 | 4620 | 1, 6, 7i
[10 empty] | (SHORT) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 18 | 211 | 75 | 208, 3 | 208, 3 | 100 | 343 | 125 | 4620 | 1, 6, 7i
SE105165 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | PLx34060 | 480 | 3 | 125 | 600 | - | 240 | 3 | 100 | 312 | 125 | 28800 | 1, 6, 7i, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C32Y | 600 | 3 | - | 312 | 125 | 240, 3 | 240, 3 | 100 | 312 | 125 | 4620 | 1, 6, 7i
[10 empty] | (ISO) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 18 | 248 | 100 | 240, 3 | 240, 3 | 100 | 312 | 125 | 4620 | 1, 6, 7i
[10 empty] | (SHORT) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 18 | 248 | 100 | 240, 3 | 240, 3 | 100 | 312 | 125 | 4620 | 1, 6, 7i
SE105166 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | C | CB | Square D | JLx36225 | 600 | 3 | 100 | 225 | - | 480 | 3 | 100 | 156 | 125 | 6468 | 1, 6, 7c, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C17Y | 600 | 3 | - | 156 | 125 | 480, 3 | 480, 3 | 100 | 156 | 125 | 4620 | 1, 6, 7c
[10 empty] | (ISO) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 65 | 156 | 125 | 480, 3 | 480, 3 | 100 | 156 | 125 | 4620 | 1, 6, 7c
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 100 | 96 | 75 | 480, 3 | 480, 3 | 100 | 156 | 125 | 4620 | 1, 6, 7c
SE105167 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | C | CB | Square D | JLx36225 | 600 | 3 | 50 | 225 | - | 600 | 3 | 50 | 125 | 125 | 6468 | 1, 6, 7n, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C14Y | 600 | 3 | - | 125 | 125 | 480, 3 | 480, 3 | 100 | 124 | 100 | 4620 | 1, 6, 7n
[10 empty] | (ISO) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 50 | 125 | 125 | 480, 3 | 480, 3 | 100 | 124 | 100 | 4620 | 1, 6, 7n
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 50 | 99 | 100 | 480, 3 | 480, 3 | 100 | 124 | 100 | 4620 | 1, 6, 7n
SE105168 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 35 | 20 | C | CB | Square D | PLx34060 | 480 | 3 | 125 | 600 | - | 208 | 3 | 100 | 396 | 150 | 50400 | 1, 6, 7e, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C48Y | 600 | 3 | - | 396 | 150 | 208, 3 | 208, 3 | 100 | 396 | 150 | 4620 | 1, 6, 7e
[10 empty] | (ISO) MC | Schneider Electric | LC1F500 (Optional) | 600 | 3 | 30 | 396 | 150 | 208, 3 | 208, 3 | 100 | 396 | 150 | 4620 | 1, 6, 7e
[10 empty] | (SHORT) MC | Schneider Electric | LC1F400 (Optional) | 600 | 3 | 18 | 273 | 100 | 208, 3 | 208, 3 | 100 | 396 | 150 | 4620 | 1, 6, 7e
SE105169 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 35 | 20 | C | CB | Square D | PLx34060 | 480 | 3 | 125 | 600 | - | 240 | 3 | 100 | 360 | 150 | 50400 | 1, 6, 7e, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C41Y | 600 | 3 | - | 360 | 150 | 240, 3 | 240, 3 | 100 | 360 | 150 | 4620 | 1, 6, 7e
[10 empty] | (ISO) MC | Schneider Electric | LC1F400 (Optional) | 600 | 3 | 18 | 312 | 125 | 240, 3 | 240, 3 | 100 | 360 | 150 | 4620 | 1, 6, 7e
[10 empty] | (SHORT) MC | Schneider Electric | LC1F400 (Optional) | 600 | 3 | 18 | 312 | 125 | 240, 3 | 240, 3 | 100 | 360 | 150 | 4620 | 1, 6, 7e
SE105170 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36400 | 600 | 3 | 100 | 400 | - | 480 | 3 | 100 | 180 | 150 | 28800 | 1, 6, 7d, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C21Y | 600 | 3 | - | 180 | 150 | 480, 3 | 480, 3 | 100 | 180 | 150 | 4620 | 1, 6, 7d
[10 empty] | (ISO) MC | Schneider Electric | LC1F225 (Optional) | 600 | 3 | 10 | 180 | 150 | 480, 3 | 480, 3 | 100 | 180 | 150 | 4620 | 1, 6, 7d
[10 empty] | (SHORT) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 10 | 124 | 100 | 480, 3 | 480, 3 | 100 | 180 | 150 | 4620 | 1, 6, 7d
SE105171 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | C | CB | Square D | JLx36225 | 600 | 3 | 50 | 225 | - | 600 | 3 | 50 | 144 | 150 | 6468 | 1, 6, 7c, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C17Y | 600 | 3 | - | 144 | 150 | 480, 3 | 480, 3 | 100 | 156 | 125 | 4620 | 1, 6, 7c
[10 empty] | (ISO) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 10 | 144 | 150 | 480, 3 | 480, 3 | 100 | 156 | 125 | 4620 | 1, 6, 7c
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 50 | 99 | 100 | 480, 3 | 480, 3 | 100 | 156 | 125 | 4620 | 1, 6, 7c
SE105172 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 35 | 20 | C | CB | Square D | PLx34080 | 480 | 3 | 125 | 800 | - | 208 | 3 | 100 | 528 | 200 | 50400 | 1, 6, 7q, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C66Y | 600 | 3 | - | 528 | 200 | 208, 3 | 208, 3 | 100 | 10.6 | 3 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1F630 (Optional) | 600 | 3 | 42 | 660 | 250 | 208, 3 | 208, 3 | 100 | 10.6 | 3 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1F500 (Optional) | 600 | 3 | 30 | 396 | 150 | 208, 3 | 208, 3 | 100 | 10.6 | 3 | 4620 | 1, 6, 7a
SE105173 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 35 | 20 | C | CB | Square D | PLx34080 | 480 | 3 | 125 | 800 | - | 240 | 3 | 100 | 480 | 200 | 50400 | 1, 6, 7r, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C59Y | 600 | 3 | - | 480 | 200 | 240, 3 | 240, 3 | 100 | 480 | 200 | 4620 | 1, 6, 7r
[10 empty] | (ISO) MC | Schneider Electric | LC1F630 (Optional) | 600 | 3 | 42 | 722 | 300 | 240, 3 | 240, 3 | 100 | 480 | 200 | 4620 | 1, 6, 7r
[10 empty] | (SHORT) MC | Schneider Electric | LC1F500 (Optional) | 600 | 3 | 30 | 480 | 200 | 240, 3 | 240, 3 | 100 | 480 | 200 | 4620 | 1, 6, 7r
SE105174 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36600 | 600 | 3 | 100 | 600 | - | 480 | 3 | 100 | 240 | 200 | 28800 | 1, 6, 7h, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C25Y | 600 | 3 | - | 240 | 200 | 480, 3 | 480, 3 | 100 | 240 | 200 | 4620 | 1, 6, 7h
[10 empty] | (ISO) MC | Schneider Electric | LC1F265 (Optional) | 600 | 3 | 10 | 180 | 150 | 480, 3 | 480, 3 | 100 | 240 | 200 | 4620 | 1, 6, 7h
[10 empty] | (SHORT) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 10 | 156 | 125 | 480, 3 | 480, 3 | 100 | 240 | 200 | 4620 | 1, 6, 7h
SE105175 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36400 | 600 | 3 | 50 | 400 | - | 600 | 3 | 50 | 192 | 200 | 28800 | 1, 6, 7d, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C21Y | 600 | 3 | - | 192 | 200 | 480, 3 | 480, 3 | 100 | 180 | 150 | 4620 | 1, 6, 7d
[10 empty] | (ISO) MC | Schneider Electric | LC1F225 (Optional) | 600 | 3 | 10 | 144 | 150 | 480, 3 | 480, 3 | 100 | 180 | 150 | 4620 | 1, 6, 7d
[10 empty] | (SHORT) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 10 | 125 | 125 | 480, 3 | 480, 3 | 100 | 180 | 150 | 4620 | 1, 6, 7d
SE105176 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 35 | 20 | C | CB | Square D | PLx34100 | 480 | 3 | 125 | 1000 | - | 240 | 3 | 100 | 604 | 250 | 50400 | 1, 6, 7q, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C66Y | 600 | 3 | - | 604 | 250 | 208, 3 | 208, 3 | 100 | 10.6 | 3 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1F630 (Optional) | 600 | 3 | 42 | 722 | 300 | 208, 3 | 208, 3 | 100 | 10.6 | 3 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1F630 (Optional) | 600 | 3 | 42 | 722 | 300 | 208, 3 | 208, 3 | 100 | 10.6 | 3 | 4620 | 1, 6, 7a
SE105177 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36600 | 600 | 3 | 100 | 600 | - | 480 | 3 | 100 | 302 | 250 | 28800 | 1, 6, 7s, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C32Y | 600 | 3 | - | 302 | 250 | 480, 3 | 480, 3 | 100 | 302 | 250 | 4620 | 1, 6, 7s
[10 empty] | (ISO) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 18 | 240 | 200 | 480, 3 | 480, 3 | 100 | 302 | 250 | 4620 | 1, 6, 7s
[10 empty] | (SHORT) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 18 | 240 | 200 | 480, 3 | 480, 3 | 100 | 302 | 250 | 4620 | 1, 6, 7s
SE105178 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36600 | 600 | 3 | 50 | 600 | - | 600 | 3 | 50 | 242 | 250 | 28800 | 1, 6, 7h, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C25Y | 600 | 3 | - | 242 | 250 | 480, 3 | 480, 3 | 100 | 240 | 200 | 4620 | 1, 6, 7h
[10 empty] | (ISO) MC | Schneider Electric | LC1F265 (Optional) | 600 | 3 | 10 | 192 | 200 | 480, 3 | 480, 3 | 100 | 240 | 200 | 4620 | 1, 6, 7h
[10 empty] | (SHORT) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 10 | 144 | 150 | 480, 3 | 480, 3 | 100 | 240 | 200 | 4620 | 1, 6, 7h
SE105179 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 35 | 20 | C | CB | Square D | PLx34060 | 480 | 3 | 100 | 600 | - | 480 | 3 | 100 | 361 | 300 | 50400 | 1, 6, 7e, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C41Y | 600 | 3 | - | 361 | 300 | 480, 3 | 480, 3 | 100 | 361 | 300 | 4620 | 1, 6, 7e
[10 empty] | (ISO) MC | Schneider Electric | LC1F400 (Optional) | 600 | 3 | 18 | 302 | 250 | 480, 3 | 480, 3 | 100 | 361 | 300 | 4620 | 1, 6, 7e
[10 empty] | (SHORT) MC | Schneider Electric | LC1F400 (Optional) | 600 | 3 | 18 | 302 | 250 | 480, 3 | 480, 3 | 100 | 361 | 300 | 4620 | 1, 6, 7e
SE105180 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | C | CB | Square D | LLx36600 | 600 | 3 | 50 | 600 | - | 600 | 3 | 50 | 289 | 300 | 28800 | 1, 6, 7s, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C32Y | 600 | 3 | - | 289 | 300 | 480, 3 | 480, 3 | 100 | 302 | 250 | 4620 | 1, 6, 7s
[10 empty] | (ISO) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 18 | 242 | 250 | 480, 3 | 480, 3 | 100 | 302 | 250 | 4620 | 1, 6, 7s
[10 empty] | (SHORT) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 18 | 242 | 250 | 480, 3 | 480, 3 | 100 | 302 | 250 | 4620 | 1, 6, 7s
SE105181 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 35 | 20 | C | CB | Square D | PLx34060 | 480 | 3 | 100 | 600 | - | 480 | 3 | 100 | 414 | 350 | 50400 | 1, 6, 7f, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C48Y | 600 | 3 | - | 414 | 350 | 480, 3 | 480, 3 | 100 | 414 | 350 | 4620 | 1, 6, 7f
[10 empty] | (ISO) MC | Schneider Electric | LC1F500 (Optional) | 600 | 3 | 30 | 477 | 400 | 480, 3 | 480, 3 | 100 | 414 | 350 | 4620 | 1, 6, 7f
[10 empty] | (SHORT) MC | Schneider Electric | LC1F400 (Optional) | 600 | 3 | 18 | 302 | 250 | 480, 3 | 480, 3 | 100 | 414 | 350 | 4620 | 1, 6, 7f
SE105182 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 35 | 20 | C | CB | Square D | PLx34080 | 480 | 3 | 100 | 800 | - | 480 | 3 | 100 | 477 | 400 | 50400 | 1, 6, 7r, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C59Y | 600 | 3 | - | 477 | 400 | 480, 3 | 480, 3 | 100 | 477 | 400 | 4620 | 1, 6, 7r
[10 empty] | (ISO) MC | Schneider Electric | LC1F630 (Optional) | 600 | 3 | - | 722 | 600 | 480, 3 | 480, 3 | 100 | 477 | 400 | 4620 | 1, 6, 7r
[10 empty] | (SHORT) MC | Schneider Electric | LC1F500 (Optional) | 600 | 3 | 18 | 477 | 400 | 480, 3 | 480, 3 | 100 | 477 | 400 | 4620 | 1, 6, 7r
SE105183 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 35 | 20 | C | CB | Square D | PLx34100 | 480 | 3 | 100 | 1000 | - | 480 | 3 | 100 | 590 | 500 | 50400 | 1, 6, 7q, 8, 9, 12, 13 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C66Y | 600 | 3 | - | 590 | 500 | 208, 3 | 208, 3 | 100 | 10.6 | 3 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1F630 (Optional) | 600 | 3 | 42 | 722 | 600 | 208, 3 | 208, 3 | 100 | 10.6 | 3 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1F630 (Optional) | 600 | 3 | 42 | 722 | 600 | 208, 3 | 208, 3 | 100 | 10.6 | 3 | 4620 | 1, 6, 7a

## ATS480-Type D-IEC
Issued: 2023-01-14
Last Revised: 2023-01-14
Database Identification Number | Listed Combination Motor Controller Information | [7 empty] | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | Conditions of Use | Schematic | Other References
| Listing Report Information |  |  |  |  | Enclosure or Unit Dimensions
| UL File Number | Report Issue Date YYYY-MM-DD | Volume / Section (Vol#).(Sec#) | Model Number or Product Style/ Designation | Product Description on Page/Figure/Ill. | Enclosure or Unit Height, inches | Width, inches | Depth, inches |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | HP Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | HP Rating
SE105190 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36030M | 600 | 3 | - | 30 | - | 208 | 3 | 100 | 10.6 | 3 | 4620 | 1, 5, 6, 7a, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba | ATS480D17Y | 600 | 3 | - | 10.6 | 3
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 24.2 | 7.5
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 24.2 | 7.5
SE105191 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | IICB | Square D | HLL36030M | 600 | 3 | - | 30 | - | 208 | 3 | 100 | 16.7 | 5 | 4620 | 1, 5, 6, 7a, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D22Y | 600 | 3 | - | 16.7 | 5 | 208, 3 | 208, 3 | 100 | 16.7 | 5 | 4620
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 24.2 | 7.5 | 208, 3 | 208, 3 | 100 | 16.7 | 5 | 4620
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 24.2 | 7.5 | 208, 3 | 208, 3 | 100 | 16.7 | 5 | 4620
SE105192 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36030M | 600 | 3 | - | 30 | - | 240 | 3 | 100 | 15.2 | 5 | 4620 | 1, 5, 6, 7a, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D17Y | 600 | 3 | - | 15.2 | 5 | 240, 3 | 240, 3 | 100 | 15.2 | 5 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 22 | 7.5 | 240, 3 | 240, 3 | 100 | 15.2 | 5 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 22 | 7.5 | 240, 3 | 240, 3 | 100 | 15.2 | 5 | 4620 | 1, 6, 7a
SE105193 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36050M | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 24.2 | 7.5 | 4620 | 1, 5, 6, 7a, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D32Y | 600 | 3 | - | 24.2 | 7.5 | 208, 3 | 208, 3 | 100 | 24.2 | 7.5 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 5 | 30.8 | 10 | 208, 3 | 208, 3 | 100 | 24.2 | 7.5 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 24.2 | 7.5 | 208, 3 | 208, 3 | 100 | 24.2 | 7.5 | 4620 | 1, 6, 7a
SE105194 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36050M | 600 | 3 | - | 50 | - | 240 | 3 | 100 | 22 | 7.5 | 4620 | 1, 5, 6, 7a, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D22Y | 600 | 3 | - | 22 | 7.5 | 240, 3 | 240, 3 | 100 | 22 | 7.5 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 5 | 28 | 10 | 240, 3 | 240, 3 | 100 | 22 | 7.5 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 22 | 7.5 | 240, 3 | 240, 3 | 100 | 22 | 7.5 | 4620 | 1, 6, 7a
SE105195 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36050M | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 30.8 | 10 | 4620 | 1, 5, 6, 7a, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D38Y | 600 | 3 | - | 30.8 | 10 | 208, 3 | 208, 3 | 100 | 30.8 | 10 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D40 (Optional) | 600 | 3 | 5 | 30.8 | 10 | 208, 3 | 208, 3 | 100 | 30.8 | 10 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 5 | 30.8 | 10 | 208, 3 | 208, 3 | 100 | 30.8 | 10 | 4620 | 1, 6, 7a
SE105196 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36050M | 600 | 3 | - | 50 | - | 240 | 3 | 100 | 28 | 10 | 4620 | 1, 5, 6, 7a, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D32Y | 600 | 3 | - | 28 | 10 | 240, 3 | 240, 3 | 100 | 28 | 10 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 5 | 28 | 10 | 240, 3 | 240, 3 | 100 | 28 | 10 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 22 | 7.5 | 240, 3 | 240, 3 | 100 | 28 | 10 | 4620 | 1, 6, 7a
SE105197 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36030M | 600 | 3 | - | 30 | - | 480 | 3 | 100 | 14 | 10 | 4620 | 1, 5, 6, 7a, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D17Y | 600 | 3 | - | 14 | 10 | 480, 3 | 480, 3 | 100 | 14 | 10 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 21 | 15 | 480, 3 | 480, 3 | 100 | 14 | 10 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 21 | 15 | 480, 3 | 480, 3 | 100 | 14 | 10 | 4620 | 1, 6, 7a
SE105198 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36100M | 600 | 3 | - | 100 | - | 208 | 3 | 100 | 46.2 | 15 | 4620 | 1, 5, 6, 7b, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D62Y | 600 | 3 | - | 46.2 | 15 | 208, 3 | 208, 3 | 100 | 46.2 | 15 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 5 | 46.2 | 15 | 208, 3 | 208, 3 | 100 | 46.2 | 15 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 5 | 46.2 | 15 | 208, 3 | 208, 3 | 100 | 46.2 | 15 | 4620 | 1, 6, 7b
SE105199 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36100M | 600 | 3 | - | 100 | - | 240 | 3 | 100 | 42 | 15 | 4620 | 1, 5, 6, 7k, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D47Y | 600 | 3 | - | 42 | 15 | 240, 3 | 240, 3 | 100 | 42 | 15 | 4620 | 1, 6, 7k
[10 empty] | (ISO) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 5 | 42 | 15 | 240, 3 | 240, 3 | 100 | 42 | 15 | 4620 | 1, 6, 7k
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 5 | 42 | 15 | 240, 3 | 240, 3 | 100 | 42 | 15 | 4620 | 1, 6, 7k
SE105200 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36050M | 600 | 3 | - | 50 | - | 480 | 3 | 100 | 21 | 15 | 4620 | 1, 5, 6, 7a, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D22Y | 600 | 3 | - | 21 | 15 | 480, 3 | 480, 3 | 100 | 21 | 15 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 21 | 15 | 480, 3 | 480, 3 | 100 | 21 | 15 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 21 | 15 | 480, 3 | 480, 3 | 100 | 21 | 15 | 4620 | 1, 6, 7a
SE105201 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36030M | 600 | 3 | - | 30 | - | 600 | 3 | 50 | 17 | 15 | 4620 | 1, 5, 6, 7a, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba | ATS480D17Y | 600 | 3 | - | 17 | 15
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 22 | 20
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 22 | 20
SE105202 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36150M | 600 | 3 | - | 150 | - | 208 | 3 | 100 | 59.4 | 20 | 4620 | 1, 5, 6, 7b, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D75Y | 600 | 3 | - | 59.4 | 20 | 208, 3 | 208, 3 | 100 | 59.4 | 20 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Schneider Electric | LC1D65 (Optional) | 600 | 3 | 5 | 59.4 | 20 | 208, 3 | 208, 3 | 100 | 59.4 | 20 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 5 | 46.2 | 15 | 208, 3 | 208, 3 | 100 | 59.4 | 20 | 4620 | 1, 6, 7b
SE105203 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36100M | 600 | 3 | - | 100 | - | 240 | 3 | 100 | 54 | 20 | 4620 | 1, 5, 6, 7b, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D62Y | 600 | 3 | - | 54 | 20 | 240, 3 | 240, 3 | 100 | 54 | 20 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Schneider Electric | LC1D65 (Optional) | 600 | 3 | 5 | 54 | 20 | 240, 3 | 240, 3 | 100 | 54 | 20 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Schneider Electric | LC1D40 (Optional) | 600 | 3 | 5 | 28 | 10 | 240, 3 | 240, 3 | 100 | 54 | 20 | 4620 | 1, 6, 7b
SE105204 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36050M | 600 | 3 | - | 50 | - | 480 | 3 | 100 | 27 | 20 | 4620 | 1, 5, 6, 7a, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D32Y | 600 | 3 | - | 27 | 20 | 480, 3 | 480, 3 | 100 | 27 | 20 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 5 | 27 | 20 | 480, 3 | 480, 3 | 100 | 27 | 20 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 21 | 15 | 480, 3 | 480, 3 | 100 | 27 | 20 | 4620 | 1, 6, 7a
SE105205 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36030M | 600 | 3 | - | 30 | - | 600 | 3 | 50 | 22 | 20 | 4620 | 1, 5, 6, 7a, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D22Y | 600 | 3 | - | 22 | 20 | 480, 3 | 480, 3 | 100 | 21 | 15 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 22 | 20 | 480, 3 | 480, 3 | 100 | 21 | 15 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 22 | 20 | 480, 3 | 480, 3 | 100 | 21 | 15 | 4620 | 1, 6, 7a
SE105206 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36150M | 600 | 3 | - | 150 | - | 208 | 3 | 100 | 74.8 | 25 | 4620 | 1, 5, 6, 7l, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D88Y | 600 | 3 | - | 74.8 | 25 | 208, 3 | 208, 3 | 100 | 74.8 | 25 | 4620 | 1, 6, 7L
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 10 | 88 | 30 | 208, 3 | 208, 3 | 100 | 74.8 | 25 | 4620 | 1, 6, 7L
[10 empty] | (SHORT) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 5 | 46.2 | 15 | 208, 3 | 208, 3 | 100 | 74.8 | 25 | 4620 | 1, 6, 7L
SE105207 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36150M | 600 | 3 | - | 150 | - | 240 | 3 | 100 | 68 | 25 | 4620 | 1, 5, 6, 7b, 8, 9, 10, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D75Y | 600 | 3 | - | 68 | 25 | 240, 3 | 240, 3 | 100 | 68 | 25 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 5 | 80 | 30 | 240, 3 | 240, 3 | 100 | 68 | 25 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 5 | 42 | 15 | 240, 3 | 240, 3 | 100 | 68 | 25 | 4620 | 1, 6, 7b
SE105208 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36050M | 600 | 3 | - | 50 | - | 480 | 3 | 100 | 34 | 25 | 4620 | 1, 5, 6, 7a, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D38Y | 600 | 3 | - | 34 | 25 | 480, 3 | 480, 3 | 100 | 34 | 25 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D40 (Optional) | 600 | 3 | 5 | 40 | 30 | 480, 3 | 480, 3 | 100 | 34 | 25 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 5 | 27 | 20 | 480, 3 | 480, 3 | 100 | 34 | 25 | 4620 | 1, 6, 7a
SE105209 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36050M | 600 | 3 | - | 50 | - | 600 | 3 | 50 | 27 | 25 | 4620 | 1, 5, 6, 7a, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D32Y | 600 | 3 | - | 27 | 25 | 480, 3 | 480, 3 | 100 | 27 | 20 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 5 | 27 | 25 | 480, 3 | 480, 3 | 100 | 27 | 20 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D25 (Optional) | 600 | 3 | 5 | 22 | 20 | 480, 3 | 480, 3 | 100 | 27 | 20 | 4620 | 1, 6, 7a
SE105210 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36150M | 600 | 3 | - | 150 | - | 208 | 3 | 100 | 88 | 30 | 4620 | 1, 5, 6, 7m, 8, 9, 10, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C11Y | 600 | 3 | - | 88 | 30 | 208, 3 | 208, 3 | 100 | 88 | 30 | 4620 | 1, 6, 7m
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 10 | 88 | 30 | 208, 3 | 208, 3 | 100 | 88 | 30 | 4620 | 1, 6, 7m
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 10 | 74.8 | 25 | 208, 3 | 208, 3 | 100 | 88 | 30 | 4620 | 1, 6, 7m
SE105211 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36150M | 600 | 3 | - | 150 | - | 240 | 3 | 100 | 80 | 30 | 4620 | 1, 5, 6, 7l, 8, 9, 10, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D88Y | 600 | 3 | - | 80 | 30 | 240, 3 | 240, 3 | 100 | 80 | 30 | 4620 | 1, 6, 7L
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 10 | 104 | 40 | 240, 3 | 240, 3 | 100 | 80 | 30 | 4620 | 1, 6, 7L
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 5 | 80 | 30 | 240, 3 | 240, 3 | 100 | 80 | 30 | 4620 | 1, 6, 7L
SE105212 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36100M | 600 | 3 | - | 100 | - | 480 | 3 | 100 | 40 | 30 | 4620 | 1, 5, 6, 7k, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D47Y | 600 | 3 | - | 40 | 30 | 480, 3 | 480, 3 | 100 | 40 | 30 | 4620 | 1, 6, 7k
[10 empty] | (ISO) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 5 | 52 | 40 | 480, 3 | 480, 3 | 100 | 40 | 30 | 4620 | 1, 6, 7k
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 5 | 27 | 20 | 480, 3 | 480, 3 | 100 | 40 | 30 | 4620 | 1, 6, 7k
SE105213 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36050M | 600 | 3 | - | 50 | - | 600 | 3 | 50 | 32 | 30 | 4620 | 1, 5, 6, 7a, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D38Y | 600 | 3 | - | 32 | 30 | 480, 3 | 480, 3 | 100 | 34 | 25 | 4620 | 1, 6, 7a
[10 empty] | (ISO) MC | Schneider Electric | LC1D40 (Optional) | 600 | 3 | 5 | 32 | 30 | 480, 3 | 480, 3 | 100 | 34 | 25 | 4620 | 1, 6, 7a
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 5 | 27 | 25 | 480, 3 | 480, 3 | 100 | 34 | 25 | 4620 | 1, 6, 7a
SE105214 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | D | ICB | Square D | HLL36150M | 600 | 3 | - | 150 | - | 208 | 3 | 100 | 114 | 40 | 6468 | 1, 5, 6, 7n, 8, 9, 10, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C14Y | 600 | 3 | - | 114 | 40 | 208, 3 | 208, 3 | 100 | 114 | 40 | 4620 | 1, 6, 7n
[10 empty] | (ISO) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 10 | 114 | 40 | 208, 3 | 208, 3 | 100 | 114 | 40 | 4620 | 1, 6, 7n
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 5 | 74.8 | 25 | 208, 3 | 208, 3 | 100 | 114 | 40 | 4620 | 1, 6, 7n
SE105215 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36150M | 600 | 3 | - | 150 | - | 240 | 3 | 100 | 104 | 40 | 4620 | 1, 5, 6, 7m, 8, 9, 10, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C11Y | 600 | 3 | - | 104 | 40 | 240, 3 | 240, 3 | 100 | 104 | 40 | 4620 | 1, 6, 7m
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 10 | 104 | 40 | 240, 3 | 240, 3 | 100 | 104 | 40 | 4620 | 1, 6, 7m
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 5 | 80 | 30 | 240, 3 | 240, 3 | 100 | 104 | 40 | 4620 | 1, 6, 7m
SE105216 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36100M | 600 | 3 | - | 100 | - | 480 | 3 | 100 | 52 | 40 | 4620 | 1, 5, 6, 7b, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D62Y | 600 | 3 | - | 52 | 40 | 480, 3 | 480, 3 | 100 | 52 | 40 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Schneider Electric | LC1D65 (Optional) | 600 | 3 | 5 | 52 | 40 | 480, 3 | 480, 3 | 100 | 52 | 40 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Schneider Electric | LC1D40 (Optional) | 600 | 3 | 5 | 40 | 30 | 480, 3 | 480, 3 | 100 | 52 | 40 | 4620 | 1, 6, 7b
SE105217 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36100M | 600 | 3 | - | 100 | - | 600 | 3 | 50 | 41 | 40 | 4620 | 1, 5, 6, 7k, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D47Y | 600 | 3 | - | 41 | 40 | 480, 3 | 480, 3 | 100 | 40 | 30 | 4620 | 1, 6, 7k
[10 empty] | (ISO) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 5 | 41 | 40 | 480, 3 | 480, 3 | 100 | 40 | 30 | 4620 | 1, 6, 7k
[10 empty] | (SHORT) MC | Schneider Electric | LC1D32 (Optional) | 600 | 3 | 5 | 27 | 25 | 480, 3 | 480, 3 | 100 | 40 | 30 | 4620 | 1, 6, 7k
SE105218 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | D | ICB | Square D | JLL36250M | 600 | 3 | - | 250 | - | 208 | 3 | 100 | 143 | 50 | 6468 | 1, 5, 6, 7c, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C17Y | 600 | 3 | - | 143 | 50 | 208, 3 | 208, 3 | 100 | 143 | 50 | 4620 | 1, 6, 7c
[10 empty] | (ISO) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 65 | 143 | 50 | 208, 3 | 208, 3 | 100 | 143 | 50 | 4620 | 1, 6, 7c
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 10 | 88 | 30 | 208, 3 | 208, 3 | 100 | 143 | 50 | 4620 | 1, 6, 7c
SE105219 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | D | ICB | Square D | JLL36250M | 600 | 3 | - | 250 | - | 240 | 3 | 100 | 130 | 50 | 6468 | 1, 5, 6, 7n, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C14Y | 600 | 3 | - | 130 | 50 | 240, 3 | 240, 3 | 100 | 130 | 50 | 4620 | 1, 6, 7n
[10 empty] | (ISO) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 10 | 130 | 50 | 240, 3 | 240, 3 | 100 | 130 | 50 | 4620 | 1, 6, 7n
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 10 | 104 | 40 | 240, 3 | 240, 3 | 100 | 130 | 50 | 4620 | 1, 6, 7n
SE105220 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36150M | 600 | 3 | - | 150 | - | 480 | 3 | 100 | 65 | 50 | 4620 | 1, 5, 6, 7b, 8, 9, 10, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D75Y | 600 | 3 | - | 65 | 50 | 480, 3 | 480, 3 | 100 | 65 | 50 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 10 | 52 | 40 | 480, 3 | 480, 3 | 100 | 65 | 50 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 5 | 52 | 40 | 480, 3 | 480, 3 | 100 | 65 | 50 | 4620 | 1, 6, 7b
SE105221 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36100M | 600 | 3 | - | 100 | - | 600 | 3 | 50 | 52 | 50 | 4620 | 1, 5, 6, 7b, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D62Y | 600 | 3 | - | 52 | 50 | 480, 3 | 480, 3 | 100 | 52 | 40 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Schneider Electric | LC1D65 (Optional) | 600 | 3 | 5 | 52 | 50 | 480, 3 | 480, 3 | 100 | 52 | 40 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Schneider Electric | LC1D40 (Optional) | 600 | 3 | 5 | 32 | 30 | 480, 3 | 480, 3 | 100 | 52 | 40 | 4620 | 1, 6, 7b
SE105222 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | D | ICB | Square D | JLL36250M | 600 | 3 | - | 250 | - | 208 | 3 | 100 | 169 | 60 | 28800 | 1, 5, 6, 7d, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C21Y | 600 | 3 | - | 169 | 60 | 208, 3 | 208, 3 | 100 | 169 | 60 | 4620 | 1, 6, 7d
[10 empty] | (ISO) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 65 | 143 | 50 | 208, 3 | 208, 3 | 100 | 169 | 60 | 4620 | 1, 6, 7d
[10 empty] | (SHORT) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 10 | 114 | 40 | 208, 3 | 208, 3 | 100 | 169 | 60 | 4620 | 1, 6, 7d
SE105223 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | D | ICB | Square D | JLL36250M | 600 | 3 | - | 250 | - | 240 | 3 | 100 | 154 | 60 | 6468 | 1, 5, 6, 7c, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C17Y | 600 | 3 | - | 154 | 60 | 240, 3 | 240, 3 | 100 | 154 | 60 | 4620 | 1, 6, 7c
[10 empty] | (ISO) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 65 | 154 | 60 | 240, 3 | 240, 3 | 100 | 154 | 60 | 4620 | 1, 6, 7c
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 10 | 104 | 40 | 240, 3 | 240, 3 | 100 | 154 | 60 | 4620 | 1, 6, 7c
SE105224 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36150M | 600 | 3 | - | 150 | - | 480 | 3 | 100 | 77 | 60 | 4620 | 1, 5, 6, 7l, 8, 9, 10, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D88Y | 600 | 3 | - | 77 | 60 | 480, 3 | 480, 3 | 100 | 77 | 60 | 4620 | 1, 6, 7L
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 10 | 96 | 75 | 480, 3 | 480, 3 | 100 | 77 | 60 | 4620 | 1, 6, 7L
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 10 | 77 | 60 | 480, 3 | 480, 3 | 100 | 77 | 60 | 4620 | 1, 6, 7L
SE105225 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36150M | 600 | 3 | - | 150 | - | 600 | 3 | 50 | 62 | 60 | 4620 | 1, 5, 6, 7b, 8, 9, 10, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D75Y | 600 | 3 | - | 62 | 60 | 480, 3 | 480, 3 | 100 | 65 | 50 | 4620 | 1, 6, 7b
[10 empty] | (ISO) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 5 | 62 | 60 | 480, 3 | 480, 3 | 100 | 65 | 50 | 4620 | 1, 6, 7b
[10 empty] | (SHORT) MC | Schneider Electric | LC1D50 (Optional) | 600 | 3 | 5 | 41 | 40 | 480, 3 | 480, 3 | 100 | 65 | 50 | 4620 | 1, 6, 7b
SE105226 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | D | ICB | Square D | LLL36400M | 600 | 3 | - | 400 | - | 208 | 3 | 100 | 211 | 75 | 28800 | 1, 5, 6, 7p, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C25Y | 600 | 3 | - | 211 | 75 | 208, 3 | 208, 3 | 100 | 211 | 75 | 4620 | 1, 6, 7p
[10 empty] | (ISO) MC | Schneider Electric | LC1F225 (Optional) | 600 | 3 | 10 | 169 | 60 | 208, 3 | 208, 3 | 100 | 211 | 75 | 4620 | 1, 6, 7p
[10 empty] | (SHORT) MC | Schneider Electric | LC1F225 (Optional) | 600 | 3 | 10 | 169 | 60 | 208, 3 | 208, 3 | 100 | 211 | 75 | 4620 | 1, 6, 7p
SE105227 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | D | ICB | Square D | JLL36250M | 600 | 3 | - | 250 | - | 240 | 3 | 100 | 192 | 75 | 28800 | 1, 5, 6, 7d, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C21Y | 600 | 3 | - | 192 | 75 | 240, 3 | 240, 3 | 100 | 192 | 75 | 4620 | 1, 6, 7d
[10 empty] | (ISO) MC | Schneider Electric | LC1F225 (Optional) | 600 | 3 | 10 | 192 | 75 | 240, 3 | 240, 3 | 100 | 192 | 75 | 4620 | 1, 6, 7d
[10 empty] | (SHORT) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 10 | 130 | 50 | 240, 3 | 240, 3 | 100 | 192 | 75 | 4620 | 1, 6, 7d
SE105228 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36150M | 600 | 3 | - | 150 | - | 480 | 3 | 100 | 96 | 75 | 4620 | 1, 5, 6, 7m, 8, 9, 10, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C11Y | 600 | 3 | - | 96 | 75 | 480, 3 | 480, 3 | 100 | 96 | 75 | 4620 | 1, 6, 7m
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 10 | 96 | 75 | 480, 3 | 480, 3 | 100 | 96 | 75 | 4620 | 1, 6, 7m
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 10 | 77 | 60 | 480, 3 | 480, 3 | 100 | 96 | 75 | 4620 | 1, 6, 7m
SE105229 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36150M | 600 | 3 | - | 150 | - | 600 | 3 | 50 | 77 | 75 | 4620 | 1, 5, 6, 7l, 8, 9, 10, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480D88Y | 600 | 3 | - | 77 | 75 | 480, 3 | 480, 3 | 100 | 77 | 60 | 4620 | 1, 6, 7L
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 10 | 99 | 100 | 480, 3 | 480, 3 | 100 | 77 | 60 | 4620 | 1, 6, 7L
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 10 | 62 | 60 | 480, 3 | 480, 3 | 100 | 77 | 60 | 4620 | 1, 6, 7L
SE105230 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | D | ICB | Square D | LLL36600M | 600 | 3 | - | 600 | - | 208 | 3 | 100 | 273 | 100 | 28800 | 1, 5, 6, 7h, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C32Y | 600 | 3 | - | 273 | 100 | 208, 3 | 208, 3 | 100 | 273 | 100 | 4620 | 1, 6, 7h
[10 empty] | (ISO) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 18 | 211 | 75 | 208, 3 | 208, 3 | 100 | 273 | 100 | 4620 | 1, 6, 7h
[10 empty] | (SHORT) MC | Schneider Electric | LC1F265 (Optional) | 600 | 3 | 10 | 169 | 60 | 208, 3 | 208, 3 | 100 | 273 | 100 | 4620 | 1, 6, 7h
SE105231 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | D | ICB | Square D | LLL36400M | 600 | 3 | - | 400 | - | 240 | 3 | 100 | 248 | 100 | 28800 | 1, 5, 6, 7h, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C25Y | 600 | 3 | - | 248 | 100 | 240, 3 | 240, 3 | 100 | 248 | 100 | 4620 | 1, 6, 7h
[10 empty] | (ISO) MC | Schneider Electric | LC1F265 (Optional) | 600 | 3 | 10 | 192 | 75 | 240, 3 | 240, 3 | 100 | 248 | 100 | 4620 | 1, 6, 7h
[10 empty] | (SHORT) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 10 | 154 | 60 | 240, 3 | 240, 3 | 100 | 248 | 100 | 4620 | 1, 6, 7h
SE105232 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | D | ICB | Square D | JLL36250M | 600 | 3 | - | 250 | - | 480 | 3 | 100 | 124 | 100 | 6468 | 1, 5, 6, 7n, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C14Y | 600 | 3 | - | 124 | 100 | 480, 3 | 480, 3 | 100 | 124 | 100 | 4620 | 1, 6, 7n
[10 empty] | (ISO) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 10 | 124 | 100 | 480, 3 | 480, 3 | 100 | 124 | 100 | 4620 | 1, 6, 7n
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 10 | 96 | 75 | 480, 3 | 480, 3 | 100 | 124 | 100 | 4620 | 1, 6, 7n
SE105233 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 30 | 14 | 11 | D | ICB | Square D | HLL36150M | 600 | 3 | - | 150 | - | 600 | 3 | 50 | 99 | 100 | 4620 | 1, 5, 6, 7m, 8, 9, 10, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C11Y | 600 | 3 | - | 99 | 100 | 480, 3 | 480, 3 | 100 | 96 | 75 | 4620 | 1, 6, 7m
[10 empty] | (ISO) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 10 | 99 | 100 | 480, 3 | 480, 3 | 100 | 96 | 75 | 4620 | 1, 6, 7m
[10 empty] | (SHORT) MC | Schneider Electric | LC1D80* (Optional) | 600 | 3 | 10 | 62 | 60 | 480, 3 | 480, 3 | 100 | 96 | 75 | 4620 | 1, 6, 7m
SE105234 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | D | ICB | Square D | JLL36250M | 600 | 3 | - | 250 | - | 480 | 3 | 100 | 156 | 125 | 6468 | 1, 5, 6, 7c, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C17Y | 600 | 3 | - | 156 | 125 | 480, 3 | 480, 3 | 100 | 156 | 125 | 4620 | 1, 6, 7c
[10 empty] | (ISO) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 65 | 156 | 125 | 480, 3 | 480, 3 | 100 | 156 | 125 | 4620 | 1, 6, 7c
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 10 | 96 | 75 | 480, 3 | 480, 3 | 100 | 156 | 125 | 4620 | 1, 6, 7c
SE105235 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | D | ICB | Square D | JLL36250M | 600 | 3 | - | 250 | - | 600 | 3 | 50 | 125 | 125 | 6468 | 1, 5, 6, 7n, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C14Y | 600 | 3 | - | 125 | 125 | 480, 3 | 480, 3 | 100 | 124 | 100 | 4620 | 1, 6, 7n
[10 empty] | (ISO) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 10 | 125 | 125 | 480, 3 | 480, 3 | 100 | 124 | 100 | 4620 | 1, 6, 7n
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 10 | 99 | 100 | 480, 3 | 480, 3 | 100 | 124 | 100 | 4620 | 1, 6, 7n
SE105236 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | D | ICB | Square D | JLL36250M | 600 | 3 | - | 250 | - | 480 | 3 | 100 | 180 | 150 | 28800 | 1, 5, 6, 7d, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C21Y | 600 | 3 | - | 180 | 150 | 480, 3 | 480, 3 | 100 | 180 | 150 | 4620 | 1, 6, 7d
[10 empty] | (ISO) MC | Schneider Electric | LC1F225 (Optional) | 600 | 3 | 10 | 180 | 150 | 480, 3 | 480, 3 | 100 | 180 | 150 | 4620 | 1, 6, 7d
[10 empty] | (SHORT) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 10 | 124 | 100 | 480, 3 | 480, 3 | 100 | 180 | 150 | 4620 | 1, 6, 7d
SE105237 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 42 | 14 | 11 | D | ICB | Square D | JLL36250M | 600 | 3 | - | 250 | - | 600 | 3 | 50 | 144 | 150 | 6468 | 1, 5, 6, 7c, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C17Y | 600 | 3 | - | 144 | 150 | 480, 3 | 480, 3 | 100 | 156 | 125 | 4620 | 1, 6, 7c
[10 empty] | (ISO) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 65 | 144 | 150 | 480, 3 | 480, 3 | 100 | 156 | 125 | 4620 | 1, 6, 7c
[10 empty] | (SHORT) MC | Schneider Electric | LC1D115 (Optional) | 600 | 3 | 10 | 99 | 100 | 480, 3 | 480, 3 | 100 | 156 | 125 | 4620 | 1, 6, 7c
SE105238 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | D | ICB | Square D | LLL36400M | 600 | 3 | - | 400 | - | 480 | 3 | 100 | 240 | 200 | 28800 | 1, 5, 6, 7h, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C25Y | 600 | 3 | - | 240 | 200 | 480, 3 | 480, 3 | 100 | 240 | 200 | 4620 | 1, 6, 7h
[10 empty] | (ISO) MC | Schneider Electric | LC1F265 (Optional) | 600 | 3 | 10 | 180 | 150 | 480, 3 | 480, 3 | 100 | 240 | 200 | 4620 | 1, 6, 7h
[10 empty] | (SHORT) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 10 | 156 | 125 | 480, 3 | 480, 3 | 100 | 240 | 200 | 4620 | 1, 6, 7h
SE105239 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | D | ICB | Square D | JLL36250M | 600 | 3 | - | 250 | - | 600 | 3 | 50 | 192 | 200 | 28800 | 1, 5, 6, 7d, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C21Y | 600 | 3 | - | 192 | 200 | 480, 3 | 480, 3 | 100 | 180 | 150 | 4620 | 1, 6, 7d
[10 empty] | (ISO) MC | Schneider Electric | LC1F225 (Optional) | 600 | 3 | 10 | 144 | 150 | 480, 3 | 480, 3 | 100 | 180 | 150 | 4620 | 1, 6, 7d
[10 empty] | (SHORT) MC | Schneider Electric | LC1D150 (Optional) | 600 | 3 | 10 | 125 | 125 | 480, 3 | 480, 3 | 100 | 180 | 150 | 4620 | 1, 6, 7d
SE105240 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | D | ICB | Square D | LLL36600M | 600 | 3 | - | 600 | - | 480 | 3 | 100 | 302 | 250 | 28800 | 1, 5, 6, 7s, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C32Y | 600 | 3 | - | 302 | 250 | 480, 3 | 480, 3 | 100 | 302 | 250 | 4620 | 1, 6, 7s
[10 empty] | (ISO) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 18 | 240 | 200 | 480, 3 | 480, 3 | 100 | 302 | 250 | 4620 | 1, 6, 7s
[10 empty] | (SHORT) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 18 | 240 | 200 | 480, 3 | 480, 3 | 100 | 302 | 250 | 4620 | 1, 6, 7s
SE105241 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | D | ICB | Square D | LLL36400M | 600 | 3 | - | 400 | - | 600 | 3 | 50 | 242 | 250 | 28800 | 1, 5, 6, 7h, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C25Y | 600 | 3 | - | 242 | 250 | 480, 3 | 480, 3 | 100 | 240 | 200 | 4620 | 1, 6, 7h
[10 empty] | (ISO) MC | Schneider Electric | LC1F265 (Optional) | 600 | 3 | 10 | 192 | 200 | 480, 3 | 480, 3 | 100 | 240 | 200 | 4620 | 1, 6, 7h
[10 empty] | (SHORT) MC | Schneider Electric | LC1F185 (Optional) | 600 | 3 | 10 | 144 | 150 | 480, 3 | 480, 3 | 100 | 240 | 200 | 4620 | 1, 6, 7h
SE105242 | E40610 | 2004-09-01 | 12.2 | Model 6 | Page 2/ Ills.1A, 2, 4, 5, 8 | 72 | 20 | 20 | D | ICB | Square D | LLL36600M | 600 | 3 | - | 600 | - | 600 | 3 | 50 | 289 | 300 | 28800 | 1, 5, 6, 7s, 8, 9, 12 | N/A
[10 empty] | STR | Schneider Toshiba Inverter Europe | ATS480C32Y | 600 | 3 | - | 289 | 300 | 480, 3 | 480, 3 | 100 | 302 | 250 | 4620 | 1, 6, 7s
[10 empty] | (ISO) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 18 | 242 | 250 | 480, 3 | 480, 3 | 100 | 302 | 250 | 4620 | 1, 6, 7s
[10 empty] | (SHORT) MC | Schneider Electric | LC1F330 (Optional) | 600 | 3 | 18 | 242 | 250 | 480, 3 | 480, 3 | 100 | 302 | 250 | 4620 | 1, 6, 7s