## Const. E_F w MPCB (190E-191E)
Issued: 2008-01-24
Last Revised: 2017-06-16
[12 empty] | Assembled Combination Motor Controller |  |  |  |  | Component List
ID Number | Construction Type |  | Index No. | Max. Motor HP Rating [1] |  |  |  | Max. Motor FLA [2] |  |  |  | Compact * Component Combination Motor Controller |  | SCCR |  |  | Cat. Numbers for Field Assembly |  |  |  | Minimum Enclosure Volume (cu. in.) | Conditions of Acceptability | UL File Reference
| 480Y/277V | 600Y/347V |  | 200V | 230V | 460V | 575V | 200V | 230V | 460V | 575V | A-B Cat. No. | Motor Current Adjust Range (A) | 208..240V | 480Y/277V | 600Y/347V | Contactor [3] | MPCB | Terminal Adapter | Connection Module (s)
2 Component DOL Compact Combination Motor Controller - C Frame MPCB
AB190E-AN**-CA16… | E | E | 1 | --- | --- | --- | --- | 0.16 | 0.16 | 0.16 | 0.16 | 190E-AN**-CA16… | 0.1 … 0.16 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-A16 | 140M-C-TE1 | 140M-C-PEC23 | 655 | 1, 5, 6 | E205542, 2:3
AB190E-AN**-CA25… | E | E | 2 | --- | --- | --- | --- | 0.25 | 0.25 | 0.25 | 0.25 | 190E-AN**-CA25… | 0.16 … 0.25 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-A25 | 140M-C-TE1 | 140M-C-PEC23
AB190E-AN**-CA40… | E | E | 3 | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 190E-AN**-CA40… | 0.25 … 0.40 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-A40 | 140M-C-TE1 | 140M-C-PEC23
AB190E-AN**-CA63… | E | E | 4 | --- | --- | --- | --- | 0.63 | 0.63 | 0.63 | 0.63 | 190E-AN**-CA63… | 0.40 … 0.63 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-A63 | 140M-C-TE1 | 140M-C-PEC23
AB190E-AN**-CB10… | E | E | 5 | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 190E-AN**-CB10… | 0.63 … 1.0 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-B10 | 140M-C-TE1 | 140M-C-PEC23
AB190E-AN**-CB16… | E | E | 6 | --- | --- | 1 | 1 | 1.6 | 1.6 | 1.6 | 1.6 | 190E-AN**-CB16… | 1.0 … 1.6 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-B16 | 140M-C-TE1 | 140M-C-PEC23
AB190E-AN**-CB25… | E | F | 7 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 190E-AN**-CB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-C2E-B25 | 140M-C-TE1 | 140M-C-PEC23
AB190E-AN**-CB40… | F | F | 8 | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 190E-AN**-CB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-C2E-B40 | 140M-C-TE1 | 140M-C-PEC23
AB190E-AN**-CB63… | F | --- | 9 | 1-1/2 | 2 | 5 | --- | 6.3 | 6.3 | 6.3 | --- | 190E-AN**-CB63… | 4.0 … 6.3 | 65kA | 65kA | --- | 100-C09*10 | 140M-C2E-B63 | 140M-C-TE1 | 140M-C-PEC23
AB190E-AN**-CC10… | F | --- | 10 | 2 | 2 | 5 | --- | 7.8 | 6.8 | 7.6 | --- | 190E-AN**-CC10… | 6.3 … 9.0 | 65kA | 65kA | --- | 100-C09*10 | 140M-C2E-C10 | 140M-C-TE1 | 140M-C-PEC23
AB190E-BN**-CC10… | F | --- | 11 | 3 | 3 | 7-1/2 | --- | 10 | 9.6 | 10 | --- | 190E-BN**-CC10… | 6.3 … 10.0 | 65kA | 65kA | --- | 100-C12*10 | 140M-C2E-C10 | 140M-C-TE1 | 140M-C-PEC23
AB190E-CN**-CC10… | F | --- | -- | 3 | 3 | 7-1/2 | --- | 10 | 9.6 | 10 | --- | 190E-CN**-CC10… | 6.3 … 10.0 | 65kA | 65kA | --- | 100-C16*10 | 140M-C2E-C10 | 140M-C-TE1 | 140M-C-PEC23
AB190E-BN**-CC16… | F | --- | 12 | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 190E-BN**-CC16… | 10.0 … 12.0 | 30kA | 30kA | --- | 100-C12*10 | 140M-C2E-C16 | 140M-C-TE1 | 140M-C-PEC23
AB190E-CN**-CC16… | F | --- | 13 | 5 | 5 | 10 | --- | 16 | 15.2 | 14 | --- | 190E-CN**-CC16… | 10.0 … 16.0 | 30kA | 30kA | --- | 100-C16*10 | 140M-C2E-C16 | 140M-C-TE1 | 140M-C-PEC23
AB190E-DN**-CC16… | F | --- | 14 | 5 | 5 | 10 | --- | 16 | 15.2 | 14 | --- | 190E-DN**-CC16… | 10.0 … 16.0 | 30kA | 30kA | --- | 100-C23*10 | 140M-C2E-C16 | 140M-C-TE1 | 140M-C-PEC23
AB190E-DN**-CC20… | F | --- | 15 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 190E-DN**-CC20… | 14.5 … 20.0 | 10kA | 10kA | --- | 100-C23*10 | 140M-C2E-C20 | 140M-C-TE1 | 140M-C-PEC23
2 Component Reversing DOL Compact Combination Motor Controller - C Frame MPCB
AB191E-AN**-CA16... | E | E | 1 | --- | --- | --- | --- | 0.16 | 0.16 | 0.16 | 0.16 | 191E-AN**-CA16... | 0.1 … 0.16 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-A16 | 140M-C-TE1 | 140M-C-PEC23 | 655 | 1, 5, 6 | E205542, 2:3
AB191E-AN**-CA25... | E | E | 2 | --- | --- | --- | --- | 0.25 | 0.25 | 0.25 | 0.25 | 191E-AN**-CA25... | 0.16 … 0.25 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-A25 | 140M-C-TE1 | 140M-C-PEC23
AB191E-AN**-CA40... | E | E | 3 | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 191E-AN**-CA40... | 0.25 … 0.40 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-A40 | 140M-C-TE1 | 140M-C-PEC23
AB191E-AN**-CA63... | E | E | 4 | --- | --- | --- | --- | 0.63 | 0.63 | 0.63 | 0.63 | 191E-AN**-CA63... | 0.40 … 0.63 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-A63 | 140M-C-TE1 | 140M-C-PEC23
AB191E-AN**-CB10... | E | E | 5 | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 191E-AN**-CB10... | 0.63 … 1.0 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-B10 | 140M-C-TE1 | 140M-C-PEC23
AB191E-AN**-CB16... | E | E | 6 | --- | --- | 1 | 1 | 1.6 | 1.6 | 1.6 | 1.6 | 191E-AN**-CB16... | 1.0 … 1.6 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-B16 | 140M-C-TE1 | 140M-C-PEC23
AB191E-AN**-CB25... | E | F | 7 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 191E-AN**-CB25... | 1.6 … 2.5 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-C2E-B25 | 140M-C-TE1 | 140M-C-PEC23
AB191E-AN**-CB40... | F | F | 8 | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 191E-AN**-CB40... | 2.5 … 4.0 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-C2E-B40 | 140M-C-TE1 | 140M-C-PEC23
AB191E-AN**-CB63... | F | --- | 9 | 1-1/2 | 2 | 5 | --- | 6.3 | 6.3 | 6.3 | --- | 191E-AN**-CB63... | 4.0 … 6.3 | 65kA | 65kA | --- | 104-C09*22 | 140M-C2E-B63 | 140M-C-TE1 | 140M-C-PEC23
AB191E-AN**-CC10... | F | --- | 10 | 2 | 2 | 5 | --- | 7.8 | 6.8 | 7.6 | --- | 191E-AN**-CC10... | 6.3 … 9.0 | 65kA | 65kA | --- | 104-C09*22 | 140M-C2E-C10 | 140M-C-TE1 | 140M-C-PEC23
AB191E-BN**-CC10... | F | --- | 11 | 3 | 3 | 7-1/2 | --- | 10 | 9.6 | 10 | --- | 191E-BN**-CC10... | 6.3 … 10.0 | 65kA | 65kA | --- | 104-C12*22 | 140M-C2E-C10 | 140M-C-TE1 | 140M-C-PEC23
AB191E-CN**-CC10… | F | --- | -- | 3 | 3 | 7-1/2 | --- | 10 | 9.6 | 10 | --- | 191E-CN**-CC10… | 6.3 … 10.0 | 65kA | 65kA | --- | 104-C16*22 | 140M-C2E-C10 | 140M-C-TE1 | 140M-C-PEC23
AB191E-BN**-CC16... | F | --- | 12 | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 191E-BN**-CC16... | 10.0 … 12.0 | 30kA | 30kA | --- | 104-C12*22 | 140M-C2E-C16 | 140M-C-TE1 | 140M-C-PEC23
AB191E-CN**-CC16... | F | --- | 13 | 5 | 5 | 10 | --- | 16 | 15.2 | 14 | --- | 191E-CN**-CC16... | 10.0 … 16.0 | 30kA | 30kA | --- | 104-C16*22 | 140M-C2E-C16 | 140M-C-TE1 | 140M-C-PEC23
AB191E-DN**-CC16... | F | --- | 14 | 5 | 5 | 10 | --- | 16 | 15.2 | 14 | --- | 191E-DN**-CC16... | 10.0 … 16.0 | 30kA | 30kA | --- | 104-C23*22 | 140M-C2E-C16 | 140M-C-TE1 | 140M-C-PEC23
AB191E-DN**-CC20... | F | --- | 15 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 191E-DN**-CC20... | 14.5 … 20.0 | 10kA | 10kA | --- | 104-C23*22 | 140M-C2E-C20 | 140M-C-TE1 | 140M-C-PEC23
2 Component DOL Compact Combination Motor Controller - D Frame MPCB
AB190E-AN**-DB25... | E | F | 17 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 190E-AN**-DB25... | 1.6 … 2.5 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-D8E-B25 | 140M-C-TE1 | 140M-D-PEC23 | 655 | 1, 5, 6 | E205542, 2:3
AB190E-DN**-DB25... | E | E | 18 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 190E-DN**-DB25... | 1.6 … 2.5 | 65kA | 65kA | 30kA | 100-C23*10 | 140M-D8E-B25 | 140M-C-TE1 | 140M-D-PEC23
AB190E-AN**-DB40... | F | F | 19 | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 190E-AN**-DB40... | 2.5 … 4.0 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-D8E-B40 | 140M-C-TE1 | 140M-D-PEC23
AB190E-DN**-DB40... | E | E | 21 | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 190E-DN**-DB40... | 2.5 … 4.0 | 65kA | 65kA | 30kA | 100-C23*10 | 140M-D8E-B40 | 140M-C-TE1 | 140M-D-PEC23
AB190E-AN**-DB63... | F | F | 22 | 1-1/2 | 2 | 5 | 5 | 6.3 | 6.3 | 6.3 | 6.1 | 190E-AN**-DB63... | 4.0 … 6.3 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-D8E-B63 | 140M-C-TE1 | 140M-D-PEC23
AB190E-AN**-DC10... | F | F | 24 | 2 | 2 | 5 | 7-1/2 | 7.8 | 6.8 | 7.6 | 9 | 190E-AN**-DC10... | 6.3 … 9.0 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-D8E-C10 | 140M-C-TE1 | 140M-D-PEC23
AB190E-BN**-DC10... | F | F | 25 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 190E-BN**-DC10... | 6.3 … 10.0 | 65kA | 65kA | 30kA | 100-C12*10 | 140M-D8E-C10 | 140M-C-TE1 | 140M-D-PEC23
AB190E-CN**-DC10... | F | F | 26 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 190E-CN**-DC10... | 6.3 … 10.0 | 65kA | 65kA | 30kA | 100-C16*10 | 140M-D8E-C10 | 140M-C-TE1 | 140M-D-PEC23
AB190E-BN**-DC16... | F | F | -- | 3 | 3 | 7-1/2 | 10 | 11 | 9.6 | 11 | 11 | 190E-BN**-DC16... | 10 … 12.0 | 65kA | 65kA | 30kA | 100-C12*10 | 140M-D8E-C16 | 140M-C-TE1 | 140M-D-PEC23
AB190E-CN**-DC16... | F | F | 28 | 5 | 5 | 10 | 10 | 16 | 15.2 | 14 | 11 | 190E-CN**-DC16... | 10 … 16.0 | 65kA | 65kA | 30kA | 100-C16*10 | 140M-D8E-C16 | 140M-C-TE1 | 140M-D-PEC23
AB190E-DN**-DC16... | F | F | 29 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 190E-DN**-DC16... | 10 … 16.0 | 65kA | 65kA | 30kA | 100-C23*10 | 140M-D8E-C16 | 140M-C-TE1 | 140M-D-PEC23
AB190E-DN**-DC20... | F | --- | 31 | 5 | 7.5 | 15 | --- | 17.5 | 15.2 | 20 | --- | 190E-DN**-DC20... | 14.5 … 20.0 | 65kA | 65kA | --- | 100-C23*10 | 140M-D8E-C20 | 140M-C-TE1 | 140M-D-PEC23
AB190E-DN**-DC25... | F | --- | 33 | 5 | 7.5 | 15 | --- | 25 | 22 | 21 | --- | 190E-DN**-DC25... | 18.0 … 22.0 | 65kA | 65kA | --- | 100-C23*10 | 140M-D8E-C25 | 140M-C-TE1 | 140M-D-PEC23
2 Component Reversing Compact Combination Motor Controller - D Frame MPCB
AB191E-AN**-DB25... | E | F | 17 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 191E-AN**-DB25... | 1.6 … 2.5 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-D8E-B25 | 140M-C-TE1 | 140M-D-PEC23 | 655 | 1, 5, 6 | E205542, 2:3
AB191E-DN**-DB25... | E | E | 18 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 191E-DN**-DB25... | 1.6 … 2.5 | 65kA | 65kA | 30kA | 104-C23*22 | 140M-D8E-B25 | 140M-C-TE1 | 140M-D-PEC23
AB191E-AN**-DB40... | F | F | 19 | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 191E-AN**-DB40... | 2.5 … 4.0 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-D8E-B40 | 140M-C-TE1 | 140M-D-PEC23
AB191E-DN**-DB40... | E | E | 21 | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 191E-DN**-DB40... | 2.5 … 4.0 | 65kA | 65kA | 30kA | 104-C23*22 | 140M-D8E-B40 | 140M-C-TE1 | 140M-D-PEC23
AB191E-AN**-DB63... | F | F | 22 | 1-1/2 | 2 | 5 | 5 | 6.3 | 6.3 | 6.3 | 6.1 | 191E-AN**-DB63... | 4.0 … 6.3 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-D8E-B63 | 140M-C-TE1 | 140M-D-PEC23
AB191E-AN**-DC10... | F | F | 24 | 2 | 2 | 5 | 7-1/2 | 7.8 | 6.8 | 7.6 | 9 | 191E-AN**-DC10... | 6.3 … 9.0 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-D8E-C10 | 140M-C-TE1 | 140M-D-PEC23
AB191E-BN**-DC10... | F | F | 25 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 191E-BN**-DC10... | 6.3 … 10.0 | 65kA | 65kA | 30kA | 104-C12*22 | 140M-D8E-C10 | 140M-C-TE1 | 140M-D-PEC23
AB191E-CN**-DC10... | F | F | 26 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 191E-CN**-DC10... | 6.3 … 10.0 | 65kA | 65kA | 30kA | 104-C16*22 | 140M-D8E-C10 | 140M-C-TE1 | 140M-D-PEC23
AB191E-BN**-DC16... | F | F | -- | 3 | 3 | 7-1/2 | 10 | 11 | 9.6 | 11 | 11 | 191E-BN**-DC16... | 10 … 12.0 | 65kA | 65kA | 30kA | 104-C12*22 | 140M-D8E-C16 | 140M-C-TE1 | 140M-D-PEC23
AB191E-CN**-DC16... | F | F | 28 | 5 | 5 | 10 | 10 | 16 | 15.2 | 14 | 11 | 191E-CN**-DC16... | 10 … 16.0 | 65kA | 65kA | 30kA | 104-C16*22 | 140M-D8E-C16 | 140M-C-TE1 | 140M-D-PEC23
AB191E-DN**-DC16... | F | F | 29 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 191E-DN**-DC16... | 10 … 16.0 | 65kA | 65kA | 30kA | 104-C23*22 | 140M-D8E-C16 | 140M-C-TE1 | 140M-D-PEC23
AB191E-DN**-DC20... | F | --- | 31 | 5 | 7.5 | 15 | --- | 17.5 | 15.2 | 20 | --- | 191E-DN**-DC20... | 14.5 … 20.0 | 65kA | 65kA | --- | 104-C23*22 | 140M-D8E-C20 | 140M-C-TE1 | 140M-D-PEC23
AB191E-DN**-DC25... | F | --- | 33 | 5 | 7.5 | 15 | --- | 25 | 22 | 21 | --- | 191E-DN**-DC25... | 18.0 … 22.0 | 65kA | 65kA | --- | 104-C23*22 | 140M-D8E-C25 | 140M-C-TE1 | 140M-D-PEC23
Notes:
[1] Horsepower ratings shown are for reference only, final selection of Combination Motor Controller depends on the actual motor full load current and service factor
[2] Full load current values from NEC Table 430.25 or represent the maximum current rating of the combination motor controller
[3] Spacing adapter required for Type E or Type F construction (-TE suffix)
[4] Minimum Contactor Size - Contactors may be upsized within the frame to provide increased electrical life
* Insert approprite coil code
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches.
Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = In lieu of the following R/C (NKCR2) Connection Modules the following Jumper wires may be used for the following Combination Motor Controllers.
| Connection Modules |  |  |  | Combination Motor Controller |  |  |  | Jumper Wire
| 140M-C-PEC23 or 140M-D-PEC23 |  |  |  | 190E-191E |  |  |  | 105°C, 600V; 14, 12 or 10 AWG

## Const. E_F w MPCB (103S-107S)
Issued: 2008-01-24
Last Revised: 2017-06-16
[12 empty] | Assembled Starter |  |  |  |  | Component List
ID Number | Construction Type |  | Index No. | Max. Motor HP Rating [1] |  |  |  | Motor FLA [2] |  |  |  | 2 Component Starter |  | SCCR |  |  | Cat. Numbers for Field Assembly | [5 empty] | Minimum Enclosure Volume (cu. in.) | Conditions of Acceptability | UL File Reference
| 480Y/277V | 600Y/347V |  | 200V | 230V | 460V | 575V | 200V | 230V | 460V | 575V | A-B Cat. No. | Motor Current Adjust Range (A) | 208..240V | 480Y/277V | 600Y/347V | Contactor [3] | MPCB | Mounting Module (s) |  | Terminal Adapter | Connection Module (s)
2 Component DOL ECO Starter w/ Standard Bus Bar Mount - C Frame MPCB
AB103S-AT**-CA16… | E | E | 1 | --- | --- | --- | --- | 0.16 | 0.16 | 0.16 | 0.16 | 103S-AT**-CA16… | 0.1 … 0.16 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-A16 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23 | 655 | 1, 5, 6 | E205542, 1:4, 2:2
AB103S-AT**-CA25… | E | E | 2 | --- | --- | --- | --- | 0.25 | 0.25 | 0.25 | 0.25 | 103S-AT**-CA25… | 0.16 … 0.25 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-A25 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AT**-CA40… | E | E | 3 | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 103S-AT**-CA40… | 0.25 … 0.40 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-A40 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AT**-CA63… | E | E | 4 | --- | --- | --- | --- | 0.63 | 0.63 | 0.63 | 0.63 | 103S-AT**-CA63… | 0.40 … 0.63 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-A63 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AT**-CB10… | E | E | 5 | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 103S-AT**-CB10… | 0.63 … 1.0 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-B10 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AT**-CB16… | E | E | 6 | --- | --- | 1 | 1 | 1.6 | 1.6 | 1.6 | 1.4 | 103S-AT**-CB16… | 1.0 … 1.6 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-B16 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AT**-CB25… | E | F | 7 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 103S-AT**-CB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-C2E-B25 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AT**-CB40… | F | F | 8 | 1 | 1 | 3 | 3 | 4 | 3.6 | 4 | 3.9 | 103S-AT**-CB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-C2E-B40 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AT**-CB63… | F | --- | 9 | 1-1/2 | 2 | 5 | --- | 6 | 6.3 | 6.3 | --- | 103S-AT**-CB63… | 4.0 … 6.3 | 65kA | 65kA | --- | 100-C09*10 | 140M-C2E-B63 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AT**-CC10… | F | --- | 10 | 2 | 2 | 5 | --- | 7.8 | 6.8 | 7.6 | --- | 103S-AT**-CC10… | 6.3 … 9.0 | 65kA | 65kA | --- | 100-C09*10 | 140M-C2E-C10 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-BT**-CC10… | F | --- | 11 | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 103S-BT**-CC10… | 6.3 … 10.0 | 65kA | 65kA | --- | 100-C12*10 | 140M-C2E-C10 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-CT**-CC10… | F | --- | --- | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 103S-CT**-CC10… | 6.3 … 10.0 | 65kA | 65kA | --- | 100-C16*10 | 140M-C2E-C10 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-BT**-CC16… | F | --- | 12 | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 103S-BT**-CC16… | 10.0 … 12.0 | 30kA | 30kA | --- | 100-C12*10 | 140M-C2E-C16 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-CT**-CC16… | F | --- | 13 | 5 | 5 | 10 | --- | 16 | 15.2 | 14 | --- | 103S-CT**-CC16… | 10.0 … 16.0 | 30kA | 30kA | --- | 100-C16*10 | 140M-C2E-C16 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-DT**-CC16… | F | --- | 14 | 5 | 5 | 10 | --- | 16 | 15.2 | 14 | --- | 103S-DT**-CC16… | 10.0 … 16.0 | 30kA | 30kA | --- | 100-C23*10 | 140M-C2E-C16 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-DT**-CC20… | F | --- | 15 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 103S-DT**-CC20… | 14.5 … 20.0 | 10kA | 10kA | --- | 100-C23*10 | 140M-C2E-C20 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
2 Component Reversing Starter w/ Standard Bus Bar Mount - C Frame MPCB
AB107S-AT**-CA16… | E | E | 1 | --- | --- | --- | --- | 0.16 | 0.16 | 0.16 | 0.16 | 107S-AT**-CA16… | 0.1 … 0.16 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-A16 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-C-PNC23 | 655 | 1, 5, 6 | E205542, 1:4, 2:2
AB107S-AT**-CA25… | E | E | 2 | --- | --- | --- | --- | 0.25 | 0.25 | 0.25 | 0.25 | 107S-AT**-CA25… | 0.16 … 0.25 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-A25 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-AT**-CA40… | E | E | 3 | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 107S-AT**-CA40… | 0.25 … 0.40 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-A40 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-AT**-CA63… | E | E | 4 | --- | --- | --- | --- | 0.63 | 0.63 | 0.63 | 0.63 | 107S-AT**-CA63… | 0.40 … 0.63 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-A63 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-AT**-CB10… | E | E | 5 | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 107S-AT**-CB10… | 0.63 … 1.0 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-B10 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-AT**-CB16… | E | E | 6 | --- | --- | 1 | 1 | 1.6 | 1.6 | 1.6 | 1.4 | 107S-AT**-CB16… | 1.0 … 1.6 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-B16 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-AT**-CB25… | E | F | 7 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 107S-AT**-CB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-C2E-B25 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-AT**-CB40… | F | F | 8 | 1 | 1 | 3 | 3 | 4 | 3.6 | 4 | 3.9 | 107S-AT**-CB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-C2E-B40 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-AT**-CB63… | F | --- | 9 | 1-1/2 | 2 | 5 | --- | 6 | 6.3 | 6.3 | --- | 107S-AT**-CB63… | 4.0 … 6.3 | 65kA | 65kA | --- | 104-C09*22 | 140M-C2E-B63 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-AT**-CC10… | F | --- | 10 | 2 | 2 | 5 | --- | 7.8 | 6.8 | 7.6 | --- | 107S-AT**-CC10… | 6.3 … 9.0 | 65kA | 65kA | --- | 104-C09*22 | 140M-C2E-C10 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-BT**-CC10… | F | --- | 11 | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 107S-BT**-CC10… | 6.3 … 10.0 | 65kA | 65kA | --- | 104-C12*22 | 140M-C2E-C10 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-CT**-CC10… | F | --- | --- | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 107S-CT**-CC10… | 6.3 … 10.0 | 65kA | 65kA | --- | 104-C16*22 | 140M-C2E-C10 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-BT**-CC16… | F | --- | 12 | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 107S-BT**-CC16… | 10.0 … 12.0 | 30kA | 30kA | --- | 104-C12*22 | 140M-C2E-C16 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-CT**-CC16… | F | --- | 13 | 5 | 5 | 10 | --- | 16 | 15.2 | 14 | --- | 107S-CT**-CC16… | 10.0 … 16.0 | 30kA | 30kA | --- | 104-C16*22 | 140M-C2E-C16 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-DT**-CC16… | F | --- | 14 | 5 | 5 | 10 | --- | 16 | 15.2 | 14 | --- | 107S-DT**-CC16… | 10.0 … 16.0 | 30kA | 30kA | --- | 104-C23*22 | 140M-C2E-C16 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-DT**-CC20… | F | --- | 15 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 107S-DT**-CC20… | 14.5 … 20.0 | 10kA | 10kA | --- | 104-C23*22 | 140M-C2E-C20 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-C-PNC23
2 Component DOL Starter w/ ISO Bus Bar Mount - C Frame MPCB
AB103S-AS**-CA16… | E | E | 1 | --- | --- | --- | --- | 0.16 | 0.16 | 0.16 | 0.16 | 103S-AS**-CA16… | 0.1 … 0.16 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-A16 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23 | 655 | 1, 5, 6 | E205542, 1:4, 2:2
AB103S-AS**-CA25… | E | E | 2 | --- | --- | --- | --- | 0.25 | 0.25 | 0.25 | 0.25 | 103S-AS**-CA25… | 0.16 … 0.25 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-A25 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AS**-CA40… | E | E | 3 | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 103S-AS**-CA40… | 0.25 … 0.40 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-A40 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AS**-CA63… | E | E | 4 | --- | --- | --- | --- | 0.63 | 0.63 | 0.63 | 0.63 | 103S-AS**-CA63… | 0.40 … 0.63 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-A63 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AS**-CB10… | E | E | 5 | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 103S-AS**-CB10… | 0.63 … 1.0 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-B10 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AS**-CB16… | E | E | 6 | --- | --- | 1 | 1 | 1.6 | 1.6 | 1.6 | 1.4 | 103S-AS**-CB16… | 1.0 … 1.6 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-B16 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AS**-CB25… | E | F | 7 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 103S-AS**-CB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-C2E-B25 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AS**-CB40… | F | F | 8 | 1 | 1 | 3 | 3 | 4 | 3.6 | 4 | 3.9 | 103S-AS**-CB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-C2E-B40 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AS**-CB63… | F | --- | 9 | 1-1/2 | 2 | 5 | --- | 6 | 6.3 | 6.3 | --- | 103S-AS**-CB63… | 4.0 … 6.3 | 65kA | 65kA | --- | 100-C09*10 | 140M-C2E-B63 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AS**-CC10… | F | --- | 10 | 2 | 2 | 5 | --- | 7.8 | 6.8 | 7.6 | --- | 103S-AS**-CC10… | 6.3 … 9.0 | 65kA | 65kA | --- | 100-C09*10 | 140M-C2E-C10 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-BS**-CC10… | F | --- | 11 | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 103S-BS**-CC10… | 6.3 … 10.0 | 65kA | 65kA | --- | 100-C12*10 | 140M-C2E-C10 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-CS**-CC10… | F | --- | --- | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 103S-CS**-CC10… | 6.3 … 10.0 | 65kA | 65kA | --- | 100-C16*10 | 140M-C2E-C10 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-BS**-CC16… | F | --- | 12 | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 103S-BS**-CC16… | 10.0 … 12.0 | 30kA | 30kA | --- | 100-C12*10 | 140M-C2E-C16 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-CS**-CC16… | F | --- | 13 | 5 | 5 | 10 | --- | 16 | 15.2 | 14 | --- | 103S-CS**-CC16… | 10.0 … 16.0 | 30kA | 30kA | --- | 100-C16*10 | 140M-C2E-C16 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-DS**-CC16… | F | --- | 14 | 5 | 5 | 10 | --- | 16 | 15.2 | 14 | --- | 103S-DS**-CC16… | 10.0 … 16.0 | 30kA | 30kA | --- | 100-C23*10 | 140M-C2E-C16 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-DS**-CC20… | F | --- | 15 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 103S-DS**-CC20… | 14.5 … 20.0 | 10kA | 10kA | --- | 100-C23*10 | 140M-C2E-C20 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-C-PNC23
2 Component Reversing Starter w/ ISO Bus Bar Mount - C Frame MPCB
AB107S-AS**-CA16… | E | E | 1 | --- | --- | --- | --- | 0.16 | 0.16 | 0.16 | 0.16 | 107S-AS**-CA16… | 0.1 … 0.16 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-A16 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-C-PNC23 | 655 | 1, 5, 6 | E205542, 1:4, 2:2
AB107S-AS**-CA25… | E | E | 2 | --- | --- | --- | --- | 0.25 | 0.25 | 0.25 | 0.25 | 107S-AS**-CA25… | 0.16 … 0.25 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-A25 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-AS**-CA40… | E | E | 3 | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 107S-AS**-CA40… | 0.25 … 0.40 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-A40 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-AS**-CA63… | E | E | 4 | --- | --- | --- | --- | 0.63 | 0.63 | 0.63 | 0.63 | 107S-AS**-CA63… | 0.40 … 0.63 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-A63 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-AS**-CB10… | E | E | 5 | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 107S-AS**-CB10… | 0.63 … 1.0 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-B10 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-AS**-CB16… | E | E | 6 | --- | --- | 1 | 1 | 1.6 | 1.6 | 1.6 | 1.4 | 107S-AS**-CB16… | 1.0 … 1.6 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-B16 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-AS**-CB25… | E | F | 7 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 107S-AS**-CB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-C2E-B25 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-AS**-CB40… | F | F | 8 | 1 | 1 | 3 | 3 | 4 | 3.6 | 4 | 3.9 | 107S-AS**-CB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-C2E-B40 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-AS**-CB63… | F | --- | 9 | 1-1/2 | 2 | 5 | --- | 6 | 6.3 | 6.3 | --- | 107S-AS**-CB63… | 4.0 … 6.3 | 65kA | 65kA | --- | 104-C09*22 | 140M-C2E-B63 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-AS**-CC10… | F | --- | 10 | 2 | 2 | 5 | --- | 7.8 | 6.8 | 7.6 | --- | 107S-AS**-CC10… | 6.3 … 9.0 | 65kA | 65kA | --- | 104-C09*22 | 140M-C2E-C10 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-BS**-CC10… | F | --- | 11 | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 107S-BS**-CC10… | 6.3 … 10.0 | 65kA | 65kA | --- | 104-C12*22 | 140M-C2E-C10 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-CS**-CC10… | F | --- | --- | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 107S-CS**-CC10… | 6.3 … 10.0 | 65kA | 65kA | --- | 104-C16*22 | 140M-C2E-C10 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-BS**-CC16… | F | --- | 12 | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 107S-BS**-CC16… | 10.0 … 12.0 | 30kA | 30kA | --- | 104-C12*22 | 140M-C2E-C16 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-CS**-CC16… | F | --- | 13 | 5 | 5 | 10 | --- | 16 | 15.2 | 14 | --- | 107S-CS**-CC16… | 10.0 … 16.0 | 30kA | 30kA | --- | 104-C16*22 | 140M-C2E-C16 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-DS**-CC16… | F | --- | 14 | 5 | 5 | 10 | --- | 16 | 15.2 | 14 | --- | 107S-DS**-CC16… | 10.0 … 16.0 | 30kA | 30kA | --- | 104-C23*22 | 140M-C2E-C16 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-C-PNC23
AB107S-DS**-CC20… | F | --- | 15 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 107S-DS**-CC20… | 14.5 … 20.0 | 10kA | 10kA | --- | 104-C23*22 | 140M-C2E-C20 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-C-PNC23
2 Component DOL Starter w/ Standard Bus Bar Mount - D Frame MPCB
AB103S-AT**-DB25… | E | F | 17 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 103S-AT**-DB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-D8E-B25 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23 | 655 | 1, 5, 6 | E205542, 1:4, 2:2
AB103S-DT**-DB25… | E | E | 18 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 103S-DT**-DB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 100-C23*10 | 140M-D8E-B25 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-AT**-DB40… | F | F | 19 | 1 | 1 | 3 | 3 | 4 | 3.6 | 4 | 3.9 | 103S-AT**-DB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-D8E-B40 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-DT**-DB40… | E | E | 21 | 1 | 1 | 3 | 3 | 4 | 3.6 | 4 | 3.9 | 103S-DT**-DB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 100-C23*10 | 140M-D8E-B40 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-AT**-DB63… | F | F | 22 | 1-1/2 | 2 | 5 | 5 | 6 | 6.3 | 6.3 | 6.1 | 103S-AT**-DB63… | 4.0 … 6.3 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-D8E-B63 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-ET**-DB63… | E | E | 23 | 1-1/2 | 2 | 5 | 5 | 6 | 6.3 | 6.3 | 6.1 | 103S-ET**-DB63… | 4.0 … 6.3 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-D8E-B63 | 141A-GS54RR25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103S-AT**-DC10… | F | F | 24 | 2 | 2 | 5 | 7-1/2 | 7.8 | 6.8 | 7.6 | 9 | 103S-AT**-DC10… | 6.3 … 9.0 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-D8E-C10 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-BT**-DC10… | F | F | 25 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103S-BT**-DC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 100-C12*10 | 140M-D8E-C10 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-CT**-DC10… | F | F | 26 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103S-CT**-DC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 100-C16*10 | 140M-D8E-C10 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-ET**-DC10… | E | E | 27 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103S-ET**-DC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-D8E-C10 | 141A-GS54RR25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103S-BT**-DC16… | F | F | -- | 3 | 3 | 7-1/2 | 10 | 11 | 9.6 | 11 | 11 | 103S-BT**-DC16… | 10.0 … 12.0 | 65kA | 65kA | 30kA | 100-C12*10 | 140M-D8E-C16 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-CT**-DC16… | F | F | 28 | 5 | 5 | 10 | 10 | 16 | 15.2 | 14 | 11 | 103S-CT**-DC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 100-C16*10 | 140M-D8E-C16 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-DT**-DC16… | F | F | 29 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 103S-DT**-DC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 100-C23*10 | 140M-D8E-C16 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-ET**-DC16… | E | E | 30 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 103S-ET**-DC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-D8E-C16 | 141A-GS54RR25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103S-DT**-DC20… | F | --- | 31 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 103S-DT**-DC20… | 14.5 … 20.0 | 65kA | 65kA | --- | 100-C23*10 | 140M-D8E-C20 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-ET**-DC20… | E | --- | 32 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 103S-ET**-DC20… | 14.5 … 20.0 | 65kA | 65kA | --- | 100-C30*10 | 140M-D8E-C20 | 141A-GS54RR25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103S-DT**-DC25… | F | --- | 33 | 5 | 7-1/2 | 15 | --- | 25 | 22 | 21 | --- | 103S-DT**-DC25… | 18.0 … 22.0 | 65kA | 65kA | --- | 100-C23*10 | 140M-D8E-C25 | 141A-GS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-ET**-DC25… | E | --- | 34 | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 103S-ET**-DC25… | 18.0 … 25.0 | 65kA | 65kA | --- | 100-C30*10 | 140M-D8E-C25 | 141A-GS54RR25 | --- | 140M-C-TE1 | 140M-D-PNC37
2 Component Reversing Starter w/ Standard Bus Bar Mount - D Frame MPCB
AB107S-AT**-DB25… | E | F | 17 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 107S-AT**-DB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-D8E-B25 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-D-PNC23 | 655 | 1, 5, 6 | E205542, 1:4, 2:2
AB107S-DT**-DB25… | E | E | 18 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 107S-DT**-DB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 104-C23*22 | 140M-D8E-B25 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-AT**-DB40… | F | F | 19 | 1 | 1 | 3 | 3 | 4 | 3.6 | 4 | 3.9 | 107S-AT**-DB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-D8E-B40 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-DT**-DB40… | E | E | 21 | 1 | 1 | 3 | 3 | 4 | 3.6 | 4 | 3.9 | 107S-DT**-DB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 104-C23*22 | 140M-D8E-B40 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-AT**-DB63… | F | F | 22 | 1-1/2 | 2 | 5 | 5 | 6 | 6.3 | 6.3 | 6.1 | 107S-AT**-DB63… | 4.0 … 6.3 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-D8E-B63 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-ET**-DB63… | E | E | 23 | 1-1/2 | 2 | 5 | 5 | 6 | 6.3 | 6.3 | 6.1 | 107S-ET**-DB63… | 4.0 … 6.3 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-D8E-B63 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-D-PNC37
AB107S-AT**-DC10… | F | F | 24 | 2 | 2 | 5 | 7-1/2 | 7.8 | 6.8 | 7.6 | 9 | 107S-AT**-DC10… | 6.3 … 9.0 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-D8E-C10 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-BT**-DC10… | F | F | 25 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 107S-BT**-DC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 104-C12*22 | 140M-D8E-C10 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-CT**-DC10… | F | F | 26 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 107S-CT**-DC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 104-C16*22 | 140M-D8E-C10 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-ET**-DC10… | E | E | 27 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 107S-ET**-DC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-D8E-C10 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-D-PNC37
AB107S-BT**-DC16… | F | F | -- | 3 | 3 | 7-1/2 | 10 | 11 | 9.6 | 11 | 11 | 107S-BT**-DC16… | 10.0 … 12.0 | 65kA | 65kA | 30kA | 104-C12*22 | 140M-D8E-C16 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-CT**-DC16… | F | F | 28 | 5 | 5 | 10 | 10 | 16 | 15.2 | 14 | 11 | 107S-CT**-DC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 104-C16*22 | 140M-D8E-C16 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-DT**-DC16… | F | F | 29 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 107S-DT**-DC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 104-C23*22 | 140M-D8E-C16 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-ET**-DC16… | E | E | 30 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 107S-ET**-DC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-D8E-C16 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-D-PNC37
AB107S-DT**-DC20… | F | --- | 31 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 107S-DT**-DC20… | 14.5 … 20.0 | 65kA | 65kA | --- | 104-C23*22 | 140M-D8E-C20 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-ET**-DC20… | E | --- | 32 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 107S-ET**-DC20… | 14.5 … 20.0 | 65kA | 65kA | --- | 104-C30*22 | 140M-D8E-C20 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-D-PNC37
AB107S-DT**-DC25… | F | --- | 33 | 5 | 7-1/2 | 15 | --- | 25 | 22 | 21 | --- | 107S-DT**-DC25… | 18.0 … 22.0 | 65kA | 65kA | --- | 104-C23*22 | 140M-D8E-C25 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-ET**-DC25… | E | --- | 34 | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 107S-ET**-DC25… | 18.0 … 25.0 | 65kA | 65kA | --- | 104-C30*22 | 140M-D8E-C25 | 141A-GS54RR25 | 141A-GS45R | 140M-C-TE1 | 140M-D-PNC37
2 Component DOL Starter w/ ISO Bus Bar Mount - D Frame MPCB
AB103S-AS**-DB25… | E | F | 17 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 103S-AS**-DB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-D8E-B25 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23 | 655 | 1, 5, 6 | E205542, 1:4, 2:2
AB103S-DS**-DB25… | E | E | 18 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 103S-DS**-DB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 100-C23*10 | 140M-D8E-B25 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-AS**-DB40… | F | F | 19 | 1 | 1 | 3 | 3 | 4 | 3.6 | 4 | 3.9 | 103S-AS**-DB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-D8E-B40 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-DS**-DB40… | E | E | 21 | 1 | 1 | 3 | 3 | 4 | 3.6 | 4 | 3.9 | 103S-DS**-DB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 100-C23*10 | 140M-D8E-B40 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-AS**-DB63… | F | F | 22 | 1-1/2 | 2 | 5 | 5 | 6 | 6.3 | 6.3 | 6.1 | 103S-AS**-DB63… | 4.0 … 6.3 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-D8E-B63 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-ES**-DB63… | E | E | 23 | 1-1/2 | 2 | 5 | 5 | 6 | 6.3 | 6.3 | 6.1 | 103S-ES**-DB63… | 4.0 … 6.3 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-D8E-B63 | 141A-SS54RR25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103S-AS**-DC10… | F | F | 24 | 2 | 2 | 5 | 7-1/2 | 7.8 | 6.8 | 7.6 | 9 | 103S-AS**-DC10… | 6.3 … 9.0 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-D8E-C10 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-BS**-DC10… | F | F | 25 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103S-BS**-DC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 100-C12*10 | 140M-D8E-C10 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-CS**-DC10… | F | F | 26 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103S-CS**-DC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 100-C16*10 | 140M-D8E-C10 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-ES**-DC10… | E | E | 27 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103S-ES**-DC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-D8E-C10 | 141A-SS54RR25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103S-BS**-DC16… | F | F | -- | 3 | 3 | 7-1/2 | 10 | 11 | 9.6 | 11 | 11 | 103S-BS**-DC16… | 10.0 … 12.0 | 65kA | 65kA | 30kA | 100-C12*10 | 140M-D8E-C16 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-CS**-DC16… | F | F | 28 | 5 | 5 | 10 | 10 | 16 | 15.2 | 14 | 11 | 103S-CS**-DC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 100-C16*10 | 140M-D8E-C16 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-DS**-DC16… | F | F | 29 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 103S-DS**-DC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 100-C23*10 | 140M-D8E-C16 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-ES**-DC16… | E | E | 30 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 103S-ES**-DC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-D8E-C16 | 141A-SS54RR25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103S-DS**-DC20… | F | --- | 31 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 103S-DS**-DC20… | 14.5 … 20.0 | 65kA | 65kA | --- | 100-C23*10 | 140M-D8E-C20 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-ES**-DC20… | E | --- | 32 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 103S-ES**-DC20… | 14.5 … 20.0 | 65kA | 65kA | --- | 100-C30*10 | 140M-D8E-C20 | 141A-SS54RR25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103S-DS**-DC25… | F | --- | 33 | 5 | 7-1/2 | 15 | --- | 25 | 22 | 21 | --- | 103S-DS**-DC25… | 18.0 … 22.0 | 65kA | 65kA | --- | 100-C23*10 | 140M-D8E-C25 | 141A-SS45RR25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-ES**-DC25… | E | --- | 34 | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 103S-ES**-DC25… | 18.0 … 25.0 | 65kA | 65kA | --- | 100-C30*10 | 140M-D8E-C25 | 141A-SS54RR25 | --- | 140M-C-TE1 | 140M-D-PNC37
2 Component Reversing Starter w/ ISO Bus Bar Mount - D Frame MPCB
AB107S-AS**-DB25… | E | F | 17 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 107S-AS**-DB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-D8E-B25 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-D-PNC23 | 655 | 1, 5, 6 | E205542, 1:4, 2:2
AB107S-DS**-DB25… | E | E | 18 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 107S-DS**-DB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 104-C23*22 | 140M-D8E-B25 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-AS**-DB40… | F | F | 19 | 1 | 1 | 3 | 3 | 4 | 3.6 | 4 | 3.9 | 107S-AS**-DB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-D8E-B40 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-DS**-DB40… | E | E | 21 | 1 | 1 | 3 | 3 | 4 | 3.6 | 4 | 3.9 | 107S-DS**-DB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 104-C23*22 | 140M-D8E-B40 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-AS**-DB63… | F | F | 22 | 1-1/2 | 2 | 5 | 5 | 6 | 6.3 | 6.3 | 6.1 | 107S-AS**-DB63… | 4.0 … 6.3 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-D8E-B63 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-ES**-DB63… | E | E | 23 | 1-1/2 | 2 | 5 | 5 | 6 | 6.3 | 6.3 | 6.1 | 107S-ES**-DB63… | 4.0 … 6.3 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-D8E-B63 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-D-PNC37
AB107S-AS**-DC10… | F | F | 24 | 2 | 2 | 5 | 7-1/2 | 7.8 | 6.8 | 7.6 | 9 | 107S-AS**-DC10… | 6.3 … 9.0 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-D8E-C10 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-BS**-DC10… | F | F | 25 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 107S-BS**-DC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 104-C12*22 | 140M-D8E-C10 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-CS**-DC10… | F | F | 26 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 107S-CS**-DC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 104-C16*22 | 140M-D8E-C10 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-ES**-DC10… | E | E | 27 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 107S-ES**-DC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-D8E-C10 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-D-PNC37
AB107S-BS**-DC16… | F | F | -- | 3 | 3 | 7-1/2 | 10 | 11 | 9.6 | 11 | 11 | 107S-BS**-DC16… | 10.0 … 12.0 | 65kA | 65kA | 30kA | 104-C12*22 | 140M-D8E-C16 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-CS**-DC16… | F | F | 28 | 5 | 5 | 10 | 10 | 16 | 15.2 | 14 | 11 | 107S-CS**-DC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 104-C16*22 | 140M-D8E-C16 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-DS**-DC16… | F | F | 29 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 107S-DS**-DC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 104-C23*22 | 140M-D8E-C16 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-ES**-DC16… | E | E | 30 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 107S-ES**-DC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-D8E-C16 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-D-PNC37
AB107S-DS**-DC20… | F | --- | 31 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 107S-DS**-DC20… | 14.5 … 20.0 | 65kA | 65kA | --- | 104-C23*22 | 140M-D8E-C20 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-ES**-DC20… | E | --- | 32 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 107S-ES**-DC20… | 14.5 … 20.0 | 65kA | 65kA | --- | 104-C30*22 | 140M-D8E-C20 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-D-PNC37
AB107S-DS**-DC25… | F | --- | 33 | 5 | 7-1/2 | 15 | --- | 25 | 22 | 21 | --- | 107S-DS**-DC25… | 18.0 … 22.0 | 65kA | 65kA | --- | 104-C23*22 | 140M-D8E-C25 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-D-PNC23
AB107S-ES**-DC25… | E | --- | 34 | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 107S-ES**-DC25… | 18.0 … 25.0 | 65kA | 65kA | --- | 104-C30*22 | 140M-D8E-C25 | 141A-SS54RR25 | 141A-SS45R | 140M-C-TE1 | 140M-D-PNC37
2 Component DOL Starter w/ Standard Bus Bar Mount - F Frame MPCB
AB103S-ET**-FC10… | E | E | 36 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103S-ET**-FC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-F8E-C10 | 141A-GS54RR45 | --- | 140M-F-TE | 140M-F-PNC37 | 1008 | 1, 5, 6 | E205542, 1:4, 2:2
AB103S-ET**-FC16… | E | E | 37 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 103S-ET**-FC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-F8E-C16 | 141A-GS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-ET**-FC20… | E | E | 38 | 5 | 7-1/2 | 15 | 20 | 17.5 | 20 | 20 | 20 | 103S-ET**-FC20… | 14.5 … 20.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-F8E-C20 | 141A-GS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-FT**FC20… | E | E | --- | 5 | 7-1/2 | 15 | 20 | 17.5 | 20 | 20 | 20 | 103S-FT**-FC20… | 14.5 … 20.0 | 65kA | 65kA | 30kA | 100-C37*10 | 140M-F8E-C20 | 141A-GS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-ET**-FC25… | E | E | 39 | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 103S-ET**-FC25… | 18.0 … 25.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-F8E-C25 | 141A-GS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-FT**-FC25… | E | E | --- | 7-1/2 | 10 | 20 | 25 | 25 | 25 | 25 | 25 | 103S-FT**-FC25… | 18.0 … 25.0 | 65kA | 65kA | 30kA | 100-C37*10 | 140M-F8E-C25 | 141A-GS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-GT**-FC25… | E | E | 40 | 7-1/2 | 10 | 20 | 25 | 25 | 25 | 25 | 25 | 103S-GT**-FC25… | 18.0 … 25.0 | 65kA | 65kA | 30kA | 100-C43*10 | 140M-F8E-C25 | 141A-GS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-ET**-FC32… | E | E | 41 | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 103S-ET**-FC32… | 23.0 … 28.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-F8E-C32 | 141A-GS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-FT**-FC32… | E | E | 42 | 10 | 10 | 25 | 30 | 32 | 28 | 32 | 32 | 103S-FT**-FC32… | 23.0 … 32.0 | 65kA | 65kA | 30kA | 100-C37*10 | 140M-F8E-C32 | 141A-GS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-GT**-FC32… | E | E | 43 | 10 | 10 | 25 | 30 | 32 | 28 | 32 | 32 | 103S-GT**-FC32… | 23.0 … 32.0 | 65kA | 65kA | 30kA | 100-C43*10 | 140M-F8E-C32 | 141A-GS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-FT**-FC45… | E | --- | 45 | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 103S-FT**-FC45… | 32.0 … 34.0 | 65kA | 65kA | --- | 100-C37*10 | 140M-F8E-C45 | 141A-GS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-GT**-FC45… | E | --- | 46 | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 103S-GT**-FC45… | 32.0 … 42.0 | 65kA | 65kA | --- | 100-C43*10 | 140M-F8E-C45 | 141A-GS63RR45 | --- | 140M-F-TE | 140M-F-PNC43
2 Component Reversing Starter w/ Standard Bus Bar Mount - F Frame MPCB
AB107S-ET**-FC10… | E | E | 36 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 107S-ET**-FC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-F8E-C10 | 141A-GS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37 | 1008 | 1, 5, 6 | E205542, 1:4, 2:2
AB107S-ET**-FC16… | E | E | 37 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 107S-ET**-FC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-F8E-C16 | 141A-GS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-ET**-FC20… | E | E | 38 | 5 | 7-1/2 | 15 | 20 | 17.5 | 20 | 20 | 20 | 107S-ET**-FC20… | 14.5 … 20.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-F8E-C20 | 141A-GS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-FT**-FC20… | E | E | --- | 5 | 7-1/2 | 15 | 20 | 17.5 | 20 | 20 | 20 | 107S-FT**-FC20… | 14.5 … 20.0 | 65kA | 65kA | 30kA | 104-C37*22 | 140M-F8E-C20 | 141A-GS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-ET**-FC25… | E | E | 39 | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 107S-ET**-FC25… | 18.0 … 25.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-F8E-C25 | 141A-GS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-FT**-FC25… | E | E | --- | 7-1/2 | 10 | 20 | 25 | 25 | 25 | 25 | 25 | 107S-FT**-FC25… | 18.0 … 25.0 | 65kA | 65kA | 30kA | 104-C37*22 | 140M-F8E-C25 | 141A-GS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-GT**-FC25… | E | E | 40 | 7-1/2 | 10 | 20 | 25 | 25 | 25 | 25 | 25 | 107S-GT**-FC25… | 18.0 … 25.0 | 65kA | 65kA | 30kA | 104-C43*22 | 140M-F8E-C25 | 141A-GS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-ET**-FC32… | E | E | 41 | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 107S-ET**-FC32… | 23.0 … 28.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-F8E-C32 | 141A-GS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-FT**-FC32… | E | E | 42 | 10 | 10 | 25 | 30 | 32 | 28 | 32 | 32 | 107S-FT**-FC32… | 23.0 … 32.0 | 65kA | 65kA | 30kA | 104-C37*22 | 140M-F8E-C32 | 141A-GS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-GT**-FC32… | E | E | 43 | 10 | 10 | 25 | 30 | 32 | 28 | 32 | 32 | 107S-GT**-FC32… | 23.0 … 32.0 | 65kA | 65kA | 30kA | 104-C43*22 | 140M-F8E-C32 | 141A-GS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-FT**-FC45… | E | --- | 45 | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 107S-FT**-FC45… | 32.0 … 34.0 | 65kA | 65kA | --- | 104-C37*22 | 140M-F8E-C45 | 141A-GS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-GT**-FC45… | E | --- | 46 | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 107S-GT**-FC45… | 32.0 … 42.0 | 65kA | 65kA | --- | 104-C43*22 | 140M-F8E-C45 | 141A-GS63RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC43
2 Component DOL Starter w/ ISO Bus Bar Mount - F Frame MPCB
AB103S-ES**-FC10… | E | E | 36 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103S-ES**-FC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-F8E-C10 | 141A-SS54RR45 | --- | 140M-F-TE | 140M-F-PNC37 | 1008 | 1, 5, 6 | E205542, 1:4, 2:2
AB103S-ES**-FC16… | E | E | 37 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 103S-ES**-FC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-F8E-C16 | 141A-SS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-ES**-FC20… | E | E | 38 | 5 | 7-1/2 | 15 | 20 | 17.5 | 20 | 20 | 20 | 103S-ES**-FC20… | 14.5 … 20.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-F8E-C20 | 141A-SS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-FS**-FC20… | E | E | --- | 5 | 7-1/2 | 15 | 20 | 17.5 | 20 | 20 | 20 | 103S-FS**-FC20… | 14.5 … 20.0 | 65kA | 65kA | 30kA | 100-C37*10 | 140M-F8E-C20 | 141A-SS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-ES**-FC25… | E | E | 39 | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 103S-ES**-FC25… | 18.0 … 25.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-F8E-C25 | 141A-SS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-FS**-FC25… | E | E | --- | 7-1/2 | 10 | 20 | 25 | 25 | 25 | 25 | 25 | 103S-FS**-FC25… | 18.0 … 25.0 | 65kA | 65kA | 30kA | 100-C37*10 | 140M-F8E-C25 | 141A-SS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-GS**-FC25… | E | E | 40 | 7-1/2 | 10 | 20 | 25 | 25 | 25 | 25 | 25 | 103S-GS**-FC25… | 18.0 … 25.0 | 65kA | 65kA | 30kA | 100-C43*10 | 140M-F8E-C25 | 141A-SS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-ES**-FC32… | E | E | 41 | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 103S-ES**-FC32… | 23.0 … 28.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-F8E-C32 | 141A-SS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-FS**-FC32… | E | E | 42 | 10 | 10 | 25 | 30 | 32 | 28 | 32 | 32 | 103S-FS**-FC32… | 23.0 … 32.0 | 65kA | 65kA | 30kA | 100-C37*10 | 140M-F8E-C32 | 141A-SS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-GS**-FC32… | E | E | 43 | 10 | 10 | 25 | 30 | 32 | 28 | 32 | 32 | 103S-GS**-FC32… | 23.0 … 32.0 | 65kA | 65kA | 30kA | 100-C43*10 | 140M-F8E-C32 | 141A-SS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-FS**-FC45… | E | --- | 45 | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 103S-FS**-FC45… | 32.0 … 34.0 | 65kA | 65kA | --- | 100-C37*10 | 140M-F8E-C45 | 141A-SS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-GS**-FC45… | E | --- | 46 | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 103S-GS**-FC45… | 32.0 … 42.0 | 65kA | 65kA | --- | 100-C43*10 | 140M-F8E-C45 | 141A-SS63RR45 | --- | 140M-F-TE | 140M-F-PNC43
2 Component Reversing Starter w/ ISO Bus Bar Mount - F Frame MPCB
AB107S-ES**-FC10… | E | E | 36 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 107S-ES**-FC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-F8E-C10 | 141A-SS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37 | 1008 | 1, 5, 6 | E205542, 1:4, 2:2
AB107S-ES**-FC16… | E | E | 37 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 107S-ES**-FC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-F8E-C16 | 141A-SS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-ES**-FC20… | E | E | 38 | 5 | 7-1/2 | 15 | 20 | 17.5 | 20 | 20 | 20 | 107S-ES**-FC20… | 14.5 … 20.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-F8E-C20 | 141A-SS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-FS**-FC20… | E | E | --- | 5 | 7-1/2 | 15 | 20 | 17.5 | 20 | 20 | 20 | 107S-FS**-FC20… | 14.5 … 20.0 | 65kA | 65kA | 30kA | 104-C37*22 | 140M-F8E-C20 | 141A-SS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-ES**-FC25… | E | E | 39 | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 107S-ES**-FC25… | 18.0 … 25.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-F8E-C25 | 141A-SS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-FS**-FC25… | E | E | --- | 7-1/2 | 10 | 20 | 25 | 25 | 25 | 25 | 25 | 107S-FS**-FC25… | 18.0 … 25.0 | 65kA | 65kA | 30kA | 104-C37*22 | 140M-F8E-C25 | 141A-SS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-GS**-FC25… | E | E | 40 | 7-1/2 | 10 | 20 | 25 | 25 | 25 | 25 | 25 | 107S-GS**-FC25… | 18.0 … 25.0 | 65kA | 65kA | 30kA | 104-C43*22 | 140M-F8E-C25 | 141A-SS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-ES**-FC32… | E | E | 41 | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 107S-ES**-FC32… | 23.0 … 28.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-F8E-C32 | 141A-SS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-FS**-FC32… | E | E | 42 | 10 | 10 | 25 | 30 | 32 | 28 | 32 | 32 | 107S-FS**-FC32… | 23.0 … 32.0 | 65kA | 65kA | 30kA | 104-C37*22 | 140M-F8E-C32 | 141A-SS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-GS**-FC32… | E | E | 43 | 10 | 10 | 25 | 30 | 32 | 28 | 32 | 32 | 107S-GS**-FC32… | 23.0 … 32.0 | 65kA | 65kA | 30kA | 104-C43*22 | 140M-F8E-C32 | 141A-SS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-FS**-FC45… | E | --- | 45 | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 107S-FS**-FC45… | 32.0 … 34.0 | 65kA | 65kA | --- | 104-C37*22 | 140M-F8E-C45 | 141A-SS54RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC37
AB107S-GS**-FC45… | E | --- | 46 | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 107S-GS**-FC45… | 32.0 … 42.0 | 65kA | 65kA | --- | 104-C43*22 | 140M-F8E-C45 | 141A-SS63RR45 | 141A-GS45R | 140M-F-TE | 140M-F-PNC43
2 Component DOL Starter w/ Panel Mount - C Frame MPCB
AB103S-AW**-CA16… | E | E | 1 | --- | --- | --- | --- | 0.16 | 0.16 | 0.16 | 0.16 | 103S-AW**-CA16… | 0.1 … 0.16 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-A16 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-C-PNC23 | 655 | 1, 5, 6 | E205542, 1:4, 2:2
AB103S-AW**-CA25… | E | E | 2 | --- | --- | --- | --- | 0.25 | 0.25 | 0.25 | 0.25 | 103S-AW**-CA25… | 0.16 … 0.25 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-A25 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AW**-CA40… | E | E | 3 | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 103S-AW**-CA40… | 0.25 … 0.40 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-A40 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AW**-CA63… | E | E | 4 | --- | --- | --- | --- | 0.63 | 0.63 | 0.63 | 0.63 | 103S-AW**-CA63… | 0.40 … 0.63 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-A63 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AW**-CB10… | E | E | 5 | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 103S-AW**-CB10… | 0.63 … 1.0 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-B10 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AW**-CB16… | E | E | 6 | --- | --- | 1 | 1 | 1.6 | 1.6 | 1.6 | 1.4 | 103S-AW**-CB16… | 1.0 … 1.6 | 65kA | 65kA | 47kA | 100-C09*10 | 140M-C2E-B16 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AW**-CB25… | E | F | 7 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 103S-AW**-CB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-C2E-B25 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AW**-CB40… | F | F | 8 | 1 | 1 | 3 | 3 | 4 | 3.6 | 4 | 3.9 | 103S-AW**-CB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-C2E-B40 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AW**-CB63… | F | --- | 9 | 1-1/2 | 2 | 5 | --- | 6 | 6.3 | 6.3 | --- | 103S-AW**-CB63… | 4.0 … 6.3 | 65kA | 65kA | --- | 100-C09*10 | 140M-C2E-B63 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-AW**-CC10… | F | --- | 10 | 2 | 2 | 5 | --- | 7.8 | 6.8 | 7.6 | --- | 103S-AW**-CC10… | 6.3 … 9.0 | 65kA | 65kA | --- | 100-C09*10 | 140M-C2E-C10 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-BW**-CC10… | F | --- | 11 | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 103S-BW**-CC10… | 6.3 … 10.0 | 65kA | 65kA | --- | 100-C12*10 | 140M-C2E-C10 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-CW**-CC10… | F | --- | --- | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 103S-CW**-CC10… | 6.3 … 10.0 | 65kA | 65kA | --- | 100-C16*10 | 140M-C2E-C10 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-BW**-CC16… | F | --- | 12 | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 103S-BW**-CC16… | 10.0 … 12.0 | 30kA | 30kA | --- | 100-C12*10 | 140M-C2E-C16 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-CW**-CC16… | F | --- | 13 | 5 | 5 | 10 | --- | 16 | 15.2 | 14 | --- | 103S-CW**-CC16… | 10.0 … 16.0 | 30kA | 30kA | --- | 100-C23*10 | 140M-C2E-C16 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-DW**-CC16… | F | --- | 14 | 5 | 5 | 10 | --- | 16 | 15.2 | 14 | --- | 103S-DW**-CC16… | 10.0 … 16.0 | 30kA | 30kA | --- | 100-C16*10 | 140M-C2E-C16 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-C-PNC23
AB103S-DW**-CC20… | F | --- | 15 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 103S-DW**-CC20… | 14.5 … 20.0 | 10kA | 10kA | --- | 100-C23*10 | 140M-C2E-C20 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-C-PNC23
2 Component Reversing Starter w/ Panel Mount - C Frame MPCB
AB107S-AW**-CA16… | E | E | 1 | --- | --- | --- | --- | 0.16 | 0.16 | 0.16 | 0.16 | 107S-AW**-CA16… | 0.1 … 0.16 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-A16 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-C-PNC23 | 655 | 1, 5, 6 | E205542, 1:4, 2:2
AB107S-AW**-CA25… | E | E | 2 | --- | --- | --- | --- | 0.25 | 0.25 | 0.25 | 0.25 | 107S-AW**-CA25… | 0.16 … 0.25 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-A25 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-C-PNC23
AB107S-AW**-CA40… | E | E | 3 | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 107S-AW**-CA40… | 0.25 … 0.40 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-A40 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-C-PNC23
AB107S-AW**-CA63… | E | E | 4 | --- | --- | --- | --- | 0.63 | 0.63 | 0.63 | 0.63 | 107S-AW**-CA63… | 0.40 … 0.63 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-A63 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-C-PNC23
AB107S-AW**-CB10… | E | E | 5 | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 107S-AW**-CB10… | 0.63 … 1.0 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-B10 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-C-PNC23
AB107S-AW**-CB16… | E | E | 6 | --- | --- | 1 | 1 | 1.6 | 1.6 | 1.6 | 1.4 | 107S-AW**-CB16… | 1.0 … 1.6 | 65kA | 65kA | 47kA | 104-C09*22 | 140M-C2E-B16 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-C-PNC23
AB107S-AW**-CB25… | E | F | 7 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 107S-AW**-CB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-C2E-B25 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-C-PNC23
AB107S-AW**-CB40… | F | F | 8 | 1 | 1 | 3 | 3 | 4 | 3.6 | 4 | 3.9 | 107S-AW**-CB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-C2E-B40 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-C-PNC23
AB107S-AW**-CB63… | F | --- | 9 | 1-1/2 | 2 | 5 | --- | 6 | 6.3 | 6.3 | --- | 107S-AW**-CB63… | 4.0 … 6.3 | 65kA | 65kA | --- | 104-C09*22 | 140M-C2E-B63 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-C-PNC23
AB107S-AW**-CC10… | F | --- | 10 | 2 | 2 | 5 | --- | 7.8 | 6.8 | 7.6 | --- | 107S-AW**-CC10… | 6.3 … 9.0 | 65kA | 65kA | --- | 104-C09*22 | 140M-C2E-C10 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-C-PNC23
AB107S-BW**-CC10… | F | --- | 11 | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 107S-BW**-CC10… | 6.3 … 10.0 | 65kA | 65kA | --- | 104-C12*22 | 140M-C2E-C10 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-C-PNC23
AB107S-CW**-CC10… | F | --- | --- | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 107S-EW**-CC10… | 6.3 … 10.0 | 65kA | 65kA | --- | 104-C16*22 | 140M-C2E-C10 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-C-PNC23
AB107S-BW**-CC16… | F | --- | 12 | 3 | 3 | 7-1/2 | --- | 11 | 9.6 | 11 | --- | 107S-BW**-CC16… | 10.0 … 12.0 | 30kA | 30kA | --- | 104-C12*22 | 140M-C2E-C16 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-C-PNC23
AB107S-CW**-CC16… | F | --- | 13 | 5 | 5 | 10 | --- | 16 | 15.2 | 14 | --- | 107S-EW**-CC16… | 10.0 … 16.0 | 30kA | 30kA | --- | 104-C16*22 | 140M-C2E-C16 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-C-PNC23
AB107S-DW**-CC16… | F | --- | 14 | 5 | 5 | 10 | --- | 16 | 15.2 | 14 | --- | 107S-DW**-CC16… | 10.0 … 16.0 | 30kA | 30kA | --- | 104-C23*22 | 140M-C2E-C16 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-C-PNC23
AB107S-DW**-CC20… | F | --- | 15 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 107S-DW**-CC20… | 14.5 … 20.0 | 10kA | 10kA | --- | 104-C23*22 | 140M-C2E-C20 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-C-PNC23
2 Component DOL Starter w/ Panel Mount - D Frame MPCB
AB103S-AW**-DB25… | E | F | 17 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 103S-AW**-DB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-D8E-B25 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-D-PNC23 | 655 | 1, 5, 6 | E205542, 1:4, 2:2
AB103S-DW**-DB25… | E | E | 18 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 103S-DW**-DB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 100-C23*10 | 140M-D8E-B25 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-AW**-DB40… | F | F | 19 | 1 | 1 | 3 | 3 | 4 | 3.6 | 4 | 3.9 | 103S-AW**-DB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-D8E-B40 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-DW**-DB40… | E | E | 21 | 1 | 1 | 3 | 3 | 4 | 3.6 | 4 | 3.9 | 103S-DW**-DB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 100-C23*10 | 140M-D8E-B40 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-AW**-DB63… | F | F | 22 | 1-1/2 | 2 | 5 | 5 | 6 | 6.3 | 6.3 | 6.1 | 103S-AW**-DB63… | 4.0 … 6.3 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-D8E-B63 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-EW**-DB63… | E | E | 23 | 1-1/2 | 2 | 5 | 5 | 6 | 6.3 | 6.3 | 6.1 | 103S-EW**-DB63… | 4.0 … 6.3 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-D8E-B63 | 141A-WS54RR | --- | 140M-C-TE1 | 140M-D-PNC37
AB103S-AW**-DC10… | F | F | 24 | 2 | 2 | 5 | 7-1/2 | 7.8 | 6.8 | 7.6 | 9 | 103S-AW**-DC10… | 6.3 … 9.0 | 65kA | 65kA | 30kA | 100-C09*10 | 140M-D8E-C10 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-BW**-DC10… | F | F | 25 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103S-BW**-DC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 100-C12*10 | 140M-D8E-C10 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-CW**-DC10… | F | F | 26 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103S-CW**-DC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 100-C16*10 | 140M-D8E-C10 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-EW**-DC10… | E | E | 27 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103S-EW**-DC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-D8E-C10 | 141A-WS54RR | --- | 140M-C-TE1 | 140M-D-PNC37
AB103S-BW**-DC16… | F | F | -- | 3 | 3 | 7-1/2 | 10 | 11 | 9.6 | 11 | 11 | 103S-BW**-DC16… | 10.0 … 12.0 | 65kA | 65kA | 30kA | 100-C12*10 | 140M-D8E-C16 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-CW**-DC16… | F | F | 28 | 5 | 5 | 10 | 10 | 16 | 15.2 | 14 | 11 | 103S-CW**-DC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 100-C16*10 | 140M-D8E-C16 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-DW**-DC16… | F | F | 29 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 103S-DW**-DC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 100-C23*10 | 140M-D8E-C16 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-EW**-DC16… | E | E | 30 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 103S-EW**-DC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-D8E-C16 | 141A-WS54RR | --- | 140M-C-TE1 | 140M-D-PNC37
AB103S-DW**-DC20… | F | --- | 31 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 103S-DW**-DC20… | 14.5 … 20.0 | 65kA | 65kA | --- | 100-C23*10 | 140M-D8E-C20 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-EW**-DC20… | E | --- | 32 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 103S-EW**-DC20… | 14.5 … 20.0 | 65kA | 65kA | --- | 100-C30*10 | 140M-D8E-C20 | 141A-WS54RR | --- | 140M-C-TE1 | 140M-D-PNC37
AB103S-DW**-DC25… | F | --- | 33 | 5 | 7-1/2 | 15 | --- | 25 | 22 | 21 | --- | 103S-DW**-DC25… | 18.0 … 22.0 | 65kA | 65kA | --- | 100-C23*10 | 140M-D8E-C25 | 141A-WS45RR | --- | 140M-C-TE1 | 140M-D-PNC23
AB103S-EW**-DC25… | E | --- | 34 | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 103S-EW**-DC25… | 18.0 … 25.0 | 65kA | 65kA | --- | 100-C30*10 | 140M-D8E-C25 | 141A-WS54RR | --- | 140M-C-TE1 | 140M-D-PNC37
2 Component Reversing Starter w/ Panel Mount - D Frame MPCB
AB107S-AW**-DB25… | E | F | 17 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 107S-AW**-DB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-D8E-B25 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-D-PNC23 | 655 | 1, 5, 6 | E205542, 1:4, 2:2
AB107S-DW**-DB25… | E | E | 18 | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 107S-DW**-DB25… | 1.6 … 2.5 | 65kA | 65kA | 30kA | 104-C23*22 | 140M-D8E-B25 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-D-PNC23
AB107S-AW**-DB40… | F | F | 19 | 1 | 1 | 3 | 3 | 4 | 3.6 | 4 | 3.9 | 107S-AW**-DB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-D8E-B40 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-D-PNC23
AB107S-DW**-DB40… | E | E | 21 | 1 | 1 | 3 | 3 | 4 | 3.6 | 4 | 3.9 | 107S-DW**-DB40… | 2.5 … 4.0 | 65kA | 65kA | 30kA | 104-C23*22 | 140M-D8E-B40 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-D-PNC23
AB107S-AW**-DB3*… | F | F | 22 | 1-1/2 | 2 | 5 | 5 | 6 | 6.3 | 6.3 | 6.1 | 107S-AW**-DB63… | 4.0 … 6.3 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-D8E-B63 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-D-PNC23
AB107S-EW**-DB63… | E | E | 23 | 1-1/2 | 2 | 5 | 5 | 6 | 6.3 | 6.3 | 6.1 | 107S-EW**-DB63… | 4.0 … 6.3 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-D8E-B63 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-D-PNC37
AB107S-AW**-DC10… | F | F | 24 | 2 | 2 | 5 | 7-1/2 | 7.8 | 6.8 | 7.6 | 9 | 107S-AW**-DC10… | 6.3 … 9.0 | 65kA | 65kA | 30kA | 104-C09*22 | 140M-D8E-C10 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-D-PNC23
AB107S-BW**-DC10… | F | F | 25 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 107S-BW**-DC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 104-C12*22 | 140M-D8E-C10 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-D-PNC23
AB107S-CW**-DC10… | F | F | 26 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 107S-EW**-DC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 104-C16*22 | 140M-D8E-C10 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-D-PNC23
AB107S-EW**-DC10… | E | E | 27 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 107S-EW**-DC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-D8E-C10 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-D-PNC37
AB107S-BW**-DC16… | F | F | -- | 3 | 3 | 7-1/2 | 10 | 11 | 9.6 | 11 | 11 | 107S-BW**-DC16… | 10.0 … 12.0 | 65kA | 65kA | 30kA | 104-C12*22 | 140M-D8E-C16 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-D-PNC23
AB107S-CW**-DC16… | F | F | 28 | 5 | 5 | 10 | 10 | 16 | 15.2 | 14 | 11 | 107S-EW**-DC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 104-C16*22 | 140M-D8E-C16 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-D-PNC23
AB107S-DW**-DC16… | F | F | 29 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 107S-DW**-DC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 104-C23*22 | 140M-D8E-C16 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-D-PNC23
AB107S-EW**-DC16… | E | E | 30 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 107S-EW**-DC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-D8E-C16 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-D-PNC37
AB107S-DW**-DC20… | F | --- | 31 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 107S-DW**-DC20… | 14.5 … 20.0 | 65kA | 65kA | --- | 104-C23*22 | 140M-D8E-C20 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-D-PNC23
AB107S-EW**-DC20… | E | --- | 32 | 5 | 7-1/2 | 15 | --- | 17.5 | 20 | 20 | --- | 107S-EW**-DC20… | 14.5 … 20.0 | 65kA | 65kA | --- | 104-C30*22 | 140M-D8E-C20 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-D-PNC37
AB107S-DW**-DC25… | F | --- | 33 | 5 | 7-1/2 | 15 | --- | 25 | 22 | 21 | --- | 107S-DW**-DC25… | 18.0 … 22.0 | 65kA | 65kA | --- | 104-C23*22 | 140M-D8E-C25 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-D-PNC23
AB107S-EW**-DC25… | E | --- | 34 | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 107S-EW**-DC25… | 18.0 … 25.0 | 65kA | 65kA | --- | 104-C30*22 | 140M-D8E-C25 | 141A-WS54RR | 141A-WS45RR | 140M-C-TE1 | 140M-D-PNC37
2 Component DOL Starter w/ Panel Mount - F Frame MPCB
AB103S-EW**-FC10… | E | E | 36 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103S-EW**-FC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-F8E-C10 | 141A-WS54RR45 | --- | 140M-F-TE | 140M-F-PNC37 | 1008 | 1, 5, 6 | E205542, 1:4, 2:2
AB103S-EW**-FC16… | E | E | 37 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 103S-EW**-FC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-F8E-C16 | 141A-WS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-EW**-FC20… | E | E | 38 | 5 | 7-1/2 | 15 | 20 | 17.5 | 20 | 20 | 20 | 103S-EW**-FC20… | 14.5 … 20.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-F8E-C20 | 141A-WS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-FW**-FC20… | E | E | --- | 5 | 7-1/2 | 15 | 20 | 17.5 | 20 | 20 | 20 | 103S-FW**-FC20… | 14.5 … 20.0 | 65kA | 65kA | 30kA | 100-C37*10 | 140M-F8E-C20 | 141A-WS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-EW**-FC25… | E | E | 39 | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 103S-EW**-FC25… | 18.0 … 25.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-F8E-C25 | 141A-WS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-FW**-FC25… | E | E | --- | 7-1/2 | 10 | 20 | 25 | 25 | 25 | 25 | 25 | 103S-FW**-FC25… | 18.0 … 25.0 | 65kA | 65kA | 30kA | 100-C37*10 | 140M-F8E-C25 | 141A-WS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-GW**-FC25… | E | E | 40 | 7-1/2 | 10 | 20 | 25 | 25 | 25 | 25 | 25 | 103S-GW**-FC25… | 18.0 … 25.0 | 65kA | 65kA | 30kA | 100-C43*10 | 140M-F8E-C25 | 141A-WS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-EW**-FC32… | E | E | 41 | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 103S-EW**-FC32… | 23.0 … 28.0 | 65kA | 65kA | 30kA | 100-C30*10 | 140M-F8E-C32 | 141A-WS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-FW**-FC32… | E | E | 42 | 10 | 10 | 25 | 30 | 32 | 28 | 32 | 32 | 103S-FW**-FC32… | 23.0 … 32.0 | 65kA | 65kA | 30kA | 100-C37*10 | 140M-F8E-C32 | 141A-WS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-GW**-FC32… | E | E | 43 | 10 | 10 | 25 | 30 | 32 | 28 | 32 | 32 | 103S-GW**-FC32… | 23.0 … 32.0 | 65kA | 65kA | 30kA | 100-C43*10 | 140M-F8E-C32 | 141A-WS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-FW**-FC45… | E | --- | 45 | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 103S-FW**-FC45… | 32.0 … 34.0 | 65kA | 65kA | --- | 100-C37*10 | 140M-F8E-C45 | 141A-WS54RR45 | --- | 140M-F-TE | 140M-F-PNC37
AB103S-GW**-FC45… | E | --- | 46 | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 103S-GW**-FC45… | 32.0 … 42.0 | 65kA | 65kA | --- | 100-C43*10 | 140M-F8E-C45 | 141A-WS54RR45 | --- | 140M-F-TE | 140M-F-PNC43
2 Component Reversing Starter w/ Panel Mount - F Frame MPCB
AB107S-EW**-FC10… | E | E | 36 | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 107S-EW**-FC10… | 6.3 … 10.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-F8E-C10 | 141A-WS54RR | 141A-WS45RR | 140M-F-TE | 140M-F-PNC37 | 1008 | 1, 5, 6 | E205542, 1:4, 2:2
AB107S-EW**-FC16… | E | E | 37 | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 107S-EW**-FC16… | 10.0 … 16.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-F8E-C16 | 141A-WS54RR | 141A-WS45RR | 140M-F-TE | 140M-F-PNC37
AB107S-EW**-FC20… | E | E | 38 | 5 | 7-1/2 | 15 | 20 | 17.5 | 20 | 20 | 20 | 107S-EW**-FC20… | 14.5 … 20.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-F8E-C20 | 141A-WS54RR | 141A-WS45RR | 140M-F-TE | 140M-F-PNC37
AB107S-FW**-FC20… | E | E | --- | 5 | 7-1/2 | 15 | 20 | 17.5 | 20 | 20 | 20 | 107S-FW**-FC20… | 14.5 … 20.0 | 65kA | 65kA | 30kA | 104-C37*22 | 140M-F8E-C20 | 141A-WS54RR | 141A-WS45RR | 140M-F-TE | 140M-F-PNC37
AB107S-EW**-FC25… | E | E | 39 | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 107S-EW**-FC25… | 18.0 … 25.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-F8E-C25 | 141A-WS54RR | 141A-WS45RR | 140M-F-TE | 140M-F-PNC37
AB107S-FW**-FC25… | E | E | --- | 7-1/2 | 10 | 20 | 25 | 25 | 25 | 25 | 25 | 107S-FW**-FC25… | 18.0 … 25.0 | 65kA | 65kA | 30kA | 104-C37*22 | 140M-F8E-C25 | 141A-WS54RR | 141A-WS45RR | 140M-F-TE | 140M-F-PNC37
AB107S-GW**-FC25… | E | E | 40 | 7-1/2 | 10 | 20 | 25 | 25 | 25 | 25 | 25 | 107S-GW**-FC25… | 18.0 … 25.0 | 65kA | 65kA | 30kA | 104-C43*22 | 140M-F8E-C25 | 141A-WS54RR | 141A-WS45RR | 140M-F-TE | 140M-F-PNC37
AB107S-EW**-FC32… | E | E | 41 | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 107S-EW**-FC32… | 23.0 … 28.0 | 65kA | 65kA | 30kA | 104-C30*22 | 140M-F8E-C32 | 141A-WS54RR | 141A-WS45RR | 140M-F-TE | 140M-F-PNC37
AB107S-FW**-FC32… | E | E | 42 | 10 | 10 | 25 | 30 | 32 | 28 | 32 | 32 | 107S-FW**-FC32… | 23.0 … 32.0 | 65kA | 65kA | 30kA | 104-C37*22 | 140M-F8E-C32 | 141A-WS54RR | 141A-WS45RR | 140M-F-TE | 140M-F-PNC37
AB107S-GW**-FC32… | E | E | 43 | 10 | 10 | 25 | 30 | 32 | 28 | 32 | 32 | 107S-GW**-FC32… | 23.0 … 32.0 | 65kA | 65kA | 30kA | 104-C43*22 | 140M-F8E-C32 | 141A-WS54RR | 141A-WS45RR | 140M-F-TE | 140M-F-PNC37
AB107S-FW**-FC45… | E | --- | 45 | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 107S-FW**-FC45… | 32.0 … 34.0 | 65kA | 65kA | --- | 104-C37*22 | 140M-F8E-C45 | 141A-WS54RR | 141A-WS45RR | 140M-F-TE | 140M-F-PNC37
AB107S-GW**-FC45… | E | --- | 46 | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 107S-GW**-FC45… | 32.0 … 42.0 | 65kA | 65kA | --- | 104-C43*22 | 140M-F8E-C45 | 141A-WS54RR | 141A-WS54RR | 140M-F-TE | 140M-F-PNC43
Notes:
[1] Horsepower ratings shown are for reference only, final selection of starter depends on the actual motor full load current and service factor
[2] Full load current values from NEC Table 430.25 or represent the maximum current rating of the combination motor controller
[3] Spacing adapter required for Type E or Type F construction (-TE suffix)
[4] Minimum Contactor Size - Contactors may be upsized within the frame to provide increased electrical life
* Insert approprite coil code
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches.
Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = In lieu of the following R/C (NKCR2) Connection Modules the following Jumper wires may be used for the following Combination Motor Controllers.
| Connection Modules |  |  | Combination Motor Controller |  |  |  | Jumper Wire
| 140M-C-PNC23, 140-D-PNC23 |  |  | 103S-107S |  |  |  | 105°C, 600V, 12, 10, 6, 4 and 2 AWG
| 140M-D-PNC37, 140M-F-PNC37 |  |  | 103S-107S |  |  |  | 105°C, 600V, 12, 10, 6, 4 and 2 AWG
| 140M-F-PNC43 |  |  | 103S-107S |  |  |  | 105°C, 600V, 12, 10, 6, 4 and 2 AWG

## Const. E w MCP (103T-107T)
Issued: 2007-12-21
[24 empty] | Last Revised: | 2018-02-16
[11 empty] | Combination Motor Controller |  |  |  |  | Component List
ID Number | Construction Type | Index No. | Max. Motor HP Rating [1] |  |  |  | Motor FLA [2] |  |  |  | 3 Component Combination |  | SCCR |  |  | Cat. Numbers for Field Assembly | [6 empty] | Minimum Enclosure Volume (cu. in.) | Conditions of Acceptability | UL File Reference
|  |  | 200V | 230V | 460V | 575V | 200V | 230V | 460V | 575V | A-B Cat. No. | Motor Current Adjust Range (A) | 208..240V | 480Y/277V | 600Y/347V | Contactor [3] | MCP | OLR | Mounting Module (s) |  | Terminal Adapter | Connection Module (s) [4]
3 Component DOL Starter w/ Standard Bus Bar Mount - C Frame MPCB
AB103T-AT**-QA40...-D1A | E |  | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 103T-AT**-QA40...-D1A | 0.1 … .4 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-A40 | 193-ED1AB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-C-PNC23 | 655 | 1, 5, 6 | E125316, 3:3
AB103T-AT**-QA40...-E1A |  |  | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 103T-AT**-QA40...-E1A | 0.1 … .4 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-A40 | 193-EEAB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AT**-QB10...-D1B |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 103T-AT**-QB10...-D1B | 0.2 … 1.0 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-B10 | 193-ED1BB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AT**-QB10...-E1B |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 103T-AT**-QB10...-E1B | 0.2 … 1.0 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-B10 | 193-EEBB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AT**-QB10...-C1P |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 103T-AT**-QB10...-C1P | 0.4 … 1.0 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-B10 | 193-EC1PB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AT**-QB10...-C2P |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 103T-AT**-QB10...-C2P | 0.4 … 1.0 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-B10 | 193-EC2PB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AT**-QB25...-C1P |  |  | 1/2 | 1/2 | 1 | --- | 2 | 2 | 2 | --- | 103T-AT**-QB25...-C1P | 0.4 … 2.0 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-EC1PB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AT**-QB25...-C2P |  |  | 1/2 | 1/2 | 1 | --- | 2 | 2 | 2 | --- | 103T-AT**-QB25...-C2P | 0.4 … 2.0 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-EC2PB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AT**-QB25...-D1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AT**-QB25...-D1C | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-ED1CB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AT**-QB25...-E1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AT**-QB25...-E1C | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-EECB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AT**-QB25...-C1A |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AT**-QB25...-C1A | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-EC1AB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AT**-QB25...-C2A |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AT**-QB25...-C2A | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-EC2AB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
3 Component Reversing Starter w/ Standard Bus Bar Mount - C Frame MPCB
AB107T-AT**-QA40...-D1A | E |  | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 107T-AT**-QA40...-D1A | 0.1 … .4 | 65kA | 65kA | 47kA | 104-C09* | 140M-C2N-A40 | 193-ED1AB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23 | 655 | 1, 5, 6 | E125316, 3:3
AB107T-AT**-QA40...-E1A |  |  | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 107T-AT**-QA40...-E1A | 0.1 … .4 | 65kA | 65kA | 47kA | 104-C09* | 140M-C2N-A40 | 193-EEAB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AT**-QB10...-D1B |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 107T-AT**-QB10...-D1B | 0.2 … 1.0 | 65kA | 65kA | 47kA | 104-C09* | 140M-C2N-B10 | 193-ED1BB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AT**-QB10...-E1B |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 107T-AT**-QB10...-E1B | 0.2 … 1.0 | 65kA | 65kA | 47kA | 104-C09* | 140M-C2N-B10 | 193-EEBB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AT**-QB10...-C2P |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 107T-AT**-QB10...-C2P | 0.4 … 1.0 | 65kA | 65kA | 47kA | 104-C09* | 140M-C2N-B10 | 193-EC2PB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AT**-QB25...-C2P |  |  | 1/2 | 1/2 | 1 | --- | 2 | 2 | 2 | --- | 107T-AT**-QB25...-C2P | 0.4 … 2.0 | 65kA | 65kA | --- | 104-C09* | 140M-C2N-B25 | 193-EC2PB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AT**-QB25...-D1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 107T-AT**-QB25...-D1C | 1.0 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-C2N-B25 | 193-ED1CB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AT**-QB25...-E1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 107T-AT**-QB25...-E1C | 1.0 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-C2N-B25 | 193-EECB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AT**-QB25...-C2A |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 107T-AT**-QB25...-C2A | 1.0 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-C2N-B25 | 193-EC2AB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
3 Component DOL Starter w/ ISO Bus Bar Mount - C Frame MPCB
AB103T-AS**-QA40...-D1A | E |  | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 103T-AS**-QA40...-D1A | 0.1 … .4 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-A40 | 193-ED1AB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-C-PNC23 | 655 | 1, 5, 6 | E125316, 3:3
AB103T-AS**-QA40...-E1A |  |  | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 103T-AS**-QA40...-E1A | 0.1 … .4 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-A40 | 193-EEAB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AS**-QB10...-D1B |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 103T-AS**-QB10...-D1B | 0.2 … 1.0 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-B10 | 193-ED1BB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AS**-QB10...-E1B |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 103T-AS**-QB10...-E1B | 0.2 … 1.0 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-B10 | 193-EEBB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AS**-QB10...-C1P |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 103T-AS**-QB10...-C1P | 0.4 … 1.0 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-B10 | 193-EC1PB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AS**-QB10...-C2P |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 103T-AS**-QB10...-C2P | 0.4 … 1.0 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-B10 | 193-EC2PB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AS**-QB25...-C1P |  |  | 1/2 | 1/2 | 1 | --- | 2 | 2 | 2 | --- | 103T-AS**-QB25...-C1P | 0.4 … 2.0 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-EC1PB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AS**-QB25...-C2P |  |  | 1/2 | 1/2 | 1 | --- | 2 | 2 | 2 | --- | 103T-AS**-QB25...-C2P | 0.4 … 2.0 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-EC2PB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AS**-QB25...-D1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AS**-QB25...-D1C | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-ED1CB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AS**-QB25...-E1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AS**-QB25...-E1C | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-EECB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AS**-QB25...-C1A |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AS**-QB25...-C1A | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-EC1AB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AS**-QB25...-C2A |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AS**-QB25...-C2A | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-EC2AB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-C-PNC23
3 Component Reversing Starter w/ ISO Bus Bar Mount - C Frame MPCB
AB107T-AS**-QA40...-D1A | E |  | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 107T-AS**-QA40...-D1A | 0.1 … .4 | 65kA | 65kA | 47kA | 104-C09* | 140M-C2N-A40 | 193-ED1AB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23 | 655 | 1, 5, 6 | E125316, 3:3
AB107T-AS**-QA40...-E1A |  |  | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 107T-AS**-QA40...-E1A | 0.1 … .4 | 65kA | 65kA | 47kA | 104-C09* | 140M-C2N-A40 | 193-EEAB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AS**-QB10...-D1B |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 107T-AS**-QB10...-D1B | 0.2 … 1.0 | 65kA | 65kA | 47kA | 104-C09* | 140M-C2N-B10 | 193-ED1BB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AS**-QB10...-E1B |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 107T-AS**-QB10...-E1B | 0.2 … 1.0 | 65kA | 65kA | 47kA | 104-C09* | 140M-C2N-B10 | 193-EEBB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AS**-QB10...-C2P |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 107T-AS**-QB10...-C2P | 0.4 … 1.0 | 65kA | 65kA | 47kA | 104-C09* | 140M-C2N-B10 | 193-EC2PB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AS**-QB25...-C2P |  |  | 1/2 | 1/2 | 1 | --- | 2 | 2 | 2 | --- | 107T-AS**-QB25...-C2P | 0.4 … 2.0 | 65kA | 65kA | --- | 104-C09* | 140M-C2N-B25 | 193-EC2PB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AS**-QB25...-D1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 107T-AS**-QB25...-D1C | 1.0 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-C2N-B25 | 193-ED1CB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AS**-QB25...-E1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 107T-AS**-QB25...-E1C | 1.0 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-C2N-B25 | 193-EECB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AS**-QB25...-C2A |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 107T-AS**-QB25...-C2A | 1.0 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-C2N-B25 | 193-EC2AB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
3 Component DOL Starter w/ Standard Bus Bar Mount - D Frame MPCB
AB103T-AT**-RB25...-C1P | E |  | 1/2 | 1/2 | 1 | --- | 2 | 2 | 2 | --- | 103T-AT**-RB25...-C1P | 0.4 … 2.0 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-EC1PB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC23 | 655 | 1, 5, 6 | E125316, 3:3
AB103T-AT**-RB25...-C2P |  |  | 1/2 | 1/2 | 1 | --- | 2 | 2 | 2 | --- | 103T-AT**-RB25...-C2P | 0.4 … 2.0 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-EC2PB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-AT**-RB25...-D1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AT**-RB25...-D1C | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-ED1CB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-AT**-RB25...-E1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AT**-RB25...-E1C | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-EECB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-AT**-RB25...-C1A |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AT**-RB25...-C1A | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-EC1AB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-AT**-RB25...-C2A |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AT**-RB25...-C2A | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-EC2AB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DT**-RB25...-C1P |  |  | 1/2 | 1/2 | 1 | 1 | 2 | 2 | 2 | 1.7 | 103T-DT**-RB25...-C1P | 0.4 … 2.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B25 | 193-EC1PB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DT**-RB25...-C2P |  |  | 1/2 | 1/2 | 1 | 1 | 2 | 2 | 2 | 1.7 | 103T-DT**-RB25...-C2P | 0.4 … 2.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B25 | 193-EC2PB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DT**-RB25...-D1C |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 103T-DT**-RB25...-D1C | 1.0 … 2.5 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B25 | 193-ED1CB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DT**-RB25...-E1C |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 103T-DT**-RB25...-E1C | 1.0 … 2.5 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B25 | 193-EECB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DT**-RB25...-C1A |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 103T-DT**-RB25...-C1A | 1.0 … 2.5 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B25 | 193-EC1AB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DT**-RB25...-C2A |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 103T-DT**-RB25...-C2A | 1.0 … 2.5 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B25 | 193-EC2AB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DT**-RB40...-D1C |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 103T-DT**-RB40...-D1C | 1.0 … 4.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B40 | 193-ED1CB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DT**-RB40...-E1C |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 103T-DT**-RB40...-E1C | 1.0 … 4.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B40 | 193-EECB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DT**-RB40...-C1A |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 103T-DT**-RB40...-C1A | 1.0 … 4.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B40 | 193-EC1AB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DT**-RB40...-C2A |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 103T-DT**-RB40...-C2A | 1.0 … 4.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B40 | 193-EC2AB | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-ET**-RC10...-E1D |  |  | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103T-ET**-RC10...-E1D | 3.2 … 10 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C10 | 193-EEDD | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-ET**-RC10...-C1B |  |  | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103T-ET**-RC10...-C1B | 3.0 … 10 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C10 | 193-EC1BD | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-ET**-RC10...-C2B |  |  | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103T-ET**-RC10...-C2B | 3.0 … 10 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C10 | 193-EC2BD | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-ET**-RC16...-E1D |  |  | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 103T-ET**-RC16...-E1D | 3.2 … 16 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C16 | 193-EEDD | 141A-G*****25 |  | 140M-C-TE1 | 140M-D-PNC37
AB103T-ET**-RC16...-C1B |  |  | 5 | 5 | 10 | 15 | 11 | 15 | 14 | 15 | 103T-ET**-RC16...-C1B | 3.0 … 15 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C16 | 193-EC1BD | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-ET**-RC16...-C2B |  |  | 5 | 5 | 10 | 15 | 11 | 15 | 14 | 15 | 103T-ET**-RC16...-C2B | 3.0 … 15 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C16 | 193-EC2BD | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-ET**-RC25...-E1E |  |  | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 103T-ET**-RC25...-E1E | 5.4 … 25 | 65kA | 65kA | --- | 100-C30* | 140M-D8N-C25 | 193-EEED | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-ET**-RC25...-C1C |  |  | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 103T-ET**-RC25...-C1C | 5.0 … 25 | 65kA | 65kA | --- | 100-C30* | 140M-D8N-C25 | 193-EC1CD | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-ET**-RC25...-C2C |  |  | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 103T-ET**-RC25...-C2C | 5.0 … 25 | 65kA | 65kA | --- | 100-C30* | 140M-D8N-C25 | 193-EC2CD | 141A-G*****25 | --- | 140M-C-TE1 | 140M-D-PNC37
3 Component Reversing Starter w/ Standard Bus Bar Mount - D Frame MPCB
AB107T-AT**-RB25...-C2P | E |  | 1/2 | 1/2 | 1 | --- | 2 | 2 | 2 | --- | 107T-AT**-RB25...-C2P | 0.4 … 2.0 | 65kA | 65kA | --- | 104-C09* | 140M-D8N-B25 | 193-EC2PB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23 | 655 | 1, 5, 6 | E125316, 3:3
AB107T-AT**-RB25...-D1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 107T-AT**-RB25...-D1C | 1.0 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-D8N-B25 | 193-ED1CB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AT**-RB25...-E1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 107T-AT**-RB25...-E1C | 1.0 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-D8N-B25 | 193-EECB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AT**-RB25...-C2A |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 107T-AT**-RB25...-C2A | 1.0 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-D8N-B25 | 193-EC2AB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DT**-RB25...-C2P |  |  | 1/2 | 1/2 | 1 | 1 | 2 | 2 | 2 | 1.7 | 107T-DT**-RB25...-C2P | 0.4 … 2.0 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B25 | 193-EC2PB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DT**-RB25...-D1C |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 107T-DT**-RB25...-D1C | 1.0 … 2.5 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B25 | 193-ED1CB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DT**-RB25...-E1C |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 107T-DT**-RB25...-E1C | 1.0 … 2.5 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B25 | 193-EECB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DT**-RB25...-C2A |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 107T-DT**-RB25...-C2A | 1.0 … 2.5 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B25 | 193-EC2AB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DT**-RB40...-D1C |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 107T-DT**-RB40...-D1C | 1.0 … 4.0 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B40 | 193-ED1CB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DT**-RB40...-E1C |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 107T-DT**-RB40...-E1C | 1.0 … 4.0 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B40 | 193-EECB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DT**-RB40...-C2A |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 107T-DT**-RB40...-C2A | 1.0 … 4.0 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B40 | 193-EC2AB | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-ET**-RC10...-E1D |  |  | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 107T-ET**-RC10...-E1D | 3.2 … 10 | 65kA | 65kA | 30kA | 104-C30* | 140M-D8N-C10 | 193-EEDD | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-D-PNC37
AB107T-ET**-RC10...-C2B |  |  | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 107T-ET**-RC10...-C2B | 3.0 … 10 | 65kA | 65kA | 30kA | 104-C30* | 140M-D8N-C10 | 193-EC2BD | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-D-PNC37
AB107T-ET**-RC16...-E1D |  |  | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 107T-ET**-RC16...-E1D | 3.2 … 16 | 65kA | 65kA | 30kA | 104-C30* | 140M-D8N-C16 | 193-EEDD | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-D-PNC37
AB107T-ET**-RC16...-C2B |  |  | 5 | 5 | 10 | 15 | 11 | 15 | 14 | 15 | 107T-ET**-RC16...-C2B | 3.0 … 15 | 65kA | 65kA | 30kA | 104-C30* | 140M-D8N-C16 | 193-EC2BD | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-D-PNC37
AB107T-ET**-RC25...-E1E |  |  | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 107T-ET**-RC25...-E1E | 5.4 … 25 | 65kA | 65kA | --- | 104-C30* | 140M-D8N-C25 | 193-EEED | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-D-PNC37
AB107T-ET**-RC25...-C2C |  |  | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 107T-ET**-RC25...-C2C | 5.0 … 25 | 65kA | 65kA | --- | 104-C30* | 140M-D8N-C25 | 193-EC2CD | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-D-PNC37
3 Component DOL Starter w/ ISO Bus Bar Mount - D Frame MPCB
AB103T-AS**-RB25...-C1P | E |  | 1/2 | 1/2 | 1 | --- | 2 | 2 | 2 | --- | 103T-AS**-RB25...-C1P | 0.4 … 2.0 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-EC1PB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC23 | 655 | 1, 5, 6 | E125316, 3:3
AB103T-AS**-RB25...-C2P |  |  | 1/2 | 1/2 | 1 | --- | 2 | 2 | 2 | --- | 103T-AS**-RB25...-C2P | 0.4 … 2.0 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-EC2PB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-AS**-RB25...-D1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AS**-RB25...-D1C | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-ED1CB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-AS**-RB25...-E1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AS**-RB25...-E1C | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-EECB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-AS**-RB25...-C1A |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AS**-RB25...-C1A | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-EC1AB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-AS**-RB25...-C2A |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AS**-RB25...-C2A | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-EC2AB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DS**-RB25...-C1P |  |  | 1/2 | 1/2 | 1 | 1 | 2 | 2 | 2 | 1.7 | 103T-DS**-RB25...-C1P | 0.4 … 2.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B25 | 193-EC1PB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DS**-RB25...-C2P |  |  | 1/2 | 1/2 | 1 | 1 | 2 | 2 | 2 | 1.7 | 103T-DS**-RB25...-C2P | 0.4 … 2.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B25 | 193-EC2PB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DS**-RB25...-D1C |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 103T-DS**-RB25...-D1C | 1.0 … 2.5 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B25 | 193-ED1CB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DS**-RB25...-E1C |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 103T-DS**-RB25...-E1C | 1.0 … 2.5 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B25 | 193-EECB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DS**-RB25...-C1A |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 103T-DS**-RB25...-C1A | 1.0 … 2.5 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B25 | 193-EC1AB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DS**-RB25...-C2A |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 103T-DS**-RB25...-C2A | 1.0 … 2.5 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B25 | 193-EC2AB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DS**-RB40...-D1C |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 103T-DS**-RB40...-D1C | 1.0 … 4.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B40 | 193-ED1CB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DS**-RB40...-E1C |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 103T-DS**-RB40...-E1C | 1.0 … 4.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B40 | 193-EECB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DS**-RB40...-C1A |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 103T-DS**-RB40...-C1A | 1.0 … 4.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B40 | 193-EC1AB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DS**-RB40...-C2A |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 103T-DS**-RB40...-C2A | 1.0 … 4.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B40 | 193-EC2AB | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-ES**-RC10...-E1D |  |  | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103T-ES**-RC10...-E1D | 3.2 … 10 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C10 | 193-EEDD | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-ES**-RC10...-C1B |  |  | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103T-ES**-RC10...-C1B | 3.0 … 10 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C10 | 193-EC1BD | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-ES**-RC10...-C2B |  |  | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103T-ES**-RC10...-C2B | 3.0 … 10 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C10 | 193-EC2BD | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-ES**-RC16...-E1D |  |  | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 103T-ES**-RC16...-E1D | 3.2 … 16 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C16 | 193-EEDD | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-ES**-RC16...-C1B |  |  | 5 | 5 | 10 | 15 | 11 | 15 | 14 | 15 | 103T-ES**-RC16...-C1B | 3.0 … 15 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C16 | 193-EC1BD | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-ES**-RC16...-C2B |  |  | 5 | 5 | 10 | 15 | 11 | 15 | 14 | 15 | 103T-ES**-RC16...-C2B | 3.0 … 15 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C16 | 193-EC2BD | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-ES**-RC25...-E1E |  |  | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 103T-ES**-RC25...-E1E | 5.4 … 25 | 65kA | 65kA | --- | 100-C30* | 140M-D8N-C25 | 193-EEED | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-ES**-RC25...-C1C |  |  | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 103T-ES**-RC25...-C1C | 5.0 … 25 | 65kA | 65kA | --- | 100-C30* | 140M-D8N-C25 | 193-EC1CD | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-ES**-RC25...-C2C |  |  | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 103T-ES**-RC25...-C2C | 5.0 … 25 | 65kA | 65kA | --- | 100-C30* | 140M-D8N-C25 | 193-EC2CD | 141A-S*****25 | --- | 140M-C-TE1 | 140M-D-PNC37
3 Component Reversing Starter w/ ISO Bus Bar Mount - D Frame MPCB
AB107T-AS**-RB25...-C2P | E |  | 1/2 | 1/2 | 1 | --- | 2 | 2 | 2 | --- | 107T-AS**-RB25...-C2P | 0.4 … 2.0 | 65kA | 65kA | --- | 104-C09* | 140M-D8N-B25 | 193-EC2PB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23 | 655 | 1, 5, 6 | E125316, 3:3
AB107T-AS**-RB25...-D1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 107T-AS**-RB25...-D1C | 1.0 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-D8N-B25 | 193-ED1CB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AS**-RB25...-E1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 107T-AS**-RB25...-E1C | 1.0 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-D8N-B25 | 193-EECB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AS**-RB25...-C2A |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 107T-AS**-RB25...-C2A | 1.0 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-D8N-B25 | 193-EC2AB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DS**-RB25...-C2P |  |  | 1/2 | 1/2 | 1 | 1 | 2 | 2 | 2 | 1.7 | 107T-DS**-RB25...-C2P | 0.4 … 2.0 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B25 | 193-EC2PB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DS**-RB25...-D1C |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 107T-DS**-RB25...-D1C | 1.0 … 2.5 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B25 | 193-ED1CB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DS**-RB25...-E1C |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 107T-DS**-RB25...-E1C | 1.0 … 2.5 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B25 | 193-EECB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DS**-RB25...-C2A |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 107T-DS**-RB25...-C2A | 1.0 … 2.5 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B25 | 193-EC2AB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DS**-RB40...-D1C |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 107T-DS**-RB40...-D1C | 1.0 … 4.0 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B40 | 193-ED1CB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DS**-RB40...-E1C |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 107T-DS**-RB40...-E1C | 1.0 … 4.0 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B40 | 193-EECB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DS**-RB40...-C2A |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 107T-DS**-RB40...-C2A | 1.0 … 4.0 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B40 | 193-EC2AB | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-ES**-RC10...-E1D |  |  | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 107T-ES**-RC10...-E1D | 3.2 … 10 | 65kA | 65kA | 30kA | 104-C30* | 140M-D8N-C10 | 193-EEDD | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-D-PNC37
AB107T-ES**-RC10...-C2B |  |  | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 107T-ES**-RC10...-C2B | 3.0 … 10 | 65kA | 65kA | 30kA | 104-C30* | 140M-D8N-C10 | 193-EC2BD | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-D-PNC37
AB107T-ES**-RC16...-E1D |  |  | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 107T-ES**-RC16...-E1D | 3.2… 16 | 65kA | 65kA | 30kA | 104-C30* | 140M-D8N-C16 | 193-EEDD | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-D-PNC37
AB107T-ES**-RC16...-C2B |  |  | 5 | 5 | 10 | 15 | 11 | 15 | 14 | 15 | 107T-ES**-RC16...-C2B | 3.0 … 15 | 65kA | 65kA | 30kA | 104-C30* | 140M-D8N-C16 | 193-EC2BD | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-D-PNC37
AB107T-ES**-RC25...-E1E |  |  | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 107T-ES**-RC25...-E1E | 5.4 … 25 | 65kA | 65kA | --- | 104-C30* | 140M-D8N-C25 | 193-EEED | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-D-PNC37
AB107T-ES**-RC25...-C2C |  |  | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 107T-ES**-RC25...-C2C | 5.0 … 25 | 65kA | 65kA | --- | 104-C30* | 140M-D8N-C25 | 193-EC2CD | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-D-PNC37
3 Component DOL Starter w/ Standard Bus Bar Mount - F Frame MPCB
AB103T-ET**-TC25...-E1E | E |  | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 103T-ET**-TC25...-E1E | 5.4 … 25 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C25 | 193-EEED | 141A-G*****45 | --- | 140M-F-TE | 140M-F-PNC37 | 1008 | 1, 5, 6 | E125316, 3:3
AB103T-ET**-TC25...-C1C |  |  | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 103T-ET**-TC25...-C1C | 5.0 … 25 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C25 | 193-EC1CD | 141A-G*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-ET**-TC25...-C2C |  |  | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 103T-ET**-TC25...-C2C | 5.0 … 25 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C25 | 193-EC2CD | 141A-G*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-ET**-TC32...-E1F |  |  | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 103T-ET**-TC32...-E1F | 9.0 … 30 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C32 | 193-EEFD | 141A-G*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-ET**-TC32...-C1D |  |  | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 103T-ET**-TC32...-C1D | 9.0 … 30 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C32 | 193-EC1DD | 141A-G*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-ET**-TC32...-C2D |  |  | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 103T-ET**-TC32...-C2D | 9.0 … 30 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C32 | 193-EC2DD | 141A-G*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-FT**-TC32...-E1F |  |  | 10 | 10 | 25 | 30 | 25.3 | 28 | 32 | 32 | 103T-FT**-TC32...-E1F | 9.0 … 32 | 65kA | 65kA | 30kA | 100-C37* | 140M-F8N-C32 | 193-EEFD | 141A-G*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-FT**-TC32...-C1D |  |  | 10 | 10 | 25 | 30 | 25.3 | 28 | 32 | 32 | 103T-FT**-TC32...-C1D | 9.0 … 32 | 65kA | 65kA | 30kA | 100-C37* | 140M-F8N-C32 | 193-EC1DD | 141A-G*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-FT**-TC32...-C2D |  |  | 10 | 10 | 25 | 30 | 25.3 | 28 | 32 | 32 | 103T-FT**-TC32...-C2D | 9.0 … 32 | 65kA | 65kA | 30kA | 100-C37* | 140M-F8N-C32 | 193-EC2DD | 141A-G*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-FT**-TC45...-E1F |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 103T-FT**-TC45...-E1F | 9.0 … 37 | 65kA | 65kA | --- | 100-C37* | 140M-F8N-C45 | 193-EEFD | 141A-G*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-FT**-TC45...-C1D |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 103T-FT**-TC45...-C1D | 9.0 … 37 | 65kA | 65kA | --- | 100-C37* | 140M-F8N-C45 | 193-EC1DD | 141A-G*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-FT**-TC45...-C2D |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 103T-FT**-TC45...-C2D | 9.0 … 37 | 65kA | 65kA | --- | 100-C37* | 140M-F8N-C45 | 193-EC2DD | 141A-G*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-GT**-TC45...-E1F |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 103T-GT**-TC45...-E1F | 9.0 … 43 | 65kA | 65kA | --- | 100-C43* | 140M-F8N-C45 | 193-EEFD | 141A-G*****45 | --- | 140M-F-TE | 140M-F-PNC43
AB103T-GT**-TC45...-C1D |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 103T-GT**-TC45...-C1D | 9.0 … 43 | 65kA | 65kA | --- | 100-C43* | 140M-F8N-C45 | 193-EC1DD | 141A-G*****45 | --- | 140M-F-TE | 140M-F-PNC43
AB103T-GT**-TC45...-C2D |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 103T-GT**-TC45...-C2D | 9.0 … 43 | 65kA | 65kA | --- | 100-C43* | 140M-F8N-C45 | 193-EC2DD | 141A-G*****45 | --- | 140M-F-TE | 140M-F-PNC43
AB103T-HT**-TC45...-E1G |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 103T-HT**-TC45...-E1G | 18 … 45 | 65kA | 65kA | --- | 100-C60* | 140M-F8N-C45 | 193-EEGE | 141A-G*****45 | 141A-G**** | 140M-F-TE | #6 AWG Wire
AB103T-HT**-TC45...-C1D |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 103T-HT**-TC45...-C1D | 9.0 … 45 | 65kA | 65kA | --- | 100-C60* | 140M-F8N-C45 | 193-EC1DE | 141A-G*****45 | 141A-G**** | 140M-F-TE | #6 AWG Wire
AB103T-HT**-TC45...-C2D |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 103T-HT**-TC45...-C2D | 9.0 … 45 | 65kA | 65kA | --- | 100-C60* | 140M-F8N-C45 | 193-EC2DE | 141A-G*****45 | 141A-G**** | 140M-F-TE | #6 AWG Wire
3 Component Reversing Starter w/ Standard Bus Bar Mount - F Frame MPCB
AB107T-ET**-TC25...-E1E | E |  | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 107T-ET**-TC25...-E1E | 5.4 … 25 | 65kA | 65kA | 30kA | 104-C30* | 140M-F8N-C25 | 193-EEED | 141A-G*****45 | 141A-G**** | 140M-F-TE | 140M-F-PNC37 | 1008 | 1, 5, 6 | E125316, 3:3
AB107T-ET**-TC25...-C2C |  |  | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 107T-ET**-TC25...-C2C | 5.0 … 25 | 65kA | 65kA | 30kA | 104-C30* | 140M-F8N-C25 | 193-EC2CD | 141A-G*****45 | 141A-G**** | 140M-F-TE | 140M-F-PNC37
AB107T-ET**-TC32...-E1F |  |  | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 107T-ET**-TC32...-E1F | 9.0 … 30 | 65kA | 65kA | 30kA | 104-C30* | 140M-F8N-C32 | 193-EEFD | 141A-G*****45 | 141A-G**** | 140M-F-TE | 140M-F-PNC37
AB107T-ET**-TC32...-C2D |  |  | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 107T-ET**-TC32...-C2D | 9.0 … 30 | 65kA | 65kA | 30kA | 104-C30* | 140M-F8N-C32 | 193-EC2DD | 141A-G*****45 | 141A-G**** | 140M-F-TE | 140M-F-PNC37
AB107T-FT**-TC32...-E1F |  |  | 10 | 10 | 25 | 30 | 25.3 | 28 | 32 | 32 | 107T-FT**-TC32...-E1F | 9.0 … 32 | 65kA | 65kA | 30kA | 104-C37* | 140M-F8N-C32 | 193-EEFD | 141A-G*****45 | 141A-G**** | 140M-F-TE | 140M-F-PNC37
AB107T-FT**-TC32...-C2D |  |  | 10 | 10 | 25 | 30 | 25.3 | 28 | 32 | 32 | 107T-FT**-TC32...-C2D | 9.0 … 32 | 65kA | 65kA | 30kA | 104-C37* | 140M-F8N-C32 | 193-EC2DD | 141A-G*****45 | 141A-G**** | 140M-F-TE | 140M-F-PNC37
AB107T-FT**-TC45...-E1F |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 107T-FT**-TC45...-E1F | 9.0 … 37 | 65kA | 65kA | --- | 104-C37* | 140M-F8N-C45 | 193-EEFD | 141A-G*****45 | 141A-G**** | 140M-F-TE | 140M-F-PNC37
AB107T-FT**-TC45...-C2D |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 107T-FT**-TC45...-C2D | 9.0 … 37 | 65kA | 65kA | --- | 104-C37* | 140M-F8N-C45 | 193-EC2DD | 141A-G*****45 | 141A-G**** | 140M-F-TE | 140M-F-PNC37
AB107T-GT**-TC45...-E1F |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 107T-GT**-TC45...-E1F | 9.0 … 43 | 65kA | 65kA | --- | 104-C43* | 140M-F8N-C45 | 193-EEFD | 141A-G*****45 | 141A-G**** | 140M-F-TE | 140M-F-PNC43
AB107T-GT**-TC45...-C2D |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 107T-GT**-TC45...-C2D | 9.0 … 43 | 65kA | 65kA | --- | 104-C43* | 140M-F8N-C45 | 193-EC2DD | 141A-G*****45 | 141A-G**** | 140M-F-TE | 140M-F-PNC43
AB107T-HT**-TC45...-E1G |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 107T-HT**-TC45...-E1G | 18 … 45 | 65kA | 65kA | --- | 104-C60* | 140M-F8N-C45 | 193-EEGE | 141A-G*****45 | 141A-G**** | 140M-F-TE | #6 AWG Wire
AB107T-HT**-TC45...-C2D |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 107T-HT**-TC45...-C2D | 9.0 … 45 | 65kA | 65kA | --- | 104-C60* | 140M-F8N-C45 | 193-EC2DE | 141A-G*****45 | 141A-G**** | 140M-F-TE | #6 AWG Wire
3 Component DOL Starter w/ ISO Bus Bar Mount - F Frame MPCB
AB103T-ES**-TC25...-E1E | E |  | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 103T-ES**-TC25...-E1E | 5.4 … 25 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C25 | 193-EEED | 141A-S*****45 | --- | 140M-F-TE | 140M-F-PNC37 | 1008 | 1, 5, 6 | E125316, 3:3
AB103T-ES**-TC25...-C1C |  |  | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 103T-ES**-TC25...-C1C | 5.0 … 25 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C25 | 193-EC1CD | 141A-S*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-ES**-TC25...-C2C |  |  | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 103T-ES**-TC25...-C2C | 5.0 … 25 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C25 | 193-EC2CD | 141A-S*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-ES**-TC32...-E1F |  |  | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 103T-ES**-TC32...-E1F | 9.0 … 30 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C32 | 193-EEFD | 141A-S*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-ES**-TC32...-C1D |  |  | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 103T-ES**-TC32...-C1D | 9.0 … 30 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C32 | 193-EC1DD | 141A-S*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-ES**-TC32...-C2D |  |  | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 103T-ES**-TC32...-C2D | 9.0 … 30 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C32 | 193-EC2DD | 141A-S*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-FS**-TC32...-E1F |  |  | 10 | 10 | 25 | 30 | 25.3 | 28 | 32 | 32 | 103T-FS**-TC32...-E1F | 9.0 … 32 | 65kA | 65kA | 30kA | 100-C37* | 140M-F8N-C32 | 193-EEFD | 141A-S*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-FS**-TC32...-C1D |  |  | 10 | 10 | 25 | 30 | 25.3 | 28 | 32 | 32 | 103T-FS**-TC32...-C1D | 9.0 … 32 | 65kA | 65kA | 30kA | 100-C37* | 140M-F8N-C32 | 193-EC1DD | 141A-S*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-FS**-TC32...-C2D |  |  | 10 | 10 | 25 | 30 | 25.3 | 28 | 32 | 32 | 103T-FS**-TC32...-C2D | 9.0 … 32 | 65kA | 65kA | 30kA | 100-C37* | 140M-F8N-C32 | 193-EC2DD | 141A-S*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-FS**-TC45...-E1F |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 103T-FS**-TC45...-E1F | 9.0 … 37 | 65kA | 65kA | --- | 100-C37* | 140M-F8N-C45 | 193-EEFD | 141A-S*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-FS**-TC45...-C1D |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 103T-FS**-TC45...-C1D | 9.0 … 37 | 65kA | 65kA | --- | 100-C37* | 140M-F8N-C45 | 193-EC1DD | 141A-S*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-FS**-TC45...-C2D |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 103T-FS**-TC45...-C2D | 9.0 … 37 | 65kA | 65kA | --- | 100-C37* | 140M-F8N-C45 | 193-EC2DD | 141A-S*****45 | --- | 140M-F-TE | 140M-F-PNC37
AB103T-GS**-TC45...-E1F |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 103T-GS**-TC45...-E1F | 9.0 … 43 | 65kA | 65kA | --- | 100-C43* | 140M-F8N-C45 | 193-EEFD | 141A-S*****45 | --- | 140M-F-TE | 140M-F-PNC43
AB103T-GS**-TC45...-C1D |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 103T-GS**-TC45...-C1D | 9.0 … 43 | 65kA | 65kA | --- | 100-C43* | 140M-F8N-C45 | 193-EC1DD | 141A-S*****45 | --- | 140M-F-TE | 140M-F-PNC43
AB103T-GS**-TC45...-C2D |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 103T-GS**-TC45...-C2D | 9.0 … 43 | 65kA | 65kA | --- | 100-C43* | 140M-F8N-C45 | 193-EC2DD | 141A-S*****45 | --- | 140M-F-TE | 140M-F-PNC43
3 Component Reversing Starter w/ ISO Bus Bar Mount - F Frame MPCB
AB107T-ES**-TC25...-E1E | E |  | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 107T-ES**-TC25...-E1E | 5.4 … 25 | 65kA | 65kA | 30kA | 104-C30* | 140M-F8N-C25 | 193-EEED | 141A-S*****45 | 141A-S**** | 140M-F-TE | 140M-F-PNC37 | 1008 | 1, 5, 6 | E125316, 3:3
AB107T-ES**-TC25...-C2C |  |  | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 107T-ES**-TC25...-C2C | 5.0 … 25 | 65kA | 65kA | 30kA | 104-C30* | 140M-F8N-C25 | 193-EC2CD | 141A-S*****45 | 141A-S**** | 140M-F-TE | 140M-F-PNC37
AB107T-ES**-TC32...-E1F |  |  | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 107T-ES**-TC32...-E1F | 9.0 … 30 | 65kA | 65kA | 30kA | 104-C30* | 140M-F8N-C32 | 193-EEFD | 141A-S*****45 | 141A-S**** | 140M-F-TE | 140M-F-PNC37
AB107T-ES**-TC32...-C2D |  |  | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 107T-ES**-TC32...-C2D | 9.0 … 30 | 65kA | 65kA | 30kA | 104-C30* | 140M-F8N-C32 | 193-EC2DD | 141A-S*****45 | 141A-S**** | 140M-F-TE | 140M-F-PNC37
AB107T-FS**-TC32...-E1F |  |  | 10 | 10 | 25 | 30 | 25.3 | 28 | 32 | 32 | 107T-FS**-TC32...-E1F | 9.0 … 32 | 65kA | 65kA | 30kA | 104-C37* | 140M-F8N-C32 | 193-EEFD | 141A-S*****45 | 141A-S**** | 140M-F-TE | 140M-F-PNC37
AB107T-FS**-TC32...-C2D |  |  | 10 | 10 | 25 | 30 | 25.3 | 28 | 32 | 32 | 107T-FS**-TC32...-C2D | 9.0 … 32 | 65kA | 65kA | 30kA | 104-C37* | 140M-F8N-C32 | 193-EC2DD | 141A-S*****45 | 141A-S**** | 140M-F-TE | 140M-F-PNC37
AB107T-FS**-TC45...-E1F |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 107T-FS**-TC45...-E1F | 9.0 … 37 | 65kA | 65kA | --- | 104-C37* | 140M-F8N-C45 | 193-EEFD | 141A-S*****45 | 141A-S**** | 140M-F-TE | 140M-F-PNC37
AB107T-FS**-TC45...-C2D |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 107T-FS**-TC45...-C2D | 9.0 … 37 | 65kA | 65kA | --- | 104-C37* | 140M-F8N-C45 | 193-EC2DD | 141A-S*****45 | 141A-S**** | 140M-F-TE | 140M-F-PNC37
AB107T-GS**-TC45...-E1F |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 107T-GS**-TC45...-E1F | 9.0 … 43 | 65kA | 65kA | --- | 104-C43* | 140M-F8N-C45 | 193-EEFD | 141A-S*****45 | 141A-S**** | 140M-F-TE | 140M-F-PNC43
AB107T-GS**-TC45...-C2D |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 107T-GS**-TC45...-C2D | 9.0 … 43 | 65kA | 65kA | --- | 104-C43* | 140M-F8N-C45 | 193-EC2DD | 141A-S*****45 | 141A-S**** | 140M-F-TE | 140M-F-PNC43
3 Component DOL Starter w/ Panel Mount - C Frame MPCB
AB103T-AW**-QA40...-D1A | E |  | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 103T-AW**-QA40...-D1A | 0.1 … .4 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-A40 | 193-ED1AB | 141A-W***** | --- | 140M-C-TE1 | 140M-C-PNC23 | 655 | 1, 5, 6 | E125316, 3:3
AB103T-AW**-QA40...-E1A |  |  | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 103T-AW**-QA40...-E1A | 0.1 … .4 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-A40 | 193-EEAB | 141A-W***** | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AW**-QB10...-D1B |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 103T-AW**-QB10...-D1B | 0.2 … 1.0 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-B10 | 193-ED1BB | 141A-W***** | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AW**-QB10...-E1B |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 103T-AW**-QB10...-E1B | 0.2 … 1.0 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-B10 | 193-EEBB | 141A-W***** | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AW**-QB10...-C1P |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 103T-AW**-QB10...-C1P | 0.4 … 1.0 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-B10 | 193-EC1PB | 141A-W***** | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AW**-QB10...-C2P |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 103T-AW**-QB10...-C2P | 0.4 … 1.0 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-B10 | 193-EC2PB | 141A-W***** | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AW**-QB25...-C1P |  |  | 1/2 | 1/2 | 1 | --- | 2 | 2 | 2 | --- | 103T-AW**-QB25...-C1P | 0.4 … 2.0 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-EC1PB | 141A-W***** | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AW**-QB25...-C2P |  |  | 1/2 | 1/2 | 1 | --- | 2 | 2 | 2 | --- | 103T-AW**-QB25...-C2P | 0.4 … 2.0 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-EC2PB | 141A-W***** | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AW**-QB25...-D1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AW**-QB25...-D1C | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-ED1CB | 141A-W***** | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AW**-QB25...-E1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AW**-QB25...-E1C | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-EECB | 141A-W***** | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AW**-QB25...-C1A |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AW**-QB25...-C1A | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-EC1AB | 141A-W***** | --- | 140M-C-TE1 | 140M-C-PNC23
AB103T-AW**-QB25...-C2A |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AW**-QB25...-C2A | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-EC2AB | 141A-W***** | --- | 140M-C-TE1 | 140M-C-PNC23
3 Component Reversing Starter w/ Panel Mount - C Frame MPCB
AB107T-AW**-QA40...-D1A | E |  | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 107T-AW**-QA40...-D1A | 0.1 … .4 | 65kA | 65kA | 47kA | 104-C09* | 140M-C2N-A40 | 193-ED1AB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23 | 655 | 1, 5, 6 | E125316, 3:3
AB107T-AW**-QA40...-E1A |  |  | --- | --- | --- | --- | 0.4 | 0.4 | 0.4 | 0.4 | 107T-AW**-QA40...-E1A | 0.1 … .4 | 65kA | 65kA | 47kA | 104-C09* | 140M-C2N-A40 | 193-EEAB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AW**-QB10...-D1B |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 107T-AW**-QB10...-D1B | 0.2 … 1.0 | 65kA | 65kA | 47kA | 104-C09* | 140M-C2N-B10 | 193-ED1BB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AW**-QB10...-E1B |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 107T-AW**-QB10...-E1B | 0.2 … 1.0 | 65kA | 65kA | 47kA | 104-C09* | 140M-C2N-B10 | 193-EEBB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AW**-QB10...-C2P |  |  | --- | --- | 1/2 | 3/4 | 1 | 1 | 1 | 1 | 107T-AW**-QB10...-C2P | 0.4 … 1.0 | 65kA | 65kA | 47kA | 104-C09* | 140M-C2N-B10 | 193-EC2PB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AW**-QB25...-C2P |  |  | 1/2 | 1/2 | 1 | --- | 2 | 2 | 2 | --- | 107T-AW**-QB25...-C2P | 0.4 … 2.0 | 65kA | 65kA | --- | 104-C09* | 140M-C2N-B25 | 193-EC2PB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AW**-QB25...-D1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 107T-AW**-QB25...-D1C | 1.0 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-C2N-B25 | 193-ED1CB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AW**-QB25...-E1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 107T-AW**-QB25...-E1C | 1.0 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-C2N-B25 | 193-EECB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AW**-QB25...-C2A |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 107T-AW**-QB25...-C2A | 1.0 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-C2N-B25 | 193-EC2AB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23
3 Component DOL Starter w/ Panel Mount - D Frame MPCB
AB103T-AW**-RB25...-C1P | E |  | 1/2 | 1/2 | 1 | --- | 2 | 2 | 2 | --- | 103T-AW**-RB25...-C1P | 0.4 … 2.0 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-EC1PB | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC23 | 655 | 1, 5, 6 | E125316, 3:3
AB103T-AW**-RB25...-C2P |  |  | 1/2 | 1/2 | 1 | --- | 2 | 2 | 2 | --- | 103T-AW**-RB25...-C2P | 0.4 … 2.0 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-EC2PB | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-AW**-RB25...-D1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AW**-RB25...-D1C | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-ED1CB | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-AW**-RB25...-E1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AW**-RB25...-E1C | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-EECB | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-AW**-RB25...-C1A |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AW**-RB25...-C1A | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-EC1AB | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-AW**-RB25...-C2A |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 103T-AW**-RB25...-C2A | 1.0 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-EC2AB | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DW**-RB25...-C1P |  |  | 1/2 | 1/2 | 1 | 1 | 2 | 2 | 2 | 1.7 | 103T-DW**-RB25...-C1P | 0.4 … 2.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B25 | 193-EC1PB | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DW**-RB25...-C2P |  |  | 1/2 | 1/2 | 1 | 1 | 2 | 2 | 2 | 1.7 | 103T-DW**-RB25...-C2P | 0.4 … 2.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B25 | 193-EC2PB | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DW**-RB25...-D1C |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 103T-DW**-RB25...-D1C | 1.0 … 2.5 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B25 | 193-ED1CB | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DW**-RB25...-E1C |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 103T-DW**-RB25...-E1C | 1.0 … 2.5 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B25 | 193-EECB | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DW**-RB25...-C1A |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 103T-DW**-RB25...-C1A | 1.0 … 2.5 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B25 | 193-EC1AB | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DW**-RB25...-C2A |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 103T-DW**-RB25...-C2A | 1.0 … 2.5 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B25 | 193-EC2AB | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DW**-RB40...-D1C |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 103T-DW**-RB40...-D1C | 1.0 … 4.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B40 | 193-ED1CB | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DW**-RB40...-E1C |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 103T-DW**-RB40...-E1C | 1.0 … 4.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B40 | 193-EECB | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DW**-RB40...-C1A |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 103T-DW**-RB40...-C1A | 1.0 … 4.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B40 | 193-EC1AB | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-DW**-RB40...-C2A |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 103T-DW**-RB40...-C2A | 1.0 … 4.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B40 | 193-EC2AB | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC23
AB103T-EW**-RC10...-E1D |  |  | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103T-EW**-RC10...-E1D | 3.2 … 10 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C10 | 193-EEDD | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-EW**-RC10...-C2B |  |  | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 103T-EW**-RC10...-C2B | 3.0 … 10 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C10 | 193-EC2BD | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-EW**-RC16...-E1D |  |  | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 103T-EW**-RC16...-E1D | 3.2 … 16 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C16 | 193-EEDD | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-EW**-RC16...-C1B |  |  | 5 | 5 | 10 | 15 | 11 | 15 | 14 | 15 | 103T-EW**-RC16...-C1B | 3.0 … 15 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C16 | 193-EC1BD | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-EW**-RC25...-E1E |  |  | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 103T-EW**-RC25...-E1E | 5.4 … 25 | 65kA | 65kA | --- | 100-C30* | 140M-D8N-C25 | 193-EEED | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-EW**-RC25...-C1C |  |  | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 103T-EW**-RC25...-C1C | 5.0 … 25 | 65kA | 65kA | --- | 100-C30* | 140M-D8N-C25 | 193-EC1CD | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC37
AB103T-EW**-RC25...-C2C |  |  | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 103T-EW**-RC25...-C2C | 5.0 … 25 | 65kA | 65kA | --- | 100-C30* | 140M-D8N-C25 | 193-EC2CD | 141A-W***** | --- | 140M-C-TE1 | 140M-D-PNC37
3 Component Reversing Starter w/ Panel Mount - D Frame MPCB
AB107T-AW**-RB25...-C2P | E |  | 1/2 | 1/2 | 1 | --- | 2 | 2 | 2 | --- | 107T-AW**-RB25...-C2P | 0.4 … 2.0 | 65kA | 65kA | --- | 104-C09* | 140M-D8N-B25 | 193-EC2PB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23 | 655 | 1, 5, 6 | E125316, 3:3
AB107T-AW**-RB25...-D1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 107T-AW**-RB25...-D1C | 1.0 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-D8N-B25 | 193-ED1CB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AW**-RB25...-E1C |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 107T-AW**-RB25...-E1C | 1.0 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-D8N-B25 | 193-EECB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AW**-RB25...-C2A |  |  | 1/2 | 3/4 | 1-1/2 | --- | 2.5 | 2.2 | 2.5 | --- | 107T-AW**-RB25...-C2A | 1.0 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-D8N-B25 | 193-EC2AB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DW**-RB25...-C2P |  |  | 1/2 | 1/2 | 1 | 1 | 2 | 2 | 2 | 1.7 | 107T-DW**-RB25...-C2P | 0.4 … 2.0 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B25 | 193-EC2PB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DW**-RB25...-D1C |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 107T-DW**-RB25...-D1C | 1.0 … 2.5 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B25 | 193-ED1CB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DW**-RB25...-E1C |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 107T-DW**-RB25...-E1C | 1.0 … 2.5 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B25 | 193-EECB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DW**-RB25...-C2A |  |  | 1/2 | 3/4 | 1-1/2 | 2 | 2.5 | 2.2 | 2.5 | 2.5 | 107T-DW**-RB25...-C2A | 1.0 … 2.5 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B25 | 193-EC2AB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DW**-RB40...-D1C |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 107T-DW**-RB40...-D1C | 1.0 … 4.0 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B40 | 193-ED1CB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DW**-RB40...-E1C |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 107T-DW**-RB40...-E1C | 1.0 … 4.0 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B40 | 193-EECB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23
AB107T-DW**-RB40...-C2A |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 107T-DW**-RB40...-C2A | 1.0 … 4.0 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B40 | 193-EC2AB | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-C-PNC23
AB107T-EW**-RC10...-E1D |  |  | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 107T-EW**-RC10...-E1D | 3.2 … 10 | 65kA | 65kA | 30kA | 104-C30* | 140M-D8N-C10 | 193-EEDD | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-D-PNC37
AB107T-EW**-RC10...-C2B |  |  | 3 | 3 | 7-1/2 | 10 | 10 | 9.6 | 10 | 10 | 107T-EW**-RC10...-C2B | 3.0 … 10 | 65kA | 65kA | 30kA | 104-C30* | 140M-D8N-C10 | 193-EC2BD | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-D-PNC37
AB107T-EW**-RC16...-E1D |  |  | 5 | 5 | 10 | 15 | 16 | 15.2 | 14 | 16 | 107T-EW**-RC16...-E1D | 3.2 … 16 | 65kA | 65kA | 30kA | 104-C30* | 140M-D8N-C16 | 193-EEDD | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-D-PNC37
AB107T-EW**-RC25...-E1E |  |  | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 107T-EW**-RC25...-E1E | 5.4 … 25 | 65kA | 65kA | --- | 104-C30* | 140M-D8N-C25 | 193-EEED | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-D-PNC37
AB107T-EW**-RC25...-C2C |  |  | 7-1/2 | 10 | 20 | --- | 25 | 25 | 25 | --- | 107T-EW**-RC25...-C2C | 5.0 … 25 | 65kA | 65kA | --- | 104-C30* | 140M-D8N-C25 | 193-EC2CD | 141A-W***** | 141A-W***** | 140M-C-TE1 | 140M-D-PNC37
AB103T-EW**-TC25...-E1E | E |  | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 103T-EW**-TC25...-E1E | 5.4 … 25 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C25 | 193-EEED | 141A-W***** | --- | 140M-F-TE | 140M-F-PNC37 | 1008 | 1, 5, 6 | E125316, 3:3
AB103T-EW**-TC25...-C1C |  |  | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 103T-EW**-TC25...-C1C | 5.0 … 25 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C25 | 193-EC1CD | 141A-W***** | --- | 140M-F-TE | 140M-F-PNC37
AB103T-EW**-TC25...-C2C |  |  | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 103T-EW**-TC25...-C2C | 5.0 … 25 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C25 | 193-EC2CD | 141A-W***** | --- | 140M-F-TE | 140M-F-PNC37
AB103T-EW**-TC32...-E1F |  |  | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 103T-EW**-TC32...-E1F | 9.0 … 30 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C32 | 193-EEFD | 141A-W***** | --- | 140M-F-TE | 140M-F-PNC37
AB103T-EW**-TC32...-C1D |  |  | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 103T-EW**-TC32...-C1D | 9.0 … 30 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C32 | 193-EC1DD | 141A-W***** | --- | 140M-F-TE | 140M-F-PNC37
AB103T-EW**-TC32...-C2D |  |  | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 103T-EW**-TC32...-C2D | 9.0 … 30 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C32 | 193-EC2DD | 141A-W***** | --- | 140M-F-TE | 140M-F-PNC37
AB103T-FW**-TC32...-E1F |  |  | 10 | 10 | 25 | 30 | 25.3 | 28 | 32 | 32 | 103T-FW**-TC32...-E1F | 9.0 … 32 | 65kA | 65kA | 30kA | 100-C37* | 140M-F8N-C32 | 193-EEFD | 141A-W***** | --- | 140M-F-TE | 140M-F-PNC37
AB103T-FW**-TC32...-C1D |  |  | 10 | 10 | 25 | 30 | 25.3 | 28 | 32 | 32 | 103T-FW**-TC32...-C1D | 9.0 … 32 | 65kA | 65kA | 30kA | 100-C37* | 140M-F8N-C32 | 193-EC1DD | 141A-W***** | --- | 140M-F-TE | 140M-F-PNC37
AB103T-FW**-TC32...-C2D |  |  | 10 | 10 | 25 | 30 | 25.3 | 28 | 32 | 32 | 103T-FW**-TC32...-C2D | 9.0 … 32 | 65kA | 65kA | 30kA | 100-C37* | 140M-F8N-C32 | 193-EC2DD | 141A-W***** | --- | 140M-F-TE | 140M-F-PNC37
AB103T-FW**-TC45...-E1F |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 103T-FW**-TC45...-E1F | 9.0 … 37 | 65kA | 65kA | --- | 100-C37* | 140M-F8N-C45 | 193-EEFD | 141A-W***** | --- | 140M-F-TE | 140M-F-PNC37
AB103T-FW**-TC45...-C1D |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 103T-FW**-TC45...-C1D | 9.0 … 37 | 65kA | 65kA | --- | 100-C37* | 140M-F8N-C45 | 193-EC1DD | 141A-W***** | --- | 140M-F-TE | 140M-F-PNC37
AB103T-FW**-TC45...-C2D |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 103T-FW**-TC45...-C2D | 9.0 … 37 | 65kA | 65kA | --- | 100-C37* | 140M-F8N-C45 | 193-EC2DD | 141A-W***** | --- | 140M-F-TE | 140M-F-PNC37
AB103T-GW**-TC45...-E1F |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 103T-GW**-TC45...-E1F | 9.0 … 43 | 65kA | 65kA | --- | 100-C43* | 140M-F8N-C45 | 193-EEFD | 141A-W***** | --- | 140M-F-TE | 140M-F-PNC43
AB103T-GW**-TC45...-C1D |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 103T-GW**-TC45...-C1D | 9.0 … 43 | 65kA | 65kA | --- | 100-C43* | 140M-F8N-C45 | 193-EC1DD | 141A-W***** | --- | 140M-F-TE | 140M-F-PNC43
AB103T-GW**-TC45...-C2D |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 103T-GW**-TC45...-C2D | 9.0 … 43 | 65kA | 65kA | --- | 100-C43* | 140M-F8N-C45 | 193-EC2DD | 141A-W***** | --- | 140M-F-TE | 140M-F-PNC43
AB103T-HT**-TC45...-E1G |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 103T-HT**-TC45...-E1G | 18 … 45 | 65kA | 65kA | --- | 100-C60* | 140M-F8N-C45 | 193-EEGE | 141A-W***** | 141A-W***** | 140M-F-TE | #6 AWG Wire
AB103T-HT**-TC45...-C1D |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 103T-HT**-TC45...-C1D | 9.0 … 45 | 65kA | 65kA | --- | 100-C60* | 140M-F8N-C45 | 193-EC1DE | 141A-W***** | 141A-W***** | 140M-F-TE | #6 AWG Wire
AB103T-HT**-TC45...-C2D |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 103T-HT**-TC45...-C2D | 9.0 … 45 | 65kA | 65kA | --- | 100-C60* | 140M-F8N-C45 | 193-EC2DE | 141A-W***** | 141A-W***** | 140M-F-TE | #6 AWG Wire
3 Component Reversing Starter w/ Panel Mount - F Frame MPCB
AB107T-EW**-TC25...-E1E | E |  | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 107T-EW**-TC25...-E1E | 5.4 … 25 | 65kA | 65kA | 30kA | 104-C30* | 140M-F8N-C25 | 193-EEED | 141A-W***** | 141A-W***** | 140M-F-TE | 140M-F-PNC37 | 1008 | 1, 5, 6 | E125316, 3:3
AB107T-EW**-TC25...-C2C |  |  | 7-1/2 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 107T-EW**-TC25...-C2C | 5.0 … 25 | 65kA | 65kA | 30kA | 104-C30* | 140M-F8N-C25 | 193-EC2CD | 141A-W***** | 141A-W***** | 140M-F-TE | 140M-F-PNC37
AB107T-EW**-TC32...-E1F |  |  | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 107T-EW**-TC32...-E1F | 9.0 … 30 | 65kA | 65kA | 30kA | 104-C30* | 140M-F8N-C32 | 193-EEFD | 141A-W***** | 141A-W***** | 140M-F-TE | 140M-F-PNC37
AB107T-EW**-TC32...-C2D |  |  | 7-1/2 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 107T-EW**-TC32...-C2D | 9.0 … 30 | 65kA | 65kA | 30kA | 104-C30* | 140M-F8N-C32 | 193-EC2DD | 141A-W***** | 141A-W***** | 140M-F-TE | 140M-F-PNC37
AB107T-FW**-TC32...-E1F |  |  | 10 | 10 | 25 | 30 | 25.3 | 28 | 32 | 32 | 107T-FW**-TC32...-E1F | 9.0 … 32 | 65kA | 65kA | 30kA | 104-C37* | 140M-F8N-C32 | 193-EEFD | 141A-W***** | 141A-W***** | 140M-F-TE | 140M-F-PNC37
AB107T-FW**-TC32...-C2D |  |  | 10 | 10 | 25 | 30 | 25.3 | 28 | 32 | 32 | 107T-FW**-TC32...-C2D | 9.0 … 32 | 65kA | 65kA | 30kA | 104-C37* | 140M-F8N-C32 | 193-EC2DD | 141A-W***** | 141A-W***** | 140M-F-TE | 140M-F-PNC37
AB107T-FW**-TC45...-E1F |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 107T-FW**-TC45...-E1F | 9.0 … 37 | 65kA | 65kA | --- | 104-C37* | 140M-F8N-C45 | 193-EEFD | 141A-W***** | 141A-W***** | 140M-F-TE | 140M-F-PNC37
AB107T-FW**-TC45...-C2D |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 107T-FW**-TC45...-C2D | 9.0 … 37 | 65kA | 65kA | --- | 104-C37* | 140M-F8N-C45 | 193-EC2DD | 141A-W***** | 141A-W***** | 140M-F-TE | 140M-F-PNC37
AB107T-GW**-TC45...-E1F |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 107T-GW**-TC45...-E1F | 9.0 … 43 | 65kA | 65kA | --- | 104-C43* | 140M-F8N-C45 | 193-EEFD | 141A-W***** | 141A-W***** | 140M-F-TE | 140M-F-PNC43
AB107T-GW**-TC45...-C2D |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 107T-GW**-TC45...-C2D | 9.0 … 43 | 65kA | 65kA | --- | 104-C43* | 140M-F8N-C45 | 193-EC2DD | 141A-W***** | 141A-W***** | 140M-F-TE | 140M-F-PNC43
AB107T-HT**-TC45...-E1G |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 107T-HT**-TC45...-E1G | 18 … 45 | 65kA | 65kA | --- | 104-C60* | 140M-F8N-C45 | 193-EEGE | 141A-W***** | 141A-W***** | 140M-F-TE | #6 AWG Wire
AB107T-HT**-TC45...-C2D |  |  | 10 | 15 | 30 | --- | 32.2 | 42 | 40 | --- | 107T-HT**-TC45...-C2D | 9.0 … 45 | 65kA | 65kA | --- | 104-C60* | 140M-F8N-C45 | 193-EC2DE | 141A-W***** | 141A-W***** | 140M-F-TE | #6 AWG Wire
3 Component DOL Starters with 140M MCP, 193-E300 Overload Relay, 100-C Contactor, Standard Bus Bar Mounting Module
AB103T-AT**-QB10*-E..C | E |  | (1.0/6.0) | (1.0/6.0) | 0.5 | 0.75 | 1 | 1 | 1 | 1 | 103T-AT**-QB10*-E..C | 0.5 …1.0 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-B10 | 193-ESM*-30A* | 141A-G*****16 |  | 140M-C-TE1 | 140M-C-PNC23 | 2130 | 1, 5, 6 | E125316, 3:3
AB103T-AT**-QB25*-E..C |  |  | 0.5 | 0.75 | 1.5 | --- | 2.5 | 2.5 | 2.5 | --- | 103T-AT**-QB25*-E..C | 0.5 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-ESM*-30A* | 141A-G*****16 |  | 140M-C-TE1 | 140M-C-PNC23
AB103T-AT**-RB25*-E..C |  |  | 0.5 | 0.75 | 1.5 | --- | 2.5 | 2.5 | 2.5 | --- | 103T-AT**-RB25*-E..C | 0.5 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-ESM*-30A* | 141A-G*****16 |  | 140M-C-TE1 | 140M-D-PNC23
AB103T-DT**-RB40*-E..C |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 103T-DT**-RB40*-E..C | 0.5 … 4.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B40 | 193-ESM*-30A* | 141A-G*****16 |  | 140M-C-TE1 | 140M-D-PNC23
AB103T-ET**-RC10*-E..D |  |  | 3 | 3 | 7.5 | 10 | 10 | 9.6 | 10 | 10 | 103T-ET**-RC10*-E..D | 6.0 … 10.0 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C10 | 193-ESM*-60A* | 141A-G*****16 |  | 140M-C-TE1 | 140M-D-PNC30
AB103T-ET**-RC25*-E..D |  |  | 7.5 | 10 | 20 | --- | 25 | 25 | 25 | --- | 103T-ET**-RC25*-E..D | 6.0 … 25.0 | 65kA | 65kA | --- | 100-C30* | 140M-D8N-C25 | 193-ESM*-60A* | 141A-G*****25 |  | 140M-C-TE1 | 140M-D-PNC30
AB103T-FT**-RC25*-E..D |  |  | 7.5 | 10 | 20 | --- | 25 | 25 | 25 | --- | 103T-FT**-RC25*-E..D | 6.0 … 25.0 | 65kA | 65kA | --- | 100-C37* | 140M-D8N-C25 | 193-ESM*-60A* | 141A-G*****25 |  | 140M-C-TE1 | 140M-D-PNC37
AB103T-ET**-TC25*-E..D |  |  | 7.5 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 103T-ET**-TC25*-E..D | 6.0 … 25.0 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C25 | 193-ESM*-60A* | 141A-G*****25 |  | 140M-F-TE | 140M-F-PNC37
AB103T-ET**-TC32*-E..D |  |  | 7.5 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 103T-ET**-TC32*-E..D | 6.0 … 32.0 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C32 | 193-ESM*-60A* | 141A-G*****25 |  | 140M-F-TE | 140M-F-PNC37
AB103T-FT**-TC32*-E..D |  |  | 10 | 10 | 25 | 30 | 32.2 | 28 | 32 | 32 | 103T-FT**-TC32*-E..D | 6.0 … 32.0 | 65kA | 65kA | 30kA | 100-C37* | 140M-F8N-C32 | 193-ESM*-60A* | 141A-G*****25 |  | 140M-F-TE | 140M-F-PNC37
AB103T-GT**-TC32*-E..D |  |  | 10 | 10 | 25 | 30 | 32 | 28 | 32 | 32 | 103T-GT**-TC32*-E..D | 6.0 … 32.0 | 65kA | 65kA | 30kA | 100-C43* | 140M-F8N-C32 | 193-ESM*-60A* | 141A-G*****25 |  | 140M-F-TE | 140M-F-PNC43
AB103T-FT**-TC45*-E..D |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 103T-FT**-TC45*-E..D | 6.0 … 37.0 | 65kA | 65kA | --- | 100-C37* | 140M-F8N-C45 | 193-ESM*-60A* | 141A-G*****45 |  | 140M-F-TE | 140M-F-PNC37
AB103T-GT**-TC45*-E..D |  |  | 10 | 10 | 30 | --- | 25 | 28 | 40 | --- | 103T-GT**-TC45*-E..D | 6.0 … 40.0 | 65kA | 65kA | --- | 100-C43* | 140M-F8N-C45 | 193-ESM*-60A* | 141A-G*****45 |  | 140M-F-TE | 140M-F-PNC43
AB103T-QT**-TC45*-E..D |  |  | 10 | 10 | 30 | --- | 25 | 28 | 40 | --- | 103T-QT**-TC45*-E..D | 6.0 … 40.0 | 65kA | 65kA | --- | 100-C55* | 140M-F8N-C45 | 193-ESM*-60A* | 141A-G*****45 |  | 140M-F-TE | 140M-F-PNC43
AB103T-HT**-TC45*-E..E |  |  | 10 | 10 | 30 | --- | 25.3 | 28 | 40 | --- | 103T-HT**-TC45*-E..E | 10.0 … 40.0 | 65kA | 65kA | --- | 100-C60* | 140M-F8N-C45 | 193-ESM*-100A* | 141A-G*****45 |  | 140M-F-TE | 6 AWG Wire
AB103T-JT**-TC45*-E..E |  |  | 10 | 10 | 30 | --- | 25.3 | 28 | 40 | --- | 103T-JT**-TC45*-E..E | 10.0 … 40.0 | 65kA | 65kA | --- | 100-C72* | 140M-F8N-C45 | 193-ESM*-100A* | 141A-G*****45 |  | 140M-F-TE | 6 AWG Wire
3 Component Reversing Starters with 140M MCP, 193-E300 Overload Relay, 100-C Contactors, Standard Bus Bar Mounting Modules
AB107T-AT**-QB10*-E..C | E |  | (1.0/6.0) | (1.0/6.0) | 0.5 | 0.75 | 1 | 1 | 1 | 1 | 107T-AT**-QB10*-E..C | 0.5 …1.0 | 65kA | 65kA | 47kA | 104-C09* | 140M-C2N-B10 | 193-ESM*-30A* | 141A-G*****16 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23 | 2130 | 1, 5, 6 | E125316, 3:3
AB107T-AT**-QB25*-E..C |  |  | 0.5 | 0.75 | 1.5 | --- | 2.5 | 2.5 | 2.5 | --- | 107T-AT**-QB25*-E..C | 0.5 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-C2N-B25 | 193-ESM*-30A* | 141A-G*****16 | 141A-G**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AT**-RB25*-E..C |  |  | 0.5 | 0.75 | 1.5 | --- | 2.5 | 2.5 | 2.5 | --- | 107T-AT**-RB25*-E..C | 0.5 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-D8N-B25 | 193-ESM*-30A* | 141A-G*****16 | 141A-G**** | 140M-C-TE1 | 140M-D-PNC23
AB107T-DT**-RB40*-E..C |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 107T-DT**-RB40*-E..C | 0.5 … 4.0 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B40 | 193-ESM*-30A* | 141A-G*****16 | 141A-G**** | 140M-C-TE1 | 140M-D-PNC23
AB107T-ET**-RC10*-E..D |  |  | 3 | 3 | 7.5 | 10 | 10 | 9.6 | 10 | 10 | 107T-ET**-RC10*-E..D | 6.0 … 10.0 | 65kA | 65kA | 30kA | 104-C30* | 140M-D8N-C10 | 193-ESM*-60A* | 141A-G*****16 | 141A-G**** | 140M-C-TE1 | 140M-D-PNC30
AB107T-ET**-RC25*-E..D |  |  | 7.5 | 10 | 20 | --- | 25 | 25 | 25 | --- | 107T-ET**-RC25*-E..D | 6.0 … 25.0 | 65kA | 65kA | --- | 104-C30* | 140M-D8N-C25 | 193-ESM*-60A* | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-D-PNC30
AB107T-FT**-RC25*-E..D |  |  | 7.5 | 10 | 20 | --- | 25 | 25 | 25 | --- | 107T-FT**-RC25*-E..D | 6.0 … 25.0 | 65kA | 65kA | --- | 104-C37* | 140M-D8N-C25 | 193-ESM*-60A* | 141A-G*****25 | 141A-G**** | 140M-C-TE1 | 140M-D-PNC37
AB107T-ET**-TC25*-E..D |  |  | 7.5 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 107T-ET**-TC25*-E..D | 6.0 … 25.0 | 65kA | 65kA | 30kA | 104-C30* | 140M-F8N-C25 | 193-ESM*-60A* | 141A-G*****25 | 141A-G**** | 140M-F-TE | 140M-F-PNC37
AB107T-ET**-TC32*-E..D |  |  | 7.5 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 107T-ET**-TC32*-E..D | 6.0 … 32.0 | 65kA | 65kA | 30kA | 104-C30* | 140M-F8N-C32 | 193-ESM*-60A* | 141A-G*****25 | 141A-G**** | 140M-F-TE | 140M-F-PNC37
AB107T-FT**-TC32*-E..D |  |  | 10 | 10 | 25 | 30 | 32.2 | 28 | 32 | 32 | 107T-FT**-TC32*-E..D | 6.0 … 32.0 | 65kA | 65kA | 30kA | 104-C37* | 140M-F8N-C32 | 193-ESM*-60A* | 141A-G*****25 | 141A-G**** | 140M-F-TE | 140M-F-PNC37
AB107T-GT**-TC32*-E..D |  |  | 10 | 10 | 25 | 30 | 32 | 28 | 32 | 32 | 107T-GT**-TC32*-E..D | 6.0 … 32.0 | 65kA | 65kA | 30kA | 104-C43* | 140M-F8N-C32 | 193-ESM*-60A* | 141A-G*****25 | 141A-G**** | 140M-F-TE | 140M-F-PNC43
AB107T-FT**-TC45*-E..D |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 107T-FT**-TC45*-E..D | 6.0 … 37.0 | 65kA | 65kA | --- | 104-C37* | 140M-F8N-C45 | 193-ESM*-60A* | 141A-G*****45 | 141A-G**** | 140M-F-TE | 140M-F-PNC37
AB107T-GT**-TC45*-E..D |  |  | 10 | 10 | 30 | --- | 25 | 28 | 40 | --- | 107T-GT**-TC45*-E..D | 6.0 … 40.0 | 65kA | 65kA | --- | 104-C43* | 140M-F8N-C45 | 193-ESM*-60A* | 141A-G*****45 | 141A-G**** | 140M-F-TE | 140M-F-PNC43
AB107T-QT**-TC45*-E..D |  |  | 10 | 10 | 30 | --- | 25 | 28 | 40 | --- | 107T-QT**-TC45*-E..D | 6.0 … 40.0 | 65kA | 65kA | --- | 104-C55* | 140M-F8N-C45 | 193-ESM*-60A* | 141A-G*****45 | 141A-G**** | 140M-F-TE | 140M-F-PNC43
AB107T-HT**-TC45*-E..E |  |  | 10 | 10 | 30 | --- | 25.3 | 28 | 40 | --- | 107T-HT**-TC45*-E..E | 10.0 … 40.0 | 65kA | 65kA | --- | 104-C60* | 140M-F8N-C45 | 193-ESM*-100A* | 141A-G*****45 | 141A-G**** | 140M-F-TE | 6 AWG Wire
AB107T-JT**-TC45*-E..E |  |  | 10 | 10 | 30 | --- | 25.3 | 28 | 40 | --- | 107T-JT**-TC45*-E..E | 10.0 … 40.0 | 65kA | 65kA | --- | 104-C72* | 140M-F8N-C45 | 193-ESM*-100A* | 141A-G*****45 | 141A-G**** | 140M-F-TE | 6 AWG Wire
3 Component DOL Starters with 140M MCP, 193-E300 Overload Relay, 100-C Contactor, ISO Bus Bar Mounting Module
AB103T-AS**-QB10*-E..C | E |  | (1.0/6.0) | (1.0/6.0) | 0.5 | 0.75 | 1 | 1 | 1 | 1 | 103T-AS**-QB10*-E..C | 0.5 …1.0 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-B10 | 193-ESM*-30A* | 141A-S*****16 |  | 140M-C-TE1 | 140M-C-PNC23 | 2130 | 1, 5, 6 | E125316, 3:3
AB103T-AS**-QB25*-E..C |  |  | 0.5 | 0.75 | 1.5 | --- | 2.5 | 2.5 | 2.5 | --- | 103T-AS**-QB25*-E..C | 0.5 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-ESM*-30A* | 141A-S*****16 |  | 140M-C-TE1 | 140M-C-PNC23
AB103T-AS**-RB25*-E..C |  |  | 0.5 | 0.75 | 1.5 | --- | 2.5 | 2.5 | 2.5 | --- | 103T-AS**-RB25*-E..C | 0.5 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-ESM*-30A* | 141A-S*****16 |  | 140M-C-TE1 | 140M-D-PNC23
AB103T-DS**-RB40*-E..C |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 103T-DS**-RB40*-E..C | 0.5 … 4.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B40 | 193-ESM*-30A* | 141A-S*****16 |  | 140M-C-TE1 | 140M-D-PNC23
AB103T-ES**-RC10*-E..D |  |  | 3 | 3 | 7.5 | 10 | 10 | 9.6 | 10 | 10 | 103T-ES**-RC10*-E..D | 6.0 … 10.0 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C10 | 193-ESM*-60A* | 141A-S*****16 |  | 140M-C-TE1 | 140M-D-PNC30
AB103T-ES**-RC25*-E..D |  |  | 7.5 | 10 | 20 | --- | 25 | 25 | 25 | --- | 103T-ES**-RC25*-E..D | 6.0 … 25.0 | 65kA | 65kA | --- | 100-C30* | 140M-D8N-C25 | 193-ESM*-60A* | 141A-S*****25 |  | 140M-C-TE1 | 140M-D-PNC30
AB103T-FS**-RC25*-E..D |  |  | 7.5 | 10 | 20 | --- | 25 | 25 | 25 | --- | 103T-FS**-RC25*-E..D | 6.0 … 25.0 | 65kA | 65kA | --- | 100-C37* | 140M-D8N-C25 | 193-ESM*-60A* | 141A-S*****25 |  | 140M-C-TE1 | 140M-D-PNC37
AB103T-ES**-TC25*-E..D |  |  | 7.5 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 103T-ES**-TC25*-E..D | 6.0 … 25.0 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C25 | 193-ESM*-60A* | 141A-S*****25 |  | 140M-F-TE | 140M-F-PNC37
AB103T-ES**-TC32*-E..D |  |  | 7.5 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 103T-ES**-TC32*-E..D | 6.0 … 32.0 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C32 | 193-ESM*-60A* | 141A-S*****25 |  | 140M-F-TE | 140M-F-PNC37
AB103T-FS**-TC32*-E..D |  |  | 10 | 10 | 25 | 30 | 32.2 | 28 | 32 | 32 | 103T-FS**-TC32*-E..D | 6.0 … 32.0 | 65kA | 65kA | 30kA | 100-C37* | 140M-F8N-C32 | 193-ESM*-60A* | 141A-S*****25 |  | 140M-F-TE | 140M-F-PNC37
AB103T-GS**-TC32*-E..D |  |  | 10 | 10 | 25 | 30 | 32 | 28 | 32 | 32 | 103T-GS**-TC32*-E..D | 6.0 … 32.0 | 65kA | 65kA | 30kA | 100-C43* | 140M-F8N-C32 | 193-ESM*-60A* | 141A-S*****25 |  | 140M-F-TE | 140M-F-PNC43
AB103T-FS**-TC45*-E..D |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 103T-FS**-TC45*-E..D | 6.0 … 37.0 | 65kA | 65kA | --- | 100-C37* | 140M-F8N-C45 | 193-ESM*-60A* | 141A-S*****45 |  | 140M-F-TE | 140M-F-PNC37
AB103T-GS**-TC45*-E..D |  |  | 10 | 10 | 30 | --- | 25 | 28 | 40 | --- | 103T-GS**-TC45*-E..D | 6.0 … 40.0 | 65kA | 65kA | --- | 100-C43* | 140M-F8N-C45 | 193-ESM*-60A* | 141A-S*****45 |  | 140M-F-TE | 140M-F-PNC43
AB103T-QS**-TC45*-E..D |  |  | 10 | 10 | 30 | --- | 25 | 28 | 40 | --- | 103T-QS**-TC45*-E..D | 6.0 … 40.0 | 65kA | 65kA | --- | 100-C55* | 140M-F8N-C45 | 193-ESM*-60A* | 141A-S*****45 |  | 140M-F-TE | 140M-F-PNC43
AB103T-HS**-TC45*-E..E |  |  | 10 | 10 | 30 | --- | 25.3 | 28 | 40 | --- | 103T-HS**-TC45*-E..E | 10.0 … 40.0 | 65kA | 65kA | --- | 100-C60* | 140M-F8N-C45 | 193-ESM*-100A* | 141A-S*****45 |  | 140M-F-TE | 6 AWG Wire
AB103T-JS**-TC45*-E..E |  |  | 10 | 10 | 30 | --- | 25.3 | 28 | 40 | --- | 103T-JS**-TC45*-E..E | 10.0 … 40.0 | 65kA | 65kA | --- | 100-C72* | 140M-F8N-C45 | 193-ESM*-100A* | 141A-S*****45 |  | 140M-F-TE | 6 AWG Wire
3 Component Reversing Starters with 140M MCP, 193-E300 Overload Relay, 100-C Contactors, ISO Bus Bar Mounting Modules
AB107T-AS**-QB10*-E..C | E |  | (1.0/6.0) | (1.0/6.0) | 0.5 | 0.75 | 1 | 1 | 1 | 1 | 107T-AS**-QB10*-E..C | 0.5 …1.0 | 65kA | 65kA | 47kA | 104-C09* | 140M-C2N-B10 | 193-ESM*-30A* | 141A-S*****16 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23 | 2130 | 1, 5, 6 | E125316, 3:3
AB107T-AS**-QB25*-E..C |  |  | 0.5 | 0.75 | 1.5 | --- | 2.5 | 2.5 | 2.5 | --- | 107T-AS**-QB25*-E..C | 0.5 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-C2N-B25 | 193-ESM*-30A* | 141A-S*****16 | 141A-S**** | 140M-C-TE1 | 140M-C-PNC23
AB107T-AS**-RB25*-E..C |  |  | 0.5 | 0.75 | 1.5 | --- | 2.5 | 2.5 | 2.5 | --- | 107T-AS**-RB25*-E..C | 0.5 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-D8N-B25 | 193-ESM*-30A* | 141A-S*****16 | 141A-S**** | 140M-C-TE1 | 140M-D-PNC23
AB107T-DS**-RB40*-E..C |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 107T-DS**-RB40*-E..C | 0.5 … 4.0 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B40 | 193-ESM*-30A* | 141A-S*****16 | 141A-S**** | 140M-C-TE1 | 140M-D-PNC23
AB107T-ES**-RC10*-E..D |  |  | 3 | 3 | 7.5 | 10 | 10 | 9.6 | 10 | 10 | 107T-ES**-RC10*-E..D | 6.0 … 10.0 | 65kA | 65kA | 30kA | 104-C30* | 140M-D8N-C10 | 193-ESM*-60A* | 141A-S*****16 | 141A-S**** | 140M-C-TE1 | 140M-D-PNC30
AB107T-ES**-RC25*-E..D |  |  | 7.5 | 10 | 20 | --- | 25 | 25 | 25 | --- | 107T-ES**-RC25*-E..D | 6.0 … 25.0 | 65kA | 65kA | --- | 104-C30* | 140M-D8N-C25 | 193-ESM*-60A* | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-D-PNC30
AB107T-FS**-RC25*-E..D |  |  | 7.5 | 10 | 20 | --- | 25 | 25 | 25 | --- | 107T-FS**-RC25*-E..D | 6.0 … 25.0 | 65kA | 65kA | --- | 104-C37* | 140M-D8N-C25 | 193-ESM*-60A* | 141A-S*****25 | 141A-S**** | 140M-C-TE1 | 140M-D-PNC37
AB107T-ES**-TC25*-E..D |  |  | 7.5 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 107T-ES**-TC25*-E..D | 6.0 … 25.0 | 65kA | 65kA | 30kA | 104-C30* | 140M-F8N-C25 | 193-ESM*-60A* | 141A-S*****25 | 141A-S**** | 140M-F-TE | 140M-F-PNC37
AB107T-ES**-TC32*-E..D |  |  | 7.5 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 107T-ES**-TC32*-E..D | 6.0 … 32.0 | 65kA | 65kA | 30kA | 104-C30* | 140M-F8N-C32 | 193-ESM*-60A* | 141A-S*****25 | 141A-S**** | 140M-F-TE | 140M-F-PNC37
AB107T-FS**-TC32*-E..D |  |  | 10 | 10 | 25 | 30 | 32.2 | 28 | 32 | 32 | 107T-FS**-TC32*-E..D | 6.0 … 32.0 | 65kA | 65kA | 30kA | 104-C37* | 140M-F8N-C32 | 193-ESM*-60A* | 141A-S*****25 | 141A-S**** | 140M-F-TE | 140M-F-PNC37
AB107T-GS**-TC32*-E..D |  |  | 10 | 10 | 25 | 30 | 32 | 28 | 32 | 32 | 107T-GS**-TC32*-E..D | 6.0 … 32.0 | 65kA | 65kA | 30kA | 104-C43* | 140M-F8N-C32 | 193-ESM*-60A* | 141A-S*****25 | 141A-S**** | 140M-F-TE | 140M-F-PNC43
AB107T-FS**-TC45*-E..D |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 107T-FS**-TC45*-E..D | 6.0 … 37.0 | 65kA | 65kA | --- | 104-C37* | 140M-F8N-C45 | 193-ESM*-60A* | 141A-S*****45 | 141A-S**** | 140M-F-TE | 140M-F-PNC37
AB107T-GS**-TC45*-E..D |  |  | 10 | 10 | 30 | --- | 25 | 28 | 40 | --- | 107T-GS**-TC45*-E..D | 6.0 … 40.0 | 65kA | 65kA | --- | 104-C43* | 140M-F8N-C45 | 193-ESM*-60A* | 141A-S*****45 | 141A-S**** | 140M-F-TE | 140M-F-PNC43
AB107T-QS**-TC45*-E..D |  |  | 10 | 10 | 30 | --- | 25 | 28 | 40 | --- | 107T-QS**-TC45*-E..D | 6.0 … 40.0 | 65kA | 65kA | --- | 104-C55* | 140M-F8N-C45 | 193-ESM*-60A* | 141A-S*****45 | 141A-S**** | 140M-F-TE | 140M-F-PNC43
AB107T-HS**-TC45*-E..E |  |  | 10 | 10 | 30 | --- | 25.3 | 28 | 40 | --- | 107T-HS**-TC45*-E..E | 10.0 … 40.0 | 65kA | 65kA | --- | 104-C60* | 140M-F8N-C45 | 193-ESM*-100A* | 141A-S*****45 | 141A-S**** | 140M-F-TE | 6 AWG Wire
AB107T-JS**-TC45*-E..E |  |  | 10 | 10 | 30 | --- | 25.3 | 28 | 40 | --- | 107T-JS**-TC45*-E..E | 10.0 … 40.0 | 65kA | 65kA | --- | 104-C72* | 140M-F8N-C45 | 193-ESM*-100A* | 141A-S*****45 | 141A-S**** | 140M-F-TE | 6 AWG Wire
3 Component DOL Starters with 140M MCP, 193-E300 Overload Relay, 100-C Contactor, Panel Mount Module
AB103T-AW**-QB10*-E..C | E |  | (1.0/6.0) | (1.0/6.0) | 0.5 | 0.75 | 1 | 1 | 1 | 1 | 103T-AW**-QB10*-E..C | 0.5 …1.0 | 65kA | 65kA | 47kA | 100-C09* | 140M-C2N-B10 | 193-ESM*-30A* | 141A-W* |  | 140M-C-TE1 | 140M-C-PNC23 | 2130 | 1, 5, 6 | E125316, 3:3
AB103T-AW**-QB25*-E..C |  |  | 0.5 | 0.75 | 1.5 | --- | 2.5 | 2.5 | 2.5 | --- | 103T-AW**-QB25*-E..C | 0.5 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-C2N-B25 | 193-ESM*-30A* | 141A-W* |  | 140M-C-TE1 | 140M-C-PNC23
AB103T-AW**-RB25*-E..C |  |  | 0.5 | 0.75 | 1.5 | --- | 2.5 | 2.5 | 2.5 | --- | 103T-AW**-RB25*-E..C | 0.5 … 2.5 | 65kA | 65kA | --- | 100-C09* | 140M-D8N-B25 | 193-ESM*-30A* | 141A-W* |  | 140M-C-TE1 | 140M-D-PNC23
AB103T-DW**-RB40*-E..C |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 103T-DW**-RB40*-E..C | 0.5 … 4.0 | 65kA | 65kA | 30kA | 100-C23* | 140M-D8N-B40 | 193-ESM*-30A* | 141A-W* |  | 140M-C-TE1 | 140M-D-PNC23
AB103T-EW**-RC10*-E..D |  |  | 3 | 3 | 7.5 | 10 | 10 | 9.6 | 10 | 10 | 103T-EW**-RC10*-E..D | 6.0 … 10.0 | 65kA | 65kA | 30kA | 100-C30* | 140M-D8N-C10 | 193-ESM*-60A* | 141A-W* |  | 140M-C-TE1 | 140M-D-PNC30
AB103T-EW**-RC25*-E..D |  |  | 7.5 | 10 | 20 | --- | 25 | 25 | 25 | --- | 103T-EW**-RC25*-E..D | 6.0 … 25.0 | 65kA | 65kA | --- | 100-C30* | 140M-D8N-C25 | 193-ESM*-60A* | 141A-W* |  | 140M-C-TE1 | 140M-D-PNC30
AB103T-FW**-RC25*-E..D |  |  | 7.5 | 10 | 20 | --- | 25 | 25 | 25 | --- | 103T-FW**-RC25*-E..D | 6.0 … 25.0 | 65kA | 65kA | --- | 100-C37* | 140M-D8N-C25 | 193-ESM*-60A* | 141A-W* |  | 140M-C-TE1 | 140M-D-PNC37
AB103T-EW**-TC25*-E..D |  |  | 7.5 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 103T-EW**-TC25*-E..D | 6.0 … 25.0 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C25 | 193-ESM*-60A* | 141A-W* |  | 140M-F-TE | 140M-F-PNC37
AB103T-EW**-TC32*-E..D |  |  | 7.5 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 103T-EW**-TC32*-E..D | 6.0 … 32.0 | 65kA | 65kA | 30kA | 100-C30* | 140M-F8N-C32 | 193-ESM*-60A* | 141A-W* |  | 140M-F-TE | 140M-F-PNC37
AB103T-FW**-TC32*-E..D |  |  | 10 | 10 | 25 | 30 | 32.2 | 28 | 32 | 32 | 103T-FW**-TC32*-E..D | 6.0 … 32.0 | 65kA | 65kA | 30kA | 100-C37* | 140M-F8N-C32 | 193-ESM*-60A* | 141A-W* |  | 140M-F-TE | 140M-F-PNC37
AB103T-GW**-TC32*-E..D |  |  | 10 | 10 | 25 | 30 | 32 | 28 | 32 | 32 | 103T-GW**-TC32*-E..D | 6.0 … 32.0 | 65kA | 65kA | 30kA | 100-C43* | 140M-F8N-C32 | 193-ESM*-60A* | 141A-W* |  | 140M-F-TE | 140M-F-PNC43
AB103T-FW**-TC45*-E..D |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 103T-FW**-TC45*-E..D | 6.0 … 37.0 | 65kA | 65kA | --- | 100-C37* | 140M-F8N-C45 | 193-ESM*-60A* | 141A-W* |  | 140M-F-TE | 140M-F-PNC37
AB103T-GW**-TC45*-E..D |  |  | 10 | 10 | 30 | --- | 25 | 28 | 40 | --- | 103T-GW**-TC45*-E..D | 6.0 … 40.0 | 65kA | 65kA | --- | 100-C43* | 140M-F8N-C45 | 193-ESM*-60A* | 141A-W* |  | 140M-F-TE | 140M-F-PNC43
AB103T-QW**-TC45*-E..D |  |  | 10 | 10 | 30 | --- | 25 | 28 | 40 | --- | 103T-QW**-TC45*-E..D | 6.0 … 40.0 | 65kA | 65kA | --- | 100-C55* | 140M-F8N-C45 | 193-ESM*-60A* | 141A-W* |  | 140M-F-TE | 140M-F-PNC43
3 Component Reversing Starters with 140M MCP, 193-E300 Overload Relay, 100-C Contactors, Panel Mount Modules
AB107T-AW**-QB10*-E..C | E |  | (1.0/6.0) | (1.0/6.0) | 0.5 | 0.75 | 1 | 1 | 1 | 1 | 107T-AW**-QB10*-E..C | 0.5 …1.0 | 65kA | 65kA | 47kA | 104-C09* | 140M-C2N-B10 | 193-ESM*-30A* | 141A-W* | 141A-W* | 140M-C-TE1 | 140M-C-PNC23 | 2130 | 1, 5, 6 | E125316, 3:3
AB107T-AW**-QB25*-E..C |  |  | 0.5 | 0.75 | 1.5 | --- | 2.5 | 2.5 | 2.5 | --- | 107T-AW**-QB25*-E..C | 0.5 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-C2N-B25 | 193-ESM*-30A* | 141A-W* | 141A-W* | 140M-C-TE1 | 140M-C-PNC23
AB107T-AW**-RB25*-E..C |  |  | 0.5 | 0.75 | 1.5 | --- | 2.5 | 2.5 | 2.5 | --- | 107T-AW**-RB25*-E..C | 0.5 … 2.5 | 65kA | 65kA | --- | 104-C09* | 140M-D8N-B25 | 193-ESM*-30A* | 141A-W* | 141A-W* | 140M-C-TE1 | 140M-D-PNC23
AB107T-DW**-RB40*-E..C |  |  | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3.9 | 107T-DW**-RB40*-E..C | 0.5 … 4.0 | 65kA | 65kA | 30kA | 104-C23* | 140M-D8N-B40 | 193-ESM*-30A* | 141A-W* | 141A-W* | 140M-C-TE1 | 140M-D-PNC23
AB107T-EW**-RC10*-E..D |  |  | 3 | 3 | 7.5 | 10 | 10 | 9.6 | 10 | 10 | 107T-EW**-RC10*-E..D | 6.0 … 10.0 | 65kA | 65kA | 30kA | 104-C30* | 140M-D8N-C10 | 193-ESM*-60A* | 141A-W* | 141A-W* | 140M-C-TE1 | 140M-D-PNC30
AB107T-EW**-RC25*-E..D |  |  | 7.5 | 10 | 20 | --- | 25 | 25 | 25 | --- | 107T-EW**-RC25*-E..D | 6.0 … 25.0 | 65kA | 65kA | --- | 104-C30* | 140M-D8N-C25 | 193-ESM*-60A* | 141A-W* | 141A-W* | 140M-C-TE1 | 140M-D-PNC30
AB107T-FW**-RC25*-E..D |  |  | 7.5 | 10 | 20 | --- | 25 | 25 | 25 | --- | 107T-FW**-RC25*-E..D | 6.0 … 25.0 | 65kA | 65kA | --- | 104-C37* | 140M-D8N-C25 | 193-ESM*-60A* | 141A-W* | 141A-W* | 140M-C-TE1 | 140M-D-PNC37
AB107T-EW**-TC25*-E..D |  |  | 7.5 | 10 | 20 | 20 | 25 | 25 | 25 | 22 | 107T-EW**-TC25*-E..D | 6.0 … 25.0 | 65kA | 65kA | 30kA | 104-C30* | 140M-F8N-C25 | 193-ESM*-60A* | 141A-W* | 141A-W* | 140M-F-TE | 140M-F-PNC37
AB107T-EW**-TC32*-E..D |  |  | 7.5 | 10 | 20 | 25 | 25.3 | 28 | 27 | 27 | 107T-EW**-TC32*-E..D | 6.0 … 32.0 | 65kA | 65kA | 30kA | 104-C30* | 140M-F8N-C32 | 193-ESM*-60A* | 141A-W* | 141A-W* | 140M-F-TE | 140M-F-PNC37
AB107T-FW**-TC32*-E..D |  |  | 10 | 10 | 25 | 30 | 32.2 | 28 | 32 | 32 | 107T-FW**-TC32*-E..D | 6.0 … 32.0 | 65kA | 65kA | 30kA | 104-C37* | 140M-F8N-C32 | 193-ESM*-60A* | 141A-W* | 141A-W* | 140M-F-TE | 140M-F-PNC37
AB107T-GW**-TC32*-E..D |  |  | 10 | 10 | 25 | 30 | 32 | 28 | 32 | 32 | 107T-GW**-TC32*-E..D | 6.0 … 32.0 | 65kA | 65kA | 30kA | 104-C43* | 140M-F8N-C32 | 193-ESM*-60A* | 141A-W* | 141A-W* | 140M-F-TE | 140M-F-PNC43
AB107T-FW**-TC45*-E..D |  |  | 10 | 10 | 25 | --- | 32.2 | 28 | 34 | --- | 107T-FW**-TC45*-E..D | 6.0 … 37.0 | 65kA | 65kA | --- | 104-C37* | 140M-F8N-C45 | 193-ESM*-60A* | 141A-W* | 141A-W* | 140M-F-TE | 140M-F-PNC37
AB107T-GW**-TC45*-E..D |  |  | 10 | 10 | 30 | --- | 25 | 28 | 40 | --- | 107T-GW**-TC45*-E..D | 6.0 … 40.0 | 65kA | 65kA | --- | 104-C43* | 140M-F8N-C45 | 193-ESM*-60A* | 141A-W* | 141A-W* | 140M-F-TE | 140M-F-PNC43
AB107T-QW**-TC45*-E..D |  |  | 10 | 10 | 30 | --- | 25 | 28 | 40 | --- | 107T-QW**-TC45*-E..D | 6.0 … 40.0 | 65kA | 65kA | --- | 104-C55* | 140M-F8N-C45 | 193-ESM*-60A* | 141A-W* | 141A-W* | 140M-F-TE | 140M-F-PNC43
Notes:
[1] Horsepower ratings shown are for reference only, final selection of starter depends on the actual motor full load current and service factor
[2] Full load current values from NEC Table 430.25 or represent the maximum current rating of the combination motor controller
[3] Minimum Contactor Size - Contactors may be upsized within the frame to provide increased electrical life
[4] 6 AWG wire must be UL rated 600V, 150 Deg C.
* Insert appropriate coil code and auxiliary contact code
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches.
Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).

## Const. F w MPCB (190E-K-191E-K)
Issued: 2009-11-11
Last Revised: 2014-09-29
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP rating | Enclosure Volume, CU inches
AB190E-KM...-CA16.-..200V | F | MSP | Allen Bradley | 140M-C2E-A16 | 200 | 3 | 65 | 0.16 | - | 200 | 3 | 65 | 0.16 FLA / 0.96 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB190E-KM...-CA16.-..230V | F | MSP | Allen Bradley | 140M-C2E-A16 | 230 | 3 | 65 | 0.16 | - | 230 | 3 | 65 | 0.16 FLA / 0.96 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 230 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB190E-KM...-CA16.-..460V | F | MSP | Allen Bradley | 140M-C2E-A16 | 460 | 3 | 65 | 0.16 | - | 480Y/277 | 3 | 65 | 0.16 FLA / 0.96 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 460 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB190E-KM...-CA16.-..575V | F | MSP | Allen Bradley | 140M-C2E-A16 | 575 | 3 | 47 | 0.16 | - | 600Y/347 | 3 | 47 | 0.16 FLA / 0.96 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 575 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB190E-KM...-CA25.-..200V | F | MSP | Allen Bradley | 140M-C2E-A25 | 200 | 3 | 65 | 0.25 | - | 200 | 3 | 65 | 0.25 FLA / 1.5 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB190E-KM...-CA25.-..230V | F | MSP | Allen Bradley | 140M-C2E-A25 | 230 | 3 | 65 | 0.25 | - | 230 | 3 | 65 | 0.25 FLA / 1.5 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 230 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB190E-KM...-CA25.-..460V | F | MSP | Allen Bradley | 140M-C2E-A25 | 460 | 3 | 65 | 0.25 | - | 480Y/277 | 3 | 65 | 0.25 FLA / 1.5 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 460 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB190E-KM...-CA25.-..575V | F | MSP | Allen Bradley | 140M-C2E-A25 | 575 | 3 | 47 | 0.25 | - | 600Y/347 | 3 | 47 | 0.25 FLA / 1.5 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 575 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB190E-KM...-CA40.-..200V | F | MSP | Allen Bradley | 140M-C2E-A40 | 200 | 3 | 65 | 0.4 | - | 200 | 3 | 65 | 0.4 FLA / 2.4 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB190E-KM...-CA40.-..230V | F | MSP | Allen Bradley | 140M-C2E-A40 | 230 | 3 | 65 | 0.4 | - | 230 | 3 | 65 | 0.4 FLA / 2.4 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 230 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB190E-KM...-CA40.-..460V | F | MSP | Allen Bradley | 140M-C2E-A40 | 460 | 3 | 65 | 0.4 | - | 480Y/277 | 3 | 65 | 0.4 FLA / 2.4 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 460 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB190E-KM...-CA40.-..575V | F | MSP | Allen Bradley | 140M-C2E-A40 | 575 | 3 | 47 | 0.4 | - | 600Y/347 | 3 | 47 | 0.4 FLA / 2.4 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 575 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB190E-KM...-CA63.-..200V | F | MSP | Allen Bradley | 140M-C2E-A63 | 200 | 3 | 65 | 0.63 | - | 200 | 3 | 65 | 0.63 FLA / 3.78 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB190E-KM...-CA63.-..230V | F | MSP | Allen Bradley | 140M-C2E-A63 | 230 | 3 | 65 | 0.63 | - | 230 | 3 | 65 | 0.63 FLA / 3.78 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 230 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB190E-KM...-CA63.-..460V | F | MSP | Allen Bradley | 140M-C2E-A63 | 460 | 3 | 65 | 0.63 | - | 480Y/277 | 3 | 65 | 0.63 FLA / 3.78 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 460 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB190E-KM...-CA63.-..575V | F | MSP | Allen Bradley | 140M-C2E-A63 | 575 | 3 | 47 | 0.63 | - | 600Y/347 | 3 | 47 | 0.63 FLA / 3.78 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 575 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB190E-KM...-CB10.-..200V | F | MSP | Allen Bradley | 140M-C2E-B10 | 200 | 3 | 65 | 1 | - | 200 | 3 | 65 | 1.0 FLA / 6.0 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB190E-KM...-CB10.-..230V | F | MSP | Allen Bradley | 140M-C2E-B10 | 230 | 3 | 65 | 1 | - | 230 | 3 | 65 | 1.0 FLA / 6.0 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 230 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB190E-KM...-CB10.-..460V | F | MSP | Allen Bradley | 140M-C2E-B10 | 460 | 3 | 65 | 1 | 0.5 | 480Y/277 | 3 | 65 | 1 | 0.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 460 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB190E-KM...-CB10.-..575V | F | MSP | Allen Bradley | 140M-C2E-B10 | 575 | 3 | 47 | 1 | 0.75 | 600Y/347 | 3 | 47 | 1 | 0.75 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 575 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB190E-KM...-CB16.-..200V | F | MSP | Allen Bradley | 140M-C2E-B16 | 200 | 3 | 65 | 1.6 | - | 200 | 3 | 65 | 1.6 FLA / 9.6 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB190E-KM...-CB16.-..230V | F | MSP | Allen Bradley | 140M-C2E-B16 | 230 | 3 | 65 | 1.6 | - | 230 | 3 | 65 | 1.6 FLA / 9.6 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 230 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB190E-KM...-CB16.-..460V | F | MSP | Allen Bradley | 140M-C2E-B16 | 460 | 3 | 65 | 1.6 | 1 | 480Y/277 | 3 | 65 | 1.6 | 1 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 460 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB190E-KM...-CB16.-..575V | F | MSP | Allen Bradley | 140M-C2E-B16 | 575 | 3 | 47 | 1.6 | 1 | 600Y/347 | 3 | 47 | 1.6 | 1 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 575 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB190E-KM...-CB25.-..200V | F | MSP | Allen Bradley | 140M-C2E-B25 | 200 | 3 | 65 | 2.5 | 0.5 | 200 | 3 | 65 | 2.5 | 0.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB190E-KM...-CB25.-..230V | F | MSP | Allen Bradley | 140M-C2E-B25 | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.5 | 0.75 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 230 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB190E-KM...-CB25.-..460V | F | MSP | Allen Bradley | 140M-C2E-B25 | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 460 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB190E-KM...-CB25.-..575V | F | MSP | Allen Bradley | 140M-C2E-B25 | 575 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 30 | 2.5 | 2 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 575 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB190E-KM...-CB40.-..200V | F | MSP | Allen Bradley | 140M-C2E-B40 | 200 | 3 | 65 | 4 | 1 | 200 | 3 | 65 | 4 | 1 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB190E-KM...-CB40.-..230V | F | MSP | Allen Bradley | 140M-C2E-B40 | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 4 | 1 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 230 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB190E-KM...-CB40.-..460V | F | MSP | Allen Bradley | 140M-C2E-B40 | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 460 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB190E-KM...-CB40.-..575V | F | MSP | Allen Bradley | 140M-C2E-B40 | 575 | 3 | 25 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 575 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB190E-KM...-CB63.-..200V | F | MSP | Allen Bradley | 140M-C2E-B63 | 200 | 3 | 65 | 6.3 | 1.5 | 200 | 3 | 65 | 6.3 | 1.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB190E-KM...-CB63.-..230V | F | MSP | Allen Bradley | 140M-C2E-B63 | 230 | 3 | 65 | 6.3 | 2 | 230 | 3 | 65 | 6 | 1.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 230 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB190E-KM...-CB63.-..460V | F | MSP | Allen Bradley | 140M-C2E-B63 | 460 | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 4.8 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 460 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB190E-KN...-CB25.-..200V | F | MSP | Allen Bradley | 140M-C2E-B25 | 200 | 3 | 65 | 2.5 | 0.5 | 200 | 3 | 65 | 2.5 | 0.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB190E-KN...-CB25.-..230V | F | MSP | Allen Bradley | 140M-C2E-B25 | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.5 | 0.75 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB190E-KN...-CB25.-..460V | F | MSP | Allen Bradley | 140M-C2E-B25 | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB190E-KN...-CB25.-..575V | F | MSP | Allen Bradley | 140M-C2E-B25 | 575 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 30 | 2.5 | 2 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB190E-KN...-CB40.-..200V | F | MSP | Allen Bradley | 140M-C2E-B40 | 200 | 3 | 65 | 4 | 1 | 200 | 3 | 65 | 4 | 1 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB190E-KN...-CB40.-..230V | F | MSP | Allen Bradley | 140M-C2E-B40 | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 4 | 1 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB190E-KN...-CB40.-..460V | F | MSP | Allen Bradley | 140M-C2E-B40 | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB190E-KN...-CB40.-..575V | F | MSP | Allen Bradley | 140M-C2E-B40 | 575 | 3 | 25 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB190E-KN...-CB63.-..200V | F | MSP | Allen Bradley | 140M-C2E-B63 | 200 | 3 | 65 | 6.3 | 1.5 | 200 | 3 | 65 | 6.3 | 1.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB190E-KN...-CB63.-..230V | F | MSP | Allen Bradley | 140M-C2E-B63 | 230 | 3 | 65 | 6.3 | 2 | 230 | 3 | 65 | 6.3 | 2 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB190E-KN...-CB63.-..460V | F | MSP | Allen Bradley | 140M-C2E-B63 | 460 | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 6.3 | 5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB190E-KN...-CC10.-..200V | F | MSP | Allen Bradley | 140M-C2E-C10 | 200 | 3 | 65 | 10 | 3 | 200 | 3 | 65 | 7.8 | 2 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB190E-KN...-CC10.-.230V | F | MSP | Allen Bradley | 140M-C2E-C10 | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 6.8 | 2 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB190E-KN...-CC10.-.460V | F | MSP | Allen Bradley | 140M-C2E-C10 | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB190E-KP...-CB25.-..200V | F | MSP | Allen Bradley | 140M-C2E-B25 | 200 | 3 | 65 | 2.5 | 0.5 | 200 | 3 | 65 | 2.5 | 0.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB190E-KP...-CB25.-..230V | F | MSP | Allen Bradley | 140M-C2E-B25 | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.5 | 0.75 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB190E-KP...-CB25.-..460V | F | MSP | Allen Bradley | 140M-C2E-B25 | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB190E-KP...-CB25.-..575V | F | MSP | Allen Bradley | 140M-C2E-B25 | 575 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 30 | 2.5 | 2 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K12 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB190E-KP...-CB40.-..200V | F | MSP | Allen Bradley | 140M-C2E-B40 | 200 | 3 | 65 | 4 | 1 | 200 | 3 | 65 | 4 | 1 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB190E-KP...-CB40.-..230V | F | MSP | Allen Bradley | 140M-C2E-B40 | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 4 | 1 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB190E-KP...-CB40.-..460V | F | MSP | Allen Bradley | 140M-C2E-B40 | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB190E-KP...-CB40.-..575V | F | MSP | Allen Bradley | 140M-C2E-B40 | 575 | 3 | 25 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K12 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB190E-KP...-CB63.-..200V | F | MSP | Allen Bradley | 140M-C2E-B63 | 200 | 3 | 65 | 6.3 | 1.5 | 200 | 3 | 65 | 6.3 | 1.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB190E-KP...-CB63.-..230V | F | MSP | Allen Bradley | 140M-C2E-B63 | 230 | 3 | 65 | 6.3 | 2 | 230 | 3 | 65 | 6.3 | 2 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB190E-KP...-CB63.-..460V | F | MSP | Allen Bradley | 140M-C2E-B63 | 460 | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 6.3 | 5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB190E-KP...-CC10.-..200V | F | MSP | Allen Bradley | 140M-C2E-C10 | 200 | 3 | 65 | 10 | 3 | 200 | 3 | 65 | 10 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB190E-KP...-CC10.-..230V | F | MSP | Allen Bradley | 140M-C2E-C10 | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 9.6 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB190E-KP...-CC10.-..460V | F | MSP | Allen Bradley | 140M-C2E-C10 | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 10 | 7.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB190E-KP...-CC16.-..200V | F | MSP | Allen Bradley | 140M-C2E-C16 | 200 | 3 | 30 | 16 | 5 | 200 | 3 | 30 | 11 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB190E-KP...-CC16.-..460V | F | MSP | Allen Bradley | 140M-C2E-C16 | 460 | 3 | 30 | 16 | 10 | 480Y/277 | 3 | 30 | 11 | 7.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB191E-KM...-CA16.-..200V | F | MSP | Allen Bradley | 140M-C2E-A16 | 200 | 3 | 65 | 0.16 | - | 200 | 3 | 65 | 0.16 FLA / 0.96 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB191E-KM...-CA16.-..230V | F | MSP | Allen Bradley | 140M-C2E-A16 | 230 | 3 | 65 | 0.16 | - | 230 | 3 | 65 | 0.16 FLA / 0.96 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 230 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB191E-KM...-CA16.-..460V | F | MSP | Allen Bradley | 140M-C2E-A16 | 460 | 3 | 65 | 0.16 | - | 480Y/277 | 3 | 65 | 0.16 FLA / 0.96 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 460 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB191E-KM...-CA16.-..575V | F | MSP | Allen Bradley | 140M-C2E-A16 | 575 | 3 | 47 | 0.16 | - | 600Y/347 | 3 | 47 | 0.16 FLA / 0.96 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 575 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB191E-KM...-CA25.-..200V | F | MSP | Allen Bradley | 140M-C2E-A25 | 200 | 3 | 65 | 0.25 | - | 200 | 3 | 65 | 0.25 FLA / 1.5 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB191E-KM...-CA25.-..230V | F | MSP | Allen Bradley | 140M-C2E-A25 | 230 | 3 | 65 | 0.25 | - | 230 | 3 | 65 | 0.25 FLA / 1.5 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 230 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB191E-KM...-CA25.-..460V | F | MSP | Allen Bradley | 140M-C2E-A25 | 460 | 3 | 65 | 0.25 | - | 480Y/277 | 3 | 65 | 0.25 FLA / 1.5 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 460 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB191E-KM...-CA25.-..575V | F | MSP | Allen Bradley | 140M-C2E-A25 | 575 | 3 | 47 | 0.25 | - | 600Y/347 | 3 | 47 | 0.25 FLA / 1.5 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 575 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB191E-KM...-CA40.-..200V | F | MSP | Allen Bradley | 140M-C2E-A40 | 200 | 3 | 65 | 0.4 | - | 200 | 3 | 65 | 0.4 FLA / 2.4 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB191E-KM...-CA40.-..230V | F | MSP | Allen Bradley | 140M-C2E-A40 | 230 | 3 | 65 | 0.4 | - | 230 | 3 | 65 | 0.4 FLA / 2.4 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 230 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB191E-KM...-CA40.-..460V | F | MSP | Allen Bradley | 140M-C2E-A40 | 460 | 3 | 65 | 0.4 | - | 480Y/277 | 3 | 65 | 0.4 FLA / 2.4 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 460 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB191E-KM...-CA40.-..575V | F | MSP | Allen Bradley | 140M-C2E-A40 | 575 | 3 | 47 | 0.4 | - | 600Y/347 | 3 | 47 | 0.4 FLA / 2.4 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 575 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB191E-KM...-CA63.-..200V | F | MSP | Allen Bradley | 140M-C2E-A63 | 200 | 3 | 65 | 0.63 | - | 200 | 3 | 65 | 0.63 FLA / 3.78 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB191E-KM...-CA63.-..230V | F | MSP | Allen Bradley | 140M-C2E-A63 | 230 | 3 | 65 | 0.63 | - | 230 | 3 | 65 | 0.63 FLA / 3.78 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 230 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB191E-KM...-CA63.-..460V | F | MSP | Allen Bradley | 140M-C2E-A63 | 460 | 3 | 65 | 0.63 | - | 480Y/277 | 3 | 65 | 0.63 FLA / 3.78 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 460 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB191E-KM...-CA63.-..575V | F | MSP | Allen Bradley | 140M-C2E-A63 | 575 | 3 | 47 | 0.63 | - | 600Y/347 | 3 | 47 | 0.63 FLA / 3.78 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 575 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB191E-KM...-CB10.-..200V | F | MSP | Allen Bradley | 140M-C2E-B10 | 200 | 3 | 65 | 1 | - | 200 | 3 | 65 | 1.0 FLA / 6.0 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB191E-KM...-CB10.-..230V | F | MSP | Allen Bradley | 140M-C2E-B10 | 230 | 3 | 65 | 1 | - | 230 | 3 | 65 | 1.0 FLA / 6.0 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 230 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB191E-KM...-CB10.-..460V | F | MSP | Allen Bradley | 140M-C2E-B10 | 460 | 3 | 65 | 1 | 0.5 | 480Y/277 | 3 | 65 | 1 | 0.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 460 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB191E-KM...-CB10.-..575V | F | MSP | Allen Bradley | 140M-C2E-B10 | 575 | 3 | 47 | 1 | 0.75 | 600Y/347 | 3 | 47 | 1 | 0.75 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 575 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB191E-KM...-CB16.-..200V | F | MSP | Allen Bradley | 140M-C2E-B16 | 200 | 3 | 65 | 1.6 | - | 200 | 3 | 65 | 1.6 FLA / 9.6 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB191E-KM...-CB16.-..230V | F | MSP | Allen Bradley | 140M-C2E-B16 | 230 | 3 | 65 | 1.6 | - | 230 | 3 | 65 | 1.6 FLA / 9.6 LRA | - | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 230 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB191E-KM...-CB16.-..460V | F | MSP | Allen Bradley | 140M-C2E-B16 | 460 | 3 | 65 | 1.6 | 1 | 480Y/277 | 3 | 65 | 1.6 | 1 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 460 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB191E-KM...-CB16.-..575V | F | MSP | Allen Bradley | 140M-C2E-B16 | 575 | 3 | 47 | 1.6 | 1 | 600Y/347 | 3 | 47 | 1.6 | 1 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 575 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB191E-KM...-CB25.-..200V | F | MSP | Allen Bradley | 140M-C2E-B25 | 200 | 3 | 65 | 2.5 | 0.5 | 200 | 3 | 65 | 2.5 | 0.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB191E-KM...-CB25.-..230V | F | MSP | Allen Bradley | 140M-C2E-B25 | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.5 | 0.75 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 230 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB191E-KM...-CB25.-..460V | F | MSP | Allen Bradley | 140M-C2E-B25 | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 460 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB191E-KM...-CB25.-..575V | F | MSP | Allen Bradley | 140M-C2E-B25 | 575 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 30 | 2.5 | 2 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 575 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB191E-KM...-CB40.-..200V | F | MSP | Allen Bradley | 140M-C2E-B40 | 200 | 3 | 65 | 4 | 1 | 200 | 3 | 65 | 4 | 1 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB191E-KM...-CB40.-..230V | F | MSP | Allen Bradley | 140M-C2E-B40 | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 4 | 1 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 230 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB191E-KM...-CB40.-..460V | F | MSP | Allen Bradley | 140M-C2E-B40 | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 460 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB191E-KM...-CB40.-..575V | F | MSP | Allen Bradley | 140M-C2E-B40 | 575 | 3 | 25 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K05 | 575 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB191E-KM...-CB63.-..200V | F | MSP | Allen Bradley | 140M-C2E-B63 | 200 | 3 | 65 | 6.3 | 1.5 | 200 | 3 | 65 | 6.3 | 1.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB191E-KM...-CB63.-..230V | F | MSP | Allen Bradley | 140M-C2E-B63 | 230 | 3 | 65 | 6.3 | 2 | 230 | 3 | 65 | 6 | 1.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 230 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB191E-KM...-CB63.-..460V | F | MSP | Allen Bradley | 140M-C2E-B63 | 460 | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 4.8 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K05 | 460 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB191E-KN...-CB25.-..200V | F | MSP | Allen Bradley | 140M-C2E-B25 | 200 | 3 | 65 | 2.5 | 0.5 | 200 | 3 | 65 | 2.5 | 0.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB191E-KN...-CB25.-..230V | F | MSP | Allen Bradley | 140M-C2E-B25 | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.5 | 0.75 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB191E-KN...-CB25.-..460V | F | MSP | Allen Bradley | 140M-C2E-B25 | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB191E-KN...-CB25.-..575V | F | MSP | Allen Bradley | 140M-C2E-B25 | 575 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 30 | 2.5 | 2 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB191E-KN...-CB40.-..200V | F | MSP | Allen Bradley | 140M-C2E-B40 | 200 | 3 | 65 | 4 | 1 | 200 | 3 | 65 | 4 | 1 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB191E-KN...-CB40.-..230V | F | MSP | Allen Bradley | 140M-C2E-B40 | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 4 | 1 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB191E-KN...-CB40.-..460V | F | MSP | Allen Bradley | 140M-C2E-B40 | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB191E-KN...-CB40.-..575V | F | MSP | Allen Bradley | 140M-C2E-B40 | 575 | 3 | 25 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB191E-KN...-CB63.-..200V | F | MSP | Allen Bradley | 140M-C2E-B63 | 200 | 3 | 65 | 6.3 | 1.5 | 200 | 3 | 65 | 6.3 | 1.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB191E-KN...-CB63.-..230V | F | MSP | Allen Bradley | 140M-C2E-B63 | 230 | 3 | 65 | 6.3 | 2 | 230 | 3 | 65 | 6.3 | 2 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB191E-KN...-CB63.-..460V | F | MSP | Allen Bradley | 140M-C2E-B63 | 460 | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 6.3 | 5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB191E-KN...-CC10.-..200V | F | MSP | Allen Bradley | 140M-C2E-C10 | 200 | 3 | 65 | 10 | 3 | 200 | 3 | 65 | 7.8 | 2 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB191E-KN...-CC10.-..230V | F | MSP | Allen Bradley | 140M-C2E-C10 | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 6.8 | 2 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB191E-KN...-CC10.-..460V | F | MSP | Allen Bradley | 140M-C2E-C10 | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB191E-KP...-CB25.-..200V | F | MSP | Allen Bradley | 140M-C2E-B25 | 200 | 3 | 65 | 2.5 | 0.5 | 200 | 3 | 65 | 2.5 | 0.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K09 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB191E-KP...-CB25.-..230V | F | MSP | Allen Bradley | 140M-C2E-B25 | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.5 | 0.75 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K09 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB191E-KP...-CB25.-..460V | F | MSP | Allen Bradley | 140M-C2E-B25 | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K09 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB191E-KP...-CB25.-..575V | F | MSP | Allen Bradley | 140M-C2E-B25 | 575 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 30 | 2.5 | 2 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K09 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB191E-KP...-CB40.-..200V | F | MSP | Allen Bradley | 140M-C2E-B25 | 200 | 3 | 65 | 4 | 1 | 200 | 3 | 65 | 4 | 1 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB191E-KP...-CB40.-..230V | F | MSP | Allen Bradley | 140M-C2E-B40 | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 4 | 1 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB191E-KP...-CB40.-..460V | F | MSP | Allen Bradley | 140M-C2E-B40 | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB191E-KP...-CB40.-..575V | F | MSP | Allen Bradley | 140M-C2E-B40 | 575 | 3 | 25 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K12 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 575 | 3 | - | - | -
AB191E-KP...-CB63.-..200V | F | MSP | Allen Bradley | 140M-C2E-B63 | 200 | 3 | 65 | 6.3 | 1.5 | 200 | 3 | 65 | 6.3 | 1.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB191E-KP...-CB63.-..230V | F | MSP | Allen Bradley | 140M-C2E-B63 | 230 | 3 | 65 | 6.3 | 2 | 230 | 3 | 65 | 6.3 | 2 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB191E-KP...-CB63.-..460V | F | MSP | Allen Bradley | 140M-C2E-B63 | 460 | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 6.3 | 5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB191E-KP...-CC10.-..200V | F | MSP | Allen Bradley | 140M-C2E-C10 | 200 | 3 | 65 | 10 | 3 | 200 | 3 | 65 | 10 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB191E-KP...-CC10.-..230V | F | MSP | Allen Bradley | 140M-C2E-C10 | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 9.6 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 230 | 3 | - | - | -
AB191E-KP...-CC10.-..460V | F | MSP | Allen Bradley | 140M-C2E-C10 | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 10 | 7.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
AB191E-KP...-CC16.-..200V | F | MSP | Allen Bradley | 140M-C2E-C16 | 200 | 3 | 30 | 16 | 5 | 200 | 3 | 30 | 11 | 3 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 104-K12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 200 | 3 | - | - | -
AB191E-KP...-CC16.-..460V | F | MSP | Allen Bradley | 140M-C2E-C16 | 460 | 3 | 30 | 16 | 10 | 480Y/277 | 3 | 30 | 11 | 7.5 | 773 | 1, 5, 6 | E205542 V2 S4
|  | MC | Allen Bradley | 100-K12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Allen Bradley | 140M-C-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Allen Bradley | 140M-C-PEK12 | 460 | 3 | - | - | -
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = In lieu of the following R/C (NKCR2) Connection Modules the following Jumper wires may be used for the following Combination Motor Controllers.
|  | Connection Modules |  | Combination Motor Controller |  |  | Jumper Wire
|  | 140M-C-PEK12 |  | 190E and 191E-K |  |  | 105°C, 600V, 14 AWG

## Const. C w MCCB (113D) Series B
[16 empty] | Issued: | 2014-07-07
[16 empty] | Last Revised: | 2020-12-10
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number [1] | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP rating | Enclosure Volume, CU inches
AB113D-C30...-E1FC30-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC30-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C30 | 200 | 3 | 35 | 30 | - | 200 | 3 | 35 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC30-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C30 | 200 | 3 | 25 | 30 | - | 200 | 3 | 25 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC30-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC30-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C30 | 230 | 3 | 35 | 30 | - | 230 | 3 | 35 | 22 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC30-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C30 | 230 | 3 | 25 | 30 | - | 230 | 3 | 25 | 22 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC30-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC30-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C30 | 480 | 3 | 35 | 30 | - | 480 | 3 | 35 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC30-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C30 | 480 | 3 | 25 | 30 | - | 480 | 3 | 25 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC30-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-C30 | 600 | 3 | 25 | 30 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC30-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-C30 | 600 | 3 | 18 | 30 | - | 600 | 3 | 18 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC30-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-C30 | 600 | 3 | 14 | 30 | - | 600 | 3 | 14 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC50-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC50-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 200 | 3 | 35 | 50 | - | 200 | 3 | 35 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC50-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 200 | 3 | 25 | 50 | - | 200 | 3 | 25 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC50-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC50-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 230 | 3 | 35 | 50 | - | 230 | 3 | 35 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC50-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 230 | 3 | 25 | 50 | - | 230 | 3 | 25 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC50-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC50-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 480 | 3 | 35 | 50 | - | 480 | 3 | 35 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC50-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 480 | 3 | 25 | 50 | - | 480 | 3 | 25 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC50-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 600 | 3 | 25 | 50 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC50-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 600 | 3 | 18 | 50 | - | 600 | 3 | 18 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC50-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 600 | 3 | 14 | 50 | - | 600 | 3 | 14 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C37...-E1FC50-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C37...-E1FC50-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 200 | 3 | 35 | 50 | - | 200 | 3 | 35 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C37...-E1FC50-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 200 | 3 | 25 | 50 | - | 200 | 3 | 25 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C37...-E1FC50-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C37...-E1FC50-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 230 | 3 | 35 | 50 | - | 230 | 3 | 35 | 28 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C37...-E1FC50-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 230 | 3 | 25 | 50 | - | 230 | 3 | 25 | 28 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C37...-E1FC50-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C37...-E1FC50-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 480 | 3 | 35 | 50 | - | 480 | 3 | 35 | 34 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C37...-E1FC50-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 480 | 3 | 25 | 50 | - | 480 | 3 | 25 | 34 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C37...-E1FC50-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 600 | 3 | 25 | 50 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C37...-E1FC50-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 600 | 3 | 18 | 50 | - | 600 | 3 | 18 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C37...-E1FC50-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 600 | 3 | 14 | 50 | - | 600 | 3 | 14 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C43...-E1FC80-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C43...-E1FC80-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 200 | 3 | 35 | 80 | - | 200 | 3 | 35 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C43...-E1FC80-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 200 | 3 | 25 | 80 | - | 200 | 3 | 25 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C43...-E1FC80-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C43...-E1FC80-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 230 | 3 | 35 | 80 | - | 230 | 3 | 35 | 42 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C43...-E1FC80-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 230 | 3 | 25 | 80 | - | 230 | 3 | 25 | 42 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C43...-E1FC80-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C43...-E1FC80-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 480 | 3 | 35 | 80 | - | 480 | 3 | 35 | 40 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C43...-E1FC80-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 480 | 3 | 25 | 80 | - | 480 | 3 | 25 | 40 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C43...-E1FC80-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C43...-E1FC80-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 600 | 3 | 18 | 80 | - | 600 | 3 | 18 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C43...-E1FC80-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 600 | 3 | 14 | 80 | - | 600 | 3 | 14 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C55...-E1GC80-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 5 | 18-90 | -
AB113D-C55...-E1GC80-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 200 | 3 | 35 | 80 | - | 200 | 3 | 35 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 5 | 18-90 | -
AB113D-C55...-E1GC80-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 200 | 3 | 25 | 80 | - | 200 | 3 | 25 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 5 | 18-90 | -
AB113D-C55...-E1GC80-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 5 | 18-90 | -
AB113D-C55...-E1GC80-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 230 | 3 | 35 | 80 | - | 230 | 3 | 35 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 5 | 18-90 | -
AB113D-C55...-E1GC80-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 230 | 3 | 25 | 80 | - | 230 | 3 | 25 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 5 | 18-90 | -
AB113D-C55...-E1GC80-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 5 | 18-90 | -
AB113D-C55...-E1GC80-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 480 | 3 | 35 | 80 | - | 480 | 3 | 35 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 5 | 18-90 | -
AB113D-C55...-E1GC80-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 480 | 3 | 25 | 80 | - | 480 | 3 | 25 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 5 | 18-90 | -
AB113D-C55...-E1GC80-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 5 | 18-90 | -
AB113D-C55...-E1GC80-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 600 | 3 | 18 | 80 | - | 600 | 3 | 18 | 41 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 5 | 18-90 | -
AB113D-C55...-E1GC80-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 600 | 3 | 14 | 80 | - | 600 | 3 | 14 | 41 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 5 | 18-90 | -
AB113D-C60...-E1GD12-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C60...-E1GD12-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C60...-E1GD12-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C60...-E1GD12-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C60...-E1GD12-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C60...-E1GD12-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C60...-E1GD12-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C60...-E1GD12-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C60...-E1GD12-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C60...-E1GD12-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C60...-E1GD12-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 600 | 3 | 18 | 125 | - | 600 | 3 | 18 | 52 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C60...-E1GD12-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 600 | 3 | 14 | 125 | - | 600 | 3 | 14 | 52 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C72...-E1GD12-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C72...-E1GD12-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 62.1 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C72...-E1GD12-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 62.1 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C72...-E1GD12-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 68 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C72...-E1GD12-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 68 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C72...-E1GD12-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 68 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C72...-E1GD12-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C72...-E1GD12-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 65 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C72...-E1GD12-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 65 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C72...-E1GD12-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C72...-E1GD12-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 600 | 3 | 18 | 125 | - | 600 | 3 | 18 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C72...-E1GD12-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 600 | 3 | 14 | 125 | - | 600 | 3 | 14 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C85...-E1GD12-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C85...-E1GD12-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 78.2 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C85...-E1GD12-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 78.2 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C85...-E1GD12-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C85...-E1GD12-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C85...-E1GD12-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C85...-E1GD12-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C85...-E1GD12-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 77 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C85...-E1GD12-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 77 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C85...-E1GD12-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C85...-E1GD12-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 600 | 3 | 18 | 125 | - | 600 | 3 | 18 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C85...-E1GD12-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 600 | 3 | 14 | 125 | - | 600 | 3 | 14 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C97...-E1VD12-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EEVE | 200 | 3 | 10 | 60-120 | -
AB113D-C97...-E1VD12-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 92 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EEVE | 200 | 3 | 10 | 60-120 | -
AB113D-C97...-E1VD12-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 92 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EEVE | 200 | 3 | 10 | 60-120 | -
AB113D-C97...-E1VD12-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EEVE | 230 | 3 | 10 | 60-120 | -
AB113D-C97...-E1VD12-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EEVE | 230 | 3 | 10 | 60-120 | -
AB113D-C97...-E1VD12-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EEVE | 230 | 3 | 10 | 60-120 | -
AB113D-C97...-E1VD12-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EEVE | 480 | 3 | 10 | 60-120 | -
AB113D-C97...-E1VD12-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 96 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EEVE | 480 | 3 | 10 | 60-120 | -
AB113D-C97...-E1VD12-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 96 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EEVE | 480 | 3 | 10 | 60-120 | -
AB113D-C97...-E1VD12-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-EEVE | 600 | 3 | 10 | 60-120 | -
AB113D-C97...-E1VD12-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 600 | 3 | 18 | 125 | - | 600 | 3 | 18 | 77 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-EEVE | 600 | 3 | 10 | 60-120 | -
AB113D-C97...-E1VD12-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 600 | 3 | 14 | 125 | - | 600 | 3 | 14 | 77 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-EEVE | 600 | 3 | 10 | 60-120 | -
AB113D-C30G...-E1FC30-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC30-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C30 | 200 | 3 | 35 | 30 | - | 200 | 3 | 35 | 17.5 | 5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC30-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C30 | 200 | 3 | 25 | 30 | - | 200 | 3 | 25 | 17.5 | 5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC30-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC30-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C30 | 230 | 3 | 35 | 30 | - | 230 | 3 | 35 | 22 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC30-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C30 | 230 | 3 | 25 | 30 | - | 230 | 3 | 25 | 22 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC30-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC30-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C30 | 480 | 3 | 35 | 30 | - | 480 | 3 | 35 | 21 FLA | 15 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC30-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C30 | 480 | 3 | 25 | 30 | - | 480 | 3 | 25 | 21 FLA | 15 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC30-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-C30 | 600Y/347 | 3 | 25 | 30 | - | 600Y/347 | 3 | 25 | 22 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC30-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-C30 | 600Y/347 | 3 | 14 | 30 | - | 600Y/347 | 3 | 14 | 22 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC30-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-C30 | 600Y/347 | 3 | 10 | 30 | - | 600Y/347 | 3 | 10 | 22 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC50-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC50-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 200 | 3 | 35 | 50 | - | 200 | 3 | 35 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC50-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 200 | 3 | 25 | 50 | - | 200 | 3 | 25 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC50-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC50-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 35 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC50-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 230 | 3 | 25 | 50 | - | 230 | 3 | 25 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC50-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC50-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 480 | 3 | 35 | 50 | - | 480 | 3 | 35 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC50-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 480 | 3 | 25 | 50 | - | 480 | 3 | 25 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC50-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 600Y/347 | 3 | 25 | 50 | - | 600Y/347 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC50-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 600Y/347 | 3 | 14 | 50 | - | 600Y/347 | 3 | 14 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C30G...-E1FC50-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 600Y/347 | 3 | 10 | 50 | - | 600Y/347 | 3 | 10 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C37G...-E1FC50-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C37G...-E1FC50-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 200 | 3 | 35 | 50 | - | 200 | 3 | 35 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C37G...-E1FC50-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 200 | 3 | 25 | 50 | - | 200 | 3 | 25 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C37G...-E1FC50-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C37G...-E1FC50-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 230 | 3 | 35 | 50 | - | 230 | 3 | 35 | 28 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C37G...-E1FC50-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 230 | 3 | 25 | 50 | - | 230 | 3 | 25 | 28 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C37G...-E1FC50-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C37G...-E1FC50-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 480 | 3 | 35 | 50 | - | 480 | 3 | 35 | 34 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C37G...-E1FC50-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 480 | 3 | 25 | 50 | - | 480 | 3 | 25 | 34 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C37G...-E1FC50-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 600Y/347 | 3 | 25 | 50 | - | 600Y/347 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C37G...-E1FC50-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 600Y/347 | 3 | 14 | 50 | - | 600Y/347 | 3 | 14 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C37G...-E1FC50-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 600Y/347 | 3 | 10 | 50 | - | 600Y/347 | 3 | 10 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C43G...-E1FC80-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C43G...-E1FC80-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 200 | 3 | 35 | 80 | - | 200 | 3 | 35 | 32.2 FLA | 10 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C43G...-E1FC80-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 200 | 3 | 25 | 80 | - | 200 | 3 | 25 | 32.2 FLA | 10 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C43G...-E1FC80-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 28 FLA | 10 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C43G...-E1FC80-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 230 | 3 | 35 | 80 | - | 230 | 3 | 35 | 28 FLA | 10 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C43G...-E1FC80-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 230 | 3 | 25 | 80 | - | 230 | 3 | 25 | 28 FLA | 10 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C43G...-E1FC80-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C43G...-E1FC80-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 480 | 3 | 35 | 80 | - | 480 | 3 | 35 | 40 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C43G...-E1FC80-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 480 | 3 | 25 | 80 | - | 480 | 3 | 25 | 40 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C43G...-E1FC50-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 600Y/347 | 3 | 25 | 50 | - | 600Y/347 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C43G...-E1FC50-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 600Y/347 | 3 | 14 | 50 | - | 600Y/347 | 3 | 14 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C43G...-E1FC50-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 600Y/347 | 3 | 10 | 50 | - | 600Y/347 | 3 | 10 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C55G...-E1GC80-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 5 | 18-90 | -
AB113D-C55G...-E1GC80-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 200 | 3 | 35 | 80 | - | 200 | 3 | 35 | 48.3 FLA | 15 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 5 | 18-90 | -
AB113D-C55G...-E1GC80-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 200 | 3 | 25 | 80 | - | 200 | 3 | 25 | 48.3 FLA | 15 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 5 | 18-90 | -
AB113D-C55G...-E1GC80-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 5 | 18-90 | -
AB113D-C55G...-E1GC80-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 230 | 3 | 35 | 80 | - | 230 | 3 | 35 | 54 FLA | 20 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 5 | 18-90 | -
AB113D-C55G...-E1GC80-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 230 | 3 | 25 | 80 | - | 230 | 3 | 25 | 54 FLA | 20 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 5 | 18-90 | -
AB113D-C55G...-E1GC80-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 5 | 18-90 | -
AB113D-C55G...-E1GC80-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 480 | 3 | 35 | 80 | - | 480 | 3 | 35 | 52 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 5 | 18-90 | -
AB113D-C55G...-E1GC80-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 480 | 3 | 25 | 80 | - | 480 | 3 | 25 | 52 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 5 | 18-90 | -
AB113D-C60G...-E1GD12-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C60G...-E1GD12-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C60G...-E1GD12-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C60G...-E1GD12-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C60G...-E1GD12-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C60G...-E1GD12-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C60G...-E1GD12-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C60G...-E1GD12-..460V_140G-G3_35kA |  | CB | Allen-Bradley | 140G-G3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C60G...-E1GD12-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 25 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C60G...-E1GD12-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 600Y/347 | 3 | 25 | 125 | - | 600Y/347 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C60G...-E1GD12-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 600Y/347 | 3 | 14 | 125 | - | 600Y/347 | 3 | 14 | 52 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C60G...-E1GD12-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 600Y/347 | 3 | 25 | 125 | - | 600Y/347 | 3 | 10 | 52 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C72G...-E1GD12-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C72G...-E1GD12-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 62.1 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C72G...-E1GD12-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 62.1 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C72G...-E1GD12-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 68 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C72G...-E1GD12-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 35 | 68 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 35 | 68 | 25
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C72G...-E1GD12-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 68 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C72G...-E1GD12-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C72G...-E1GD12-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 65 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C72G...-E1GD12-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 65 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C72G...-E1GD12-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 600Y/347 | 3 | 25 | 125 | - | 600Y/347 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C72G...-E1GD12-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 600Y/347 | 3 | 14 | 125 | - | 600Y/347 | 3 | 14 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C72G...-E1GD12-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 600Y/347 | 3 | 10 | 125 | - | 600Y/347 | 3 | 10 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C85G...-E1GD12-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C85G...-E1GD12-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 78.2 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C85G...-E1GD12-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 78.2 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C85G...-E1GD12-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C85G...-E1GD12-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C85G...-E1GD12-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C85G...-E1GD12-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C85G...-E1GD12-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 77 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C85G...-E1GD12-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 77 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C85G...-E1GD12-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 600Y/347 | 3 | 25 | 125 | - | 600Y/347 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C85G...-E1GD12-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 600Y/347 | 3 | 14 | 125 | - | 600Y/347 | 3 | 14 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C85G...-E1GD12-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 600Y/347 | 3 | 10 | 125 | - | 600Y/347 | 3 | 10 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C97G...-E1VD12-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EEVE | 200 | 3 | 10 | 60-120 | -
AB113D-C97G...-E1VD12-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 92 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EEVE | 200 | 3 | 10 | 60-120 | -
AB113D-C97G...-E1VD12-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 92 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EEVE | 200 | 3 | 10 | 60-120 | -
AB113D-C97G...-E1VD12-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EEVE | 230 | 3 | 10 | 60-120 | -
AB113D-C97G...-E1VD12-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EEVE | 230 | 3 | 10 | 60-120 | -
AB113D-C97G...-E1VD12-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EEVE | 230 | 3 | 10 | 60-120 | -
AB113D-C97G...-E1VD12-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EEVE | 480 | 3 | 10 | 60-120 | -
AB113D-C97G...-E1VD12-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 96 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EEVE | 480 | 3 | 10 | 60-120 | -
AB113D-C97G...-E1VD12-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 96 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EEVE | 480 | 3 | 10 | 60-120 | -
AB113D-C97G...-E1VD12-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 600Y/347 | 3 | 25 | 125 | - | 600Y/347 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-EEVE | 600 | 3 | 10 | 60-120 | -
AB113D-C97G...-E1VD12-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 600Y/347 | 3 | 14 | 125 | - | 600Y/347 | 3 | 14 | 77 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-EEVE | 600 | 3 | 10 | 60-120 | -
AB113D-C97G...-E1VD12-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 600Y/347 | 3 | 10 | 125 | - | 600Y/347 | 3 | 10 | 77 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-EEVE | 600 | 3 | 10 | 60-120 | -
AB113D-D115...-E1HD25-..200V_140G-J6_65kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 92 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EEHF | 200 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HD25-..200V_140G-J3_35kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 200 | 3 | 35 | 250 | - | 200 | 3 | 35 | 92 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EEHF | 200 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HD25-..200V_140G-J2_25kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 200 | 3 | 25 | 250 | - | 200 | 3 | 25 | 92 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EEHF | 200 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HD25-..230V_140G-J6_65kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 104 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-EEHF | 230 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HD25-..230V_140G-J3_35kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 230 | 3 | 35 | 250 | - | 230 | 3 | 35 | 104 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-EEHF | 230 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HD25-..230V_140G-J2_25kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 230 | 3 | 25 | 250 | - | 230 | 3 | 25 | 104 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-EEHF | 230 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HD25-..460V_140G-J6_65kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 96 FLA | 75 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EEHF | 480 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HD25-..460V_140G-J3_35kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 480 | 3 | 35 | 250 | - | 480 | 3 | 35 | 96 FLA | 75 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EEHF | 480 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HD25-..460V_140G-J2_25kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 480 | 3 | 25 | 250 | - | 480 | 3 | 25 | 96 FLA | 75 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EEHF | 480 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HD25-..575V_140G-J6_25kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 99 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-EEHF | 600 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HD25-..575V_140G-J3_18kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 600 | 3 | 18 | 250 | - | 600 | 3 | 18 | 99 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-EEHF | 600 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HD25-..575V_140G-J2_14kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 600 | 3 | 14 | 250 | - | 600 | 3 | 14 | 99 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-EEHF | 600 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD25-..200V_140G-J6_65kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 120 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-EEHF | 200 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD25-..200V_140G-J3_35kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 200 | 3 | 35 | 250 | - | 200 | 3 | 35 | 120 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-EEHF | 200 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD25-..200V_140G-J2_25kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 200 | 3 | 25 | 250 | - | 200 | 3 | 25 | 120 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-EEHF | 200 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD25-..230V_140G-J6_65kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 130 FLA | 50 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-EEHF | 230 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD25-..230V_140G-J3_35kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 230 | 3 | 35 | 250 | - | 230 | 3 | 35 | 130 FLA | 50 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-EEHF | 230 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD25-..230V_140G-J2_25kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 230 | 3 | 25 | 250 | - | 230 | 3 | 25 | 130 FLA | 50 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-EEHF | 230 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD25-..460V_140G-J6_65kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 124 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-EEHF | 480 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD25-..460V_140G-J3_35kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 480 | 3 | 35 | 250 | - | 480 | 3 | 35 | 124 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-EEHF | 480 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD25-..460V_140G-J2_25kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 480 | 3 | 25 | 250 | - | 480 | 3 | 25 | 124 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-EEHF | 480 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD25-..575V_140G-J6_25kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 125 FLA | 125 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-EEHF | 600 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD25-..575V_140G-J3_18kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 600 | 3 | 18 | 250 | - | 600 | 3 | 18 | 125 FLA | 125 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-EEHF | 600 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD25-..575V_140G-J2_14kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 600 | 3 | 14 | 250 | - | 600 | 3 | 14 | 125 FLA | 125 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-EEHF | 600 | 3 | 10 | 30-150 | -
AB113D-D180...-E1JD25-..200V_140G-J6_65kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 150 FLA | 50 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 200 | 3 | 10 | 150 | 50
|  | OLR | Allen-Bradley | 193-EEJF | 200 | 3 | 10 | 40-200 | -
AB113D-D180...-E1JD25-..200V_140G-J3_35kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 200 | 3 | 35 | 250 | - | 200 | 3 | 35 | 150 FLA | 50 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 200 | 3 | 10 | 150 | 50
|  | OLR | Allen-Bradley | 193-EEJF | 200 | 3 | 10 | 40-200 | -
AB113D-D180...-E1JD25-..200V_140G-J2_25kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 200 | 3 | 25 | 250 | - | 200 | 3 | 25 | 150 FLA | 50 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 200 | 3 | 10 | 150 | 50
|  | OLR | Allen-Bradley | 193-EEJF | 200 | 3 | 10 | 40-200 | -
AB113D-D180...-E1JD25-..230V_140G-J6_65kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 154 FLA | 60 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 230 | 3 | 10 | 154 | 60
|  | OLR | Allen-Bradley | 193-EEJF | 230 | 3 | 10 | 40-200 | -
AB113D-D180...-E1JD25-..230V_140G-J3_35kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 230 | 3 | 35 | 250 | - | 230 | 3 | 35 | 154 FLA | 60 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 230 | 3 | 10 | 154 | 60
|  | OLR | Allen-Bradley | 193-EEJF | 230 | 3 | 10 | 40-200 | -
AB113D-D180...-E1JD25-..230V_140G-J2_25kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 230 | 3 | 25 | 250 | - | 230 | 3 | 25 | 154 FLA | 60 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 230 | 3 | 10 | 154 | 60
|  | OLR | Allen-Bradley | 193-EEJF | 230 | 3 | 10 | 40-200 | -
AB113D-D180...-E1JD25-..460V_140G-J6_65kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 180 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 480 | 3 | 10 | 180 | 150
|  | OLR | Allen-Bradley | 193-EEJF | 480 | 3 | 10 | 40-200 | -
AB113D-D180...-E1JD25-..460V_140G-J3_35kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 480 | 3 | 35 | 250 | - | 480 | 3 | 35 | 180 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 480 | 3 | 10 | 180 | 150
|  | OLR | Allen-Bradley | 193-EEJF | 480 | 3 | 10 | 40-200 | -
AB113D-D180...-E1JD25-..460V_140G-J2_25kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 480 | 3 | 25 | 250 | - | 480 | 3 | 25 | 180 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 480 | 3 | 10 | 180 | 150
|  | OLR | Allen-Bradley | 193-EEJF | 480 | 3 | 10 | 40-200 | -
AB113D-D180...-E1JD25-..575V_140G-J6_25kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 144 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 600 | 3 | 10 | 144 | 150
|  | OLR | Allen-Bradley | 193-EEJF | 600 | 3 | 10 | 40-200 | -
AB113D-D180...-E1JD25-..575V_140G-J3_18kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 600 | 3 | 18 | 250 | - | 600 | 3 | 18 | 144 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 600 | 3 | 10 | 144 | 150
|  | OLR | Allen-Bradley | 193-EEJF | 600 | 3 | 10 | 40-200 | -
AB113D-D180...-E1JD25-..575V_140G-J2_14kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 600 | 3 | 14 | 250 | - | 600 | 3 | 14 | 144 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 600 | 3 | 10 | 144 | 150
|  | OLR | Allen-Bradley | 193-EEJF | 600 | 3 | 10 | 40-200 | -
AB113D-D210...-E1KD40-..200V_140G-K6_65kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 200 | 3 | 65 | 400 | - | 200 | 3 | 65 | 177 FLA | 60 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 200 | 3 | 18 | 177 | 60
|  | OLR | Allen-Bradley | 193-EEKG | 200 | 3 | 18 | 60-300 | -
AB113D-D210...-E1KD40-..200V_140G-K3_35kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 200 | 3 | 35 | 400 | - | 200 | 3 | 35 | 177 FLA | 60 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 200 | 3 | 18 | 177 | 60
|  | OLR | Allen-Bradley | 193-EEKG | 200 | 3 | 18 | 60-300 | -
AB113D-D210...-E1KD40-..230V_140G-K6_65kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 230 | 3 | 65 | 400 | - | 230 | 3 | 65 | 192 FLA | 75 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 230 | 3 | 18 | 192 | 75
|  | OLR | Allen-Bradley | 193-EEKG | 230 | 3 | 18 | 60-300 | -
AB113D-D210...-E1KD40-..230V_140G-K3_35kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 230 | 3 | 35 | 400 | - | 230 | 3 | 35 | 192 FLA | 75 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 230 | 3 | 18 | 192 | 75
|  | OLR | Allen-Bradley | 193-EEKG | 230 | 3 | 18 | 60-300 | -
AB113D-D210...-E1KD40-..460V_140G-K6_65kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 480 | 3 | 65 | 400 | - | 480 | 3 | 65 | 180 FLA | 150 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 480 | 3 | 18 | 180 | 150
|  | OLR | Allen-Bradley | 193-EEKG | 480 | 3 | 18 | 60-300 | -
AB113D-D210...-E1KD40-..460V_140G-K3_35kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 480 | 3 | 35 | 400 | - | 480 | 3 | 35 | 180 FLA | 150 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 480 | 3 | 18 | 180 | 150
|  | OLR | Allen-Bradley | 193-EEKG | 480 | 3 | 18 | 60-300 | -
AB113D-D210...-E1KD40-..575V_140G-K6_30kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 600 | 3 | 30 | 400 | - | 600 | 3 | 30 | 192 FLA | 200 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 600 | 3 | 18 | 192 | 200
|  | OLR | Allen-Bradley | 193-EEKG | 600 | 3 | 18 | 60-300 | -
AB113D-D210...-E1KD40-..575V_140G-K3_25kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 600 | 3 | 25 | 400 | - | 600 | 3 | 25 | 192 FLA | 200 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 600 | 3 | 18 | 192 | 200
|  | OLR | Allen-Bradley | 193-EEKG | 600 | 3 | 18 | 60-300 | -
AB113D-D250...-E1KD40-..200V_140G-K6_65kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 200 | 3 | 65 | 400 | - | 200 | 3 | 65 | 221 FLA | 75 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 200 | 3 | 18 | 221 | 75
|  | OLR | Allen-Bradley | 193-EEKG | 200 | 3 | 18 | 60-300 | -
AB113D-D250...-E1KD40-..200V_140G-K3_35kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 200 | 3 | 35 | 400 | - | 200 | 3 | 35 | 221 FLA | 75 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 200 | 3 | 18 | 221 | 75
|  | OLR | Allen-Bradley | 193-EEKG | 200 | 3 | 18 | 60-300 | -
AB113D-D250...-E1KD40-..230V_140G-K6_65kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 230 | 3 | 65 | 400 | - | 230 | 3 | 65 | 248 FLA | 100 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 230 | 3 | 18 | 248 | 100
|  | OLR | Allen-Bradley | 193-EEKG | 230 | 3 | 18 | 60-300 | -
AB113D-D250...-E1KD40-..230V_140G-K3_35kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 230 | 3 | 35 | 400 | - | 230 | 3 | 35 | 248 FLA | 100 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 230 | 3 | 18 | 248 | 100
|  | OLR | Allen-Bradley | 193-EEKG | 230 | 3 | 18 | 60-300 | -
AB113D-D250...-E1KD40-..460V_140G-K6_65kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 480 | 3 | 65 | 400 | - | 480 | 3 | 65 | 240 FLA | 200 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 480 | 3 | 18 | 240 | 200
|  | OLR | Allen-Bradley | 193-EEKG | 480 | 3 | 18 | 60-300 | -
AB113D-D250...-E1KD40-..460V_140G-K3_35kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 480 | 3 | 35 | 400 | - | 480 | 3 | 35 | 240 FLA | 200 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 480 | 3 | 18 | 240 | 200
|  | OLR | Allen-Bradley | 193-EEKG | 480 | 3 | 18 | 60-300 | -
AB113D-D250...-E1KD40-..575V_140G-K6_30kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 600 | 3 | 30 | 400 | - | 600 | 3 | 30 | 242 FLA | 250 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 600 | 3 | 18 | 242 | 250
|  | OLR | Allen-Bradley | 193-EEKG | 600 | 3 | 18 | 60-300 | -
AB113D-D250...-E1KD40-..575V_140G-K3_25kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 600 | 3 | 25 | 400 | - | 600 | 3 | 25 | 242 FLA | 250 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 600 | 3 | 18 | 242 | 250
|  | OLR | Allen-Bradley | 193-EEKG | 600 | 3 | 18 | 60-300 | -
AB113D-D300...-E1KD40-..200V_140G-K6_65kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 200 | 3 | 65 | 400 | - | 200 | 3 | 65 | 285 FLA | 100 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 200 | 3 | 18 | 285 | 100
|  | OLR | Allen-Bradley | 193-EELG | 200 | 3 | 18 | 100-500 | -
AB113D-D300...-E1KD40-..200V_140G-K3_35kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 200 | 3 | 35 | 400 | - | 200 | 3 | 35 | 285 FLA | 100 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 200 | 3 | 18 | 285 | 100
|  | OLR | Allen-Bradley | 193-EELG | 200 | 3 | 18 | 100-500 | -
AB113D-D300...-E1KD40-..230V_140G-K6_65kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 230 | 3 | 65 | 400 | - | 230 | 3 | 65 | 312 FLA | 125 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 230 | 3 | 18 | 312 | 125
|  | OLR | Allen-Bradley | 193-EELG | 230 | 3 | 18 | 100-500 | -
AB113D-D300...-E1KD40-..230V_140G-K3_35kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 230 | 3 | 35 | 400 | - | 230 | 3 | 35 | 312 FLA | 125 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 230 | 3 | 18 | 312 | 125
|  | OLR | Allen-Bradley | 193-EELG | 230 | 3 | 18 | 100-500 | -
AB113D-D300...-E1KD40-..460V_140G-K6_65kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 480 | 3 | 65 | 400 | - | 480 | 3 | 65 | 302 FLA | 250 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 480 | 3 | 18 | 302 | 250
|  | OLR | Allen-Bradley | 193-EELG | 480 | 3 | 18 | 100-500 | -
AB113D-D300...-E1KD40-..460V_140G-K3_35kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 480 | 3 | 35 | 400 | - | 480 | 3 | 35 | 302 FLA | 250 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 480 | 3 | 18 | 302 | 250
|  | OLR | Allen-Bradley | 193-EELG | 480 | 3 | 18 | 100-500 | -
AB113D-D300...-E1KD40-..575V_140G-K6_30kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 600 | 3 | 30 | 400 | - | 600 | 3 | 30 | 289 FLA | 300 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 600 | 3 | 18 | 289 | 300
|  | OLR | Allen-Bradley | 193-EELG | 600 | 3 | 18 | 100-500 | -
AB113D-D300...-E1KD40-..575V_140G-K3_25kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 600 | 3 | 25 | 400 | - | 600 | 3 | 25 | 289 FLA | 300 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 600 | 3 | 18 | 289 | 300
|  | OLR | Allen-Bradley | 193-EELG | 600 | 3 | 18 | 100-500 | -
AB113D-D420...-E1LD80-..200V_140G-M6_65kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 200 | 3 | 65 | 800 | - | 200 | 3 | 65 | 414 FLA | 150 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 200 | 3 | 18 | 414 | 150
|  | OLR | Allen-Bradley | 193-EELG | 200 | 3 | 18 | 100-500 | -
AB113D-D420...-E1LD80-..200V_140G-M5_50kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 200 | 3 | 50 | 800 | - | 200 | 3 | 50 | 414 FLA | 150 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 200 | 3 | 18 | 414 | 150
|  | OLR | Allen-Bradley | 193-EELG | 200 | 3 | 18 | 100-500 | -
AB113D-D420...-E1LD80-..230V_140G-M6_65kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 230 | 3 | 65 | 800 | - | 230 | 3 | 65 | 420 FLA / 2520 LRA | 175 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 230 | 3 | 18 | 420 | 175
|  | OLR | Allen-Bradley | 193-EELG | 230 | 3 | 18 | 100-500 | -
AB113D-D420...-E1LD80-..230V_140G-M5_50kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 230 | 3 | 50 | 800 | - | 230 | 3 | 50 | 420 FLA / 2520 LRA | 175 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 230 | 3 | 18 | 420 | 175
|  | OLR | Allen-Bradley | 193-EELG | 230 | 3 | 18 | 100-500 | -
AB113D-D420...-E1LD80-..460V_140G-M6_65kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 480 | 3 | 65 | 800 | - | 480 | 3 | 65 | 414 FLA | 350 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 480 | 3 | 18 | 414 | 350
|  | OLR | Allen-Bradley | 193-EELG | 480 | 3 | 18 | 100-500 | -
AB113D-D420...-E1LD80-..460V_140G-M5_50kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 480 | 3 | 50 | 800 | - | 480 | 3 | 50 | 414 FLA | 350 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 480 | 3 | 18 | 414 | 350
|  | OLR | Allen-Bradley | 193-EELG | 480 | 3 | 18 | 100-500 | -
AB113D-D420...-E1LD80-..575V_140G-M6_42kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 600 | 3 | 42 | 800 | - | 600 | 3 | 42 | 382 FLA | 400 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 600 | 3 | 18 | 382 | 400
|  | OLR | Allen-Bradley | 193-EELG | 600 | 3 | 42 | 100-500 | -
AB113D-D420...-E1LD80-..575V_140G-M5_42kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 600 | 3 | 35 | 800 | - | 600 | 3 | 42 | 382 FLA | 400 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 600 | 3 | 18 | 382 | 400
|  | OLR | Allen-Bradley | 193-EELG | 600 | 3 | 18 | 100-500 | -
AB113D-D630...-E1MD80-..200V_140G-M6_65kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 200 | 3 | 65 | 800 | - | 200 | 3 | 65 | 552 FLA | 200 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 200 | 3 | 18 | 552 | 200
|  | OLR | Allen-Bradley | 193-EENH | 200 | 3 | 18 | 160-800 | -
AB113D-D630...-E1MD80-..200V_140G-M5_50kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 200 | 3 | 50 | 800 | - | 200 | 3 | 50 | 552 FLA | 200 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 200 | 3 | 18 | 552 | 200
|  | OLR | Allen-Bradley | 193-EENH | 200 | 3 | 18 | 160-800 | -
AB113D-D630...-E1MD80-..230V_140G-M6_65kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 230 | 3 | 65 | 800 | - | 230 | 3 | 65 | 604 FLA / 4832 LRA | 250 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 230 | 3 | 18 | 604 | 250
|  | OLR | Allen-Bradley | 193-EENH | 230 | 3 | 18 | 160-800 | -
AB113D-D630...-E1MD80-..230V_140G-M5_50kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 230 | 3 | 50 | 800 | - | 230 | 3 | 50 | 604 FLA / 4832 LRA | 250 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 230 | 3 | 18 | 604 | 250
|  | OLR | Allen-Bradley | 193-EENH | 230 | 3 | 18 | 160-800 | -
AB113D-D630...-E1MD80-..460V_140G-M6_65kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 480 | 3 | 65 | 800 | - | 480 | 3 | 65 | 590 FLA | 500 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 480 | 3 | 18 | 590 | 500
|  | OLR | Allen-Bradley | 193-EENH | 480 | 3 | 18 | 160-800 | -
AB113D-D630...-E1MD80-..460V_140G-M5_50kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 480 | 3 | 50 | 800 | - | 480 | 3 | 50 | 590 FLA | 500 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 480 | 3 | 18 | 590 | 500
|  | OLR | Allen-Bradley | 193-EENH | 480 | 3 | 18 | 160-800 | -
AB113D-D630...-E1MD80-..575V_140G-M6_42kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 600 | 3 | 42 | 800 | - | 600 | 3 | 42 | 562 FLA / 4496 LRA | 600 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 600 | 3 | 18 | 562 | 600
|  | OLR | Allen-Bradley | 193-EENH | 600 | 3 | 18 | 160-800 | -
AB113D-D630...-E1MD80-..575V_140G-M5_42kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 600 | 3 | 42 | 800 | - | 600 | 3 | 42 | 562 FLA / 4496 LRA | 600 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 600 | 3 | 18 | 562 | 600
|  | OLR | Allen-Bradley | 193-EENH | 600 | 3 | 18 | 160-800 | -
AB113D-D860...-E1MD80-..200V_140G-M6_65kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 200 | 3 | 65 | 800 | - | 200 | 3 | 65 | 695 FLA / 5560 LRA | 250 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 200 | 3 | 42 | 695 | 250
|  | OLR | Allen-Bradley | 193-EENH | 200 | 3 | 42 | 160-800 | -
AB113D-D860...-E1MD80-..200V_140G-M5_50kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 200 | 3 | 50 | 800 | - | 200 | 3 | 50 | 695 FLA / 5560 LRA | 250 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 200 | 3 | 42 | 695 | 250
|  | OLR | Allen-Bradley | 193-EENH | 200 | 3 | 42 | 160-800 | -
AB113D-D860...-E1MD80-..230V_140G-M6_65kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 230 | 3 | 65 | 800 | - | 230 | 3 | 65 | 722 FLA / 5776 LRA | 300 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 230 | 3 | 42 | 722 | 300
|  | OLR | Allen-Bradley | 193-EENH | 230 | 3 | 42 | 160-800 | -
AB113D-D860...-E1MD80-..230V_140G-M5_50kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 230 | 3 | 50 | 800 | - | 230 | 3 | 50 | 722 FLA / 5776 LRA | 300 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 230 | 3 | 42 | 722 | 300
|  | OLR | Allen-Bradley | 193-EENH | 230 | 3 | 42 | 160-800 | -
AB113D-D860...-E1MD80-..460V_140G-M6_65kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 480 | 3 | 65 | 800 | - | 480 | 3 | 65 | 702 FLA / 5616 LRA | 600 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 480 | 3 | 42 | 702 | 600
|  | OLR | Allen-Bradley | 193-EENH | 480 | 3 | 42 | 160-800 | -
AB113D-D860...-E1MD80-..460V_140G-M5_50kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 480 | 3 | 50 | 800 | - | 480 | 3 | 50 | 702 FLA / 5616 LRA | 600 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 480 | 3 | 42 | 702 | 600
|  | OLR | Allen-Bradley | 193-EENH | 480 | 3 | 42 | 160-800 | -
AB113D-D860...-E1MD80-..575V_140G-M6_42kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 600 | 3 | 42 | 800 | - | 600 | 3 | 42 | 651 FLA / 5208 LRA | 700 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 600 | 3 | 42 | 651 | 700
|  | OLR | Allen-Bradley | 193-EENH | 600 | 3 | 42 | 160-800 | -
AB113D-D860...-E1MD80-..575V_140G-M5_42kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 600 | 3 | 42 | 800 | - | 600 | 3 | 42 | 651 FLA / 5208 LRA | 700 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 600 | 3 | 42 | 651 | 700
|  | OLR | Allen-Bradley | 193-EENH | 600 | 3 | 42 | 160-800 | -
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number [1] | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP rating | Enclosure Volume, CU inches
AB113D-C30...-E3EC30-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C30...-E3EC30-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C30 | 200 | 3 | 35 | 30 | - | 200 | 3 | 35 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C30...-E3EC30-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C30 | 200 | 3 | 25 | 30 | - | 200 | 3 | 25 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C30...-E3EC30-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C30...-E3EC30-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C30 | 230 | 3 | 35 | 30 | - | 230 | 3 | 35 | 22 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C30...-E3EC30-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C30 | 230 | 3 | 25 | 30 | - | 230 | 3 | 25 | 22 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C30...-E3EC30-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C30...-E3EC30-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C30 | 480 | 3 | 35 | 30 | - | 480 | 3 | 35 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C30...-E3EC30-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C30 | 480 | 3 | 25 | 30 | - | 480 | 3 | 25 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C30...-E3EC30-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-C30 | 600 | 3 | 25 | 30 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C30...-E3EC30-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-C30 | 600 | 3 | 18 | 30 | - | 600 | 3 | 18 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C30...-E3EC30-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-C30 | 600 | 3 | 14 | 30 | - | 600 | 3 | 14 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C30...-E3FC50-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C30...-E3FC50-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 200 | 3 | 35 | 50 | - | 200 | 3 | 35 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C30...-E3FC50-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 200 | 3 | 25 | 50 | - | 200 | 3 | 25 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C30...-E3FC50-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C30...-E3FC50-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 230 | 3 | 35 | 50 | - | 230 | 3 | 35 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C30...-E3FC50-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 230 | 3 | 25 | 50 | - | 230 | 3 | 25 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C30...-E3FC50-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C30...-E3FC50-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 480 | 3 | 35 | 50 | - | 480 | 3 | 35 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C30...-E3FC50-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 480 | 3 | 25 | 50 | - | 480 | 3 | 25 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C30...-E3FC50-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 600 | 3 | 25 | 50 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C30...-E3FC50-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 600 | 3 | 18 | 50 | - | 600 | 3 | 18 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C30...-E3FC50-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 600 | 3 | 14 | 50 | - | 600 | 3 | 14 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C37...-E3FC50-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C37...-E3FC50-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 200 | 3 | 35 | 50 | - | 200 | 3 | 35 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C37...-E3FC50-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 200 | 3 | 25 | 50 | - | 200 | 3 | 25 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C37...-E3FC50-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C37...-E3FC50-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 230 | 3 | 35 | 50 | - | 230 | 3 | 35 | 28 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C37...-E3FC50-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 230 | 3 | 25 | 50 | - | 230 | 3 | 25 | 28 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C37...-E3FC50-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C37...-E3FC50-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 480 | 3 | 35 | 50 | - | 480 | 3 | 35 | 34 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C37...-E3FC50-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 480 | 3 | 25 | 50 | - | 480 | 3 | 25 | 34 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C37...-E3FC50-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 600 | 3 | 25 | 50 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C37...-E3FC50-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 600 | 3 | 18 | 50 | - | 600 | 3 | 18 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C37...-E3FC50-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 600 | 3 | 14 | 50 | - | 600 | 3 | 14 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C43...-E3FC80-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C43...-E3FC80-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 200 | 3 | 35 | 80 | - | 200 | 3 | 35 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C43...-E3FC80-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 200 | 3 | 25 | 80 | - | 200 | 3 | 25 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C43...-E3FC80-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C43...-E3FC80-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 230 | 3 | 35 | 80 | - | 230 | 3 | 35 | 42 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C43...-E3FC80-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 230 | 3 | 25 | 80 | - | 230 | 3 | 25 | 42 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C43...-E3FC80-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C43...-E3FC80-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 480 | 3 | 35 | 80 | - | 480 | 3 | 35 | 40 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C43...-E3FC80-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 480 | 3 | 25 | 80 | - | 480 | 3 | 25 | 40 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C43...-E3FC80-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C43...-E3FC80-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 600 | 3 | 18 | 80 | - | 600 | 3 | 18 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C43...-E3FC80-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 600 | 3 | 14 | 80 | - | 600 | 3 | 14 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C55...-E3GC80-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 5 | 18-90 | -
AB113D-C55...-E3GC80-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 200 | 3 | 35 | 80 | - | 200 | 3 | 35 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 5 | 18-90 | -
AB113D-C55...-E3GC80-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 200 | 3 | 25 | 80 | - | 200 | 3 | 25 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 5 | 18-90 | -
AB113D-C55...-E3GC80-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 5 | 18-90 | -
AB113D-C55...-E3GC80-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 230 | 3 | 35 | 80 | - | 230 | 3 | 35 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 5 | 18-90 | -
AB113D-C55...-E3GC80-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 230 | 3 | 25 | 80 | - | 230 | 3 | 25 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 5 | 18-90 | -
AB113D-C55...-E3GC80-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 5 | 18-90 | -
AB113D-C55...-E3GC80-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 480 | 3 | 35 | 80 | - | 480 | 3 | 35 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 5 | 18-90 | -
AB113D-C55...-E3GC80-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 480 | 3 | 25 | 80 | - | 480 | 3 | 25 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 5 | 18-90 | -
AB113D-C55...-E3GC80-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 5 | 18-90 | -
AB113D-C55...-E3GC80-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 600 | 3 | 18 | 80 | - | 600 | 3 | 18 | 41 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 5 | 18-90 | -
AB113D-C55...-E3GC80-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 600 | 3 | 14 | 80 | - | 600 | 3 | 14 | 41 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 5 | 18-90 | -
AB113D-C60...-E3GD12-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C60...-E3GD12-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C60...-E3GD12-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C60...-E3GD12-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C60...-E3GD12-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C60...-E3GD12-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C60...-E3GD12-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C60...-E3GD12-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C60...-E3GD12-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C60...-E3GD12-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C60...-E3GD12-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 600 | 3 | 18 | 125 | - | 600 | 3 | 18 | 52 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C60...-E3GD12-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 600 | 3 | 14 | 125 | - | 600 | 3 | 14 | 52 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C72...-E3GD12-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C72...-E3GD12-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 62.1 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C72...-E3GD12-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 62.1 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C72...-E3GD12-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 68 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C72...-E3GD12-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 68 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C72...-E3GD12-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 68 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C72...-E3GD12-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C72...-E3GD12-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 65 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C72...-E3GD12-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 65 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C72...-E3GD12-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C72...-E3GD12-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 600 | 3 | 18 | 125 | - | 600 | 3 | 18 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C72...-E3GD12-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 600 | 3 | 14 | 125 | - | 600 | 3 | 14 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C85...-E3GD12-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C85...-E3GD12-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 78.2 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C85...-E3GD12-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 78.2 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C85...-E3GD12-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C85...-E3GD12-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C85...-E3GD12-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C85...-E3GD12-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C85...-E3GD12-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 77 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C85...-E3GD12-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 77 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C85...-E3GD12-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C85...-E3GD12-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 600 | 3 | 18 | 125 | - | 600 | 3 | 18 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C85...-E3GD12-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 600 | 3 | 14 | 125 | - | 600 | 3 | 14 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C97...-E3VD12-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-C97...-E3VD12-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 92 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-C97...-E3VD12-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 92 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-C97...-E3VD12-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-C97...-E3VD12-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-C97...-E3VD12-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-C97...-E3VD12-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-C97...-E3VD12-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 96 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-C97...-E3VD12-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 96 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-C97...-E3VD12-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-C97...-E3VD12-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 600 | 3 | 18 | 125 | - | 600 | 3 | 18 | 77 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-C97...-E3VD12-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 600 | 3 | 14 | 125 | - | 600 | 3 | 14 | 77 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-C30G...-E3EC30-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3EC30-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C30 | 200 | 3 | 35 | 30 | - | 200 | 3 | 35 | 17.5 FLA | 5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3EC30-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C30 | 200 | 3 | 25 | 30 | - | 200 | 3 | 25 | 17.5 FLA | 5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3EC30-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3EC30-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C30 | 230 | 3 | 35 | 30 | - | 230 | 3 | 35 | 22 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3EC30-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C30 | 230 | 3 | 25 | 30 | - | 230 | 3 | 25 | 22 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3EC30-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3EC30-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C30 | 480 | 3 | 35 | 30 | - | 480 | 3 | 35 | 21 FLA | 15 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3EC30-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C30 | 480 | 3 | 25 | 30 | - | 480 | 3 | 25 | 21 FLA | 15 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3EC30-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-C30 | 600Y/347 | 3 | 25 | 30 | - | 600Y/347 | 3 | 25 | 22 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3EC30-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-C30 | 600Y/347 | 3 | 14 | 30 | - | 600Y/347 | 3 | 14 | 22 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3EC30-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-C30 | 600Y/347 | 3 | 10 | 30 | - | 600Y/347 | 3 | 10 | 22 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3FC50-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3FC50-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 200 | 3 | 35 | 50 | - | 200 | 3 | 35 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3FC50-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 200 | 3 | 25 | 50 | - | 200 | 3 | 25 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3FC50-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3FC50-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 230 | 3 | 35 | 50 | - | 230 | 3 | 35 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3FC50-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 230 | 3 | 25 | 50 | - | 230 | 3 | 25 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3FC50-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3FC50-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 480 | 3 | 35 | 50 | - | 480 | 3 | 35 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3FC50-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 480 | 3 | 25 | 50 | - | 480 | 3 | 25 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3FC50-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 600Y/347 | 3 | 25 | 50 | - | 600Y/347 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3FC50-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 600Y/347 | 3 | 14 | 50 | - | 600Y/347 | 3 | 14 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C30G...-E3FC50-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 600Y/347 | 3 | 10 | 50 | - | 600Y/347 | 3 | 10 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C37G...-E3FC50-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C37G...-E3FC50-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 200 | 3 | 35 | 50 | - | 200 | 3 | 35 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C37G...-E3FC50-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 200 | 3 | 25 | 50 | - | 200 | 3 | 25 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C37G...-E3FC50-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C37G...-E3FC50-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 230 | 3 | 35 | 50 | - | 230 | 3 | 35 | 28 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C37G...-E3FC50-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 230 | 3 | 25 | 50 | - | 230 | 3 | 25 | 28 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C37G...-E3FC50-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C37G...-E3FC50-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 480 | 3 | 35 | 50 | - | 480 | 3 | 35 | 34 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C37G...-E3FC50-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 480 | 3 | 25 | 50 | - | 480 | 3 | 25 | 34 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C37G...-E3FC50-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 600Y/347 | 3 | 25 | 50 | - | 600Y/347 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C37G...-E3FC50-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 600Y/347 | 3 | 14 | 50 | - | 600Y/347 | 3 | 14 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C37G...-E3FC50-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 600Y/347 | 3 | 10 | 50 | - | 600Y/347 | 3 | 10 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C43G...-E3FC80-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C43G...-E3FC80-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 200 | 3 | 35 | 80 | - | 200 | 3 | 35 | 32.2 FLA | 10 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C43G...-E3FC80-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 200 | 3 | 25 | 80 | - | 200 | 3 | 25 | 32.2 FLA | 10 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C43G...-E3FC80-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 28 FLA | 10 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C43G...-E3FC80-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 230 | 3 | 35 | 80 | - | 230 | 3 | 35 | 28 FLA | 10 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C43G...-E3FC80-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 230 | 3 | 25 | 80 | - | 230 | 3 | 25 | 28 FLA | 10 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C43G...-E3FC80-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C43G...-E3FC80-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 480 | 3 | 35 | 80 | - | 480 | 3 | 35 | 40 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C43G...-E3FC80-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 480 | 3 | 25 | 80 | - | 480 | 3 | 25 | 40 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C43G...-E3FC50-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 600Y/347 | 3 | 25 | 50 | - | 600Y/347 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C43G...-E3FC50-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 600Y/347 | 3 | 14 | 50 | - | 600Y/347 | 3 | 14 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C43G...-E3FC50-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 600Y/347 | 3 | 10 | 50 | - | 600Y/347 | 3 | 10 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C55G...-E3GC80-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 5 | 18-90 | -
AB113D-C55G...-E3GC80-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 200 | 3 | 35 | 80 | - | 200 | 3 | 35 | 48.3 FLA | 15 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 5 | 18-90 | -
AB113D-C55G...-E3GC80-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 200 | 3 | 25 | 80 | - | 200 | 3 | 25 | 48.3 FLA | 15 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 5 | 18-90 | -
AB113D-C55G...-E3GC80-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 5 | 18-90 | -
AB113D-C55G...-E3GC80-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 230 | 3 | 35 | 80 | - | 230 | 3 | 35 | 54 FLA | 20 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 5 | 18-90 | -
AB113D-C55G...-E3GC80-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 230 | 3 | 25 | 80 | - | 230 | 3 | 25 | 54 FLA | 20 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 5 | 18-90 | -
AB113D-C55G...-E3GC80-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 5 | 18-90 | -
AB113D-C55G...-E3GC80-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 480 | 3 | 35 | 80 | - | 480 | 3 | 35 | 52 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 5 | 18-90 | -
AB113D-C55G...-E3GC80-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 480 | 3 | 25 | 80 | - | 480 | 3 | 25 | 52 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 5 | 18-90 | -
AB113D-C60G...-E3GD12-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C60G...-E3GD12-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C60G...-E3GD12-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C60G...-E3GD12-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C60G...-E3GD12-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C60G...-E3GD12-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C60G...-E3GD12-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C60G...-E3GD12-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C60G...-E3GD12-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C60G...-E3GD12-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 600Y/347 | 3 | 25 | 125 | - | 600Y/347 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C60G...-E3GD12-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 600Y/347 | 3 | 14 | 125 | - | 600Y/347 | 3 | 14 | 52 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C60G...-E3GD12-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 600Y/347 | 3 | 10 | 125 | - | 600Y/347 | 3 | 10 | 52 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C72G...-E3GD12-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C72G...-E3GD12-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 62.1 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C72G...-E3GD12-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 62.1 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C72G...-E3GD12-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 68 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C72G...-E3GD12-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 68 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C72G...-E3GD12-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 68 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C72G...-E3GD12-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C72G...-E3GD12-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 65 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C72G...-E3GD12-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 65 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C72G...-E3GD12-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 600Y/347 | 3 | 25 | 125 | - | 600Y/347 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C72G...-E3GD12-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 600Y/347 | 3 | 14 | 125 | - | 600Y/347 | 3 | 14 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C72G...-E3GD12-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 600Y/347 | 3 | 10 | 125 | - | 600Y/347 | 3 | 10 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C85G...-E3GD12-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C85G...-E3GD12-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 78.2 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C85G...-E3GD12-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 78.2 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C85G...-E3GD12-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C85G...-E3GD12-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C85G...-E3GD12-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C85G...-E3GD12-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C85G...-E3GD12-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 77 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C85G...-E3GD12-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 77 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C85G...-E3GD12-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 600Y/347 | 3 | 25 | 125 | - | 600Y/347 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C85G...-E3GD12-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 600Y/347 | 3 | 14 | 125 | - | 600Y/347 | 3 | 14 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C85G...-E3GD12-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 600Y/347 | 3 | 10 | 125 | - | 600Y/347 | 3 | 10 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C97G...-E3VD12-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-C97G...-E3VD12-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 92 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-C97G...-E3VD12-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 92 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-C97G...-E3VD12-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-C97G...-E3VD12-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-C97G...-E3VD12-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-C97G...-E3VD12-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-C97G...-E3VD12-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 96 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-C97G...-E3VD12-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 96 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-C97G...-E3VD12-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 600Y/347 | 3 | 25 | 125 | - | 600Y/347 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-C97G...-E3VD12-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 600Y/347 | 3 | 14 | 125 | - | 600Y/347 | 3 | 14 | 77 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-C97G...-E3VD12-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 600Y/347 | 3 | 10 | 125 | - | 600Y/347 | 3 | 10 | 77 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HD25-..200V_140G-J6_65kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 92 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HD25-..200V_140G-J3_35kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 200 | 3 | 35 | 250 | - | 200 | 3 | 35 | 92 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HD25-..200V_140G-J2_25kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 200 | 3 | 25 | 250 | - | 200 | 3 | 25 | 92 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HD25-..230V_140G-J6_65kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 104 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HD25-..230V_140G-J3_35kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 230 | 3 | 35 | 250 | - | 230 | 3 | 35 | 104 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HD25-..230V_140G-J2_25kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 230 | 3 | 25 | 250 | - | 230 | 3 | 25 | 104 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HD25-..460V_140G-J6_65kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 96 FLA | 75 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HD25-..460V_140G-J3_35kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 480 | 3 | 35 | 250 | - | 480 | 3 | 35 | 96 FLA | 75 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HD25-..460V_140G-J2_25kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 480 | 3 | 25 | 250 | - | 480 | 3 | 25 | 96 FLA | 75 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HD25-..575V_140G-J6_25kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 99 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HD25-..575V_140G-J3_18kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 600 | 3 | 18 | 250 | - | 600 | 3 | 18 | 99 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HD25-..575V_140G-J2_14kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 600 | 3 | 14 | 250 | - | 600 | 3 | 14 | 99 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD25-..200V_140G-J6_65kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 120 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD25-..200V_140G-J3_35kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 200 | 3 | 35 | 250 | - | 200 | 3 | 35 | 120 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD25-..200V_140G-J2_25kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 200 | 3 | 25 | 250 | - | 200 | 3 | 25 | 120 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD25-..230V_140G-J6_65kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 130 FLA | 50 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD25-..230V_140G-J3_35kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 230 | 3 | 35 | 250 | - | 230 | 3 | 35 | 130 FLA | 50 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD25-..230V_140G-J2_25kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 230 | 3 | 25 | 250 | - | 230 | 3 | 25 | 130 FLA | 50 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD25-..460V_140G-J6_65kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 124 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD25-..460V_140G-J3_35kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 480 | 3 | 35 | 250 | - | 480 | 3 | 35 | 124 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD25-..460V_140G-J2_25kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 480 | 3 | 25 | 250 | - | 480 | 3 | 25 | 124 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD25-..575V_140G-J6_25kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 125 FLA | 125 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD25-..575V_140G-J3_18kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 600 | 3 | 18 | 250 | - | 600 | 3 | 18 | 125 FLA | 125 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD25-..575V_140G-J2_14kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 600 | 3 | 14 | 250 | - | 600 | 3 | 14 | 125 FLA | 125 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-D180...-E3JD25-..200V_140G-J6_65kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 150 FLA | 50 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 200 | 3 | 10 | 150 | 50
|  | OLR | Allen-Bradley | 193-EC*GF | 200 | 3 | 10 | 42-210 | -
AB113D-D180...-E3JD25-..200V_140G-J3_35kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 200 | 3 | 35 | 250 | - | 200 | 3 | 35 | 150 FLA | 50 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 200 | 3 | 10 | 150 | 50
|  | OLR | Allen-Bradley | 193-EC*GF | 200 | 3 | 10 | 42-210 | -
AB113D-D180...-E3JD25-..200V_140G-J2_25kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 200 | 3 | 25 | 250 | - | 200 | 3 | 25 | 150 FLA | 50 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 200 | 3 | 10 | 150 | 50
|  | OLR | Allen-Bradley | 193-EC*GF | 200 | 3 | 10 | 42-210 | -
AB113D-D180...-E3JD25-..230V_140G-J6_65kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 154 FLA | 60 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 230 | 3 | 10 | 154 | 60
|  | OLR | Allen-Bradley | 193-EC*GF | 230 | 3 | 10 | 42-210 | -
AB113D-D180...-E3JD25-..230V_140G-J3_35kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 230 | 3 | 35 | 250 | - | 230 | 3 | 35 | 154 FLA | 60 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 230 | 3 | 10 | 154 | 60
|  | OLR | Allen-Bradley | 193-EC*GF | 230 | 3 | 10 | 42-210 | -
AB113D-D180...-E3JD25-..230V_140G-J2_25kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 230 | 3 | 25 | 250 | - | 230 | 3 | 25 | 154 FLA | 60 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 230 | 3 | 10 | 154 | 60
|  | OLR | Allen-Bradley | 193-EC*GF | 230 | 3 | 10 | 42-210 | -
AB113D-D180...-E3JD25-..460V_140G-J6_65kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 180 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 480 | 3 | 10 | 180 | 150
|  | OLR | Allen-Bradley | 193-EC*GF | 480 | 3 | 10 | 42-210 | -
AB113D-D180...-E3JD25-..460V_140G-J3_35kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 480 | 3 | 35 | 250 | - | 480 | 3 | 35 | 180 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 480 | 3 | 10 | 180 | 150
|  | OLR | Allen-Bradley | 193-EC*GF | 480 | 3 | 10 | 42-210 | -
AB113D-D180...-E3JD25-..460V_140G-J2_25kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 480 | 3 | 25 | 250 | - | 480 | 3 | 25 | 180 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 480 | 3 | 10 | 180 | 150
|  | OLR | Allen-Bradley | 193-EC*GF | 480 | 3 | 10 | 42-210 | -
AB113D-D180...-E3JD25-..575V_140G-J6_25kA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 144 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 600 | 3 | 10 | 144 | 150
|  | OLR | Allen-Bradley | 193-EC*GF | 600 | 3 | 10 | 42-210 | -
AB113D-D180...-E3JD25-..575V_140G-J3_18kA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 600 | 3 | 18 | 250 | - | 600 | 3 | 18 | 144 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 600 | 3 | 10 | 144 | 150
|  | OLR | Allen-Bradley | 193-EC*GF | 600 | 3 | 10 | 42-210 | -
AB113D-D180...-E3JD25-..575V_140G-J2_14kA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 600 | 3 | 14 | 250 | - | 600 | 3 | 14 | 144 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 600 | 3 | 10 | 144 | 150
|  | OLR | Allen-Bradley | 193-EC*GF | 600 | 3 | 10 | 42-210 | -
AB113D-D210...-E3KD40-..200V_140G-K6_65kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 200 | 3 | 65 | 400 | - | 200 | 3 | 65 | 177 FLA | 60 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 200 | 3 | 18 | 177 | 60
|  | OLR | Allen-Bradley | 193-EC*HG | 200 | 3 | 18 | 60-302 | -
AB113D-D210...-E3KD40-..200V_140G-K3_35kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 200 | 3 | 35 | 400 | - | 200 | 3 | 35 | 177 FLA | 60 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 200 | 3 | 18 | 177 | 60
|  | OLR | Allen-Bradley | 193-EC*HG | 200 | 3 | 18 | 60-302 | -
AB113D-D210...-E3KD40-..200V_140G-K2_25kA | C | CB | Allen-Bradley | 140G-K2*3-D40 | 200 | 3 | 25 | 400 | - | 200 | 3 | 25 | 177 FLA | 60 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 200 | 3 | 18 | 177 | 60
|  | OLR | Allen-Bradley | 193-EC*HG | 200 | 3 | 18 | 60-302 | -
AB113D-D210...-E3KD40-..230V_140G-K6_65kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 230 | 3 | 65 | 400 | - | 230 | 3 | 65 | 192 FLA | 75 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 230 | 3 | 18 | 192 | 75
|  | OLR | Allen-Bradley | 193-EC*HG | 230 | 3 | 18 | 60-302 | -
AB113D-D210...-E3KD40-..230V_140G-K3_35kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 230 | 3 | 35 | 400 | - | 230 | 3 | 35 | 192 FLA | 75 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 230 | 3 | 18 | 192 | 75
|  | OLR | Allen-Bradley | 193-EC*HG | 230 | 3 | 18 | 60-302 | -
AB113D-D210...-E3KD40-..230V_140G-K2_25kA | C | CB | Allen-Bradley | 140G-K2*3-D40 | 230 | 3 | 25 | 400 | - | 230 | 3 | 25 | 192 FLA | 75 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 230 | 3 | 18 | 192 | 75
|  | OLR | Allen-Bradley | 193-EC*HG | 230 | 3 | 18 | 60-302 | -
AB113D-D210...-E3KD40-..460V_140G-K6_65kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 480 | 3 | 65 | 400 | - | 480 | 3 | 65 | 180 FLA | 150 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 480 | 3 | 18 | 180 | 150
|  | OLR | Allen-Bradley | 193-EC*HG | 480 | 3 | 18 | 60-302 | -
AB113D-D210...-E3KD40-..460V_140G-K3_35kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 480 | 3 | 35 | 400 | - | 480 | 3 | 35 | 180 FLA | 150 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 480 | 3 | 18 | 180 | 150
|  | OLR | Allen-Bradley | 193-EC*HG | 480 | 3 | 18 | 60-302 | -
AB113D-D210...-E3KD40-..460V_140G-K2_25kA | C | CB | Allen-Bradley | 140G-K2*3-D40 | 480 | 3 | 25 | 400 | - | 480 | 3 | 25 | 180 FLA | 150 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 480 | 3 | 18 | 180 | 150
|  | OLR | Allen-Bradley | 193-EC*HG | 480 | 3 | 18 | 60-302 | -
AB113D-D210...-E3KD40-..575V_140G-K6_30kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 600 | 3 | 30 | 400 | - | 600 | 3 | 30 | 192 FLA | 200 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 600 | 3 | 18 | 192 | 200
|  | OLR | Allen-Bradley | 193-EC*HG | 600 | 3 | 18 | 60-302 | -
AB113D-D210...-E3KD40-..575V_140G-K3_25kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 600 | 3 | 25 | 400 | - | 600 | 3 | 25 | 192 FLA | 200 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 600 | 3 | 18 | 192 | 200
|  | OLR | Allen-Bradley | 193-EC*HG | 600 | 3 | 18 | 60-302 | -
AB113D-D210...-E3KD40-..575V_140G-K2_18kA | C | CB | Allen-Bradley | 140G-K2*3-D40 | 600 | 3 | 18 | 400 | - | 600 | 3 | 18 | 192 FLA | 200 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 600 | 3 | 18 | 192 | 200
|  | OLR | Allen-Bradley | 193-EC*HG | 600 | 3 | 18 | 60-302 | -
AB113D-D250...-E3KD40-..200V_140G-K6_65kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 200 | 3 | 65 | 400 | - | 200 | 3 | 65 | 221 FLA | 75 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 200 | 3 | 18 | 221 | 75
|  | OLR | Allen-Bradley | 193-EC*HG | 200 | 3 | 18 | 60-302 | -
AB113D-D250...-E3KD40-..200V_140G-K3_35kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 200 | 3 | 35 | 400 | - | 200 | 3 | 35 | 221 FLA | 75 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 200 | 3 | 18 | 221 | 75
|  | OLR | Allen-Bradley | 193-EC*HG | 200 | 3 | 18 | 60-302 | -
AB113D-D250...-E3KD40-..200V_140G-K2_25kA | C | CB | Allen-Bradley | 140G-K2*3-D40 | 200 | 3 | 25 | 400 | - | 200 | 3 | 25 | 221 FLA | 75 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 200 | 3 | 18 | 221 | 75
|  | OLR | Allen-Bradley | 193-EC*HG | 200 | 3 | 18 | 60-302 | -
AB113D-D250...-E3KD40-..230V_140G-K6_65kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 230 | 3 | 65 | 400 | - | 230 | 3 | 65 | 248 FLA | 100 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 230 | 3 | 18 | 248 | 100
|  | OLR | Allen-Bradley | 193-EC*HG | 230 | 3 | 18 | 60-302 | -
AB113D-D250...-E3KD40-..230V_140G-K3_35kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 230 | 3 | 35 | 400 | - | 230 | 3 | 35 | 248 FLA | 100 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 230 | 3 | 18 | 248 | 100
|  | OLR | Allen-Bradley | 193-EC*HG | 230 | 3 | 18 | 60-302 | -
AB113D-D250...-E3KD40-..230V_140G-K2_25kA | C | CB | Allen-Bradley | 140G-K2*3-D40 | 230 | 3 | 25 | 400 | - | 230 | 3 | 25 | 248 FLA | 100 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 230 | 3 | 18 | 248 | 100
|  | OLR | Allen-Bradley | 193-EC*HG | 230 | 3 | 18 | 60-302 | -
AB113D-D250...-E3KD40-..460V_140G-K6_65kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 480 | 3 | 65 | 400 | - | 480 | 3 | 65 | 240 FLA | 200 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 480 | 3 | 18 | 240 | 200
|  | OLR | Allen-Bradley | 193-EC*HG | 480 | 3 | 18 | 60-302 | -
AB113D-D250...-E3KD40-..460V_140G-K3_35kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 480 | 3 | 35 | 400 | - | 480 | 3 | 35 | 240 FLA | 200 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 480 | 3 | 18 | 240 | 200
|  | OLR | Allen-Bradley | 193-EC*HG | 480 | 3 | 18 | 60-302 | -
AB113D-D250...-E3KD40-..460V_140G-K2_25kA | C | CB | Allen-Bradley | 140G-K2*3-D40 | 480 | 3 | 25 | 400 | - | 480 | 3 | 25 | 240 FLA | 200 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 480 | 3 | 18 | 240 | 200
|  | OLR | Allen-Bradley | 193-EC*HG | 480 | 3 | 18 | 60-302 | -
AB113D-D250...-E3KD40-..575V_140G-K6_30kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 600 | 3 | 30 | 400 | - | 600 | 3 | 30 | 242 FLA | 250 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 600 | 3 | 18 | 242 | 250
|  | OLR | Allen-Bradley | 193-EC*HG | 600 | 3 | 18 | 60-302 | -
AB113D-D250...-E3KD40-..575V_140G-K3_25kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 600 | 3 | 25 | 400 | - | 600 | 3 | 25 | 242 FLA | 250 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 600 | 3 | 18 | 242 | 250
|  | OLR | Allen-Bradley | 193-EC*HG | 600 | 3 | 18 | 60-302 | -
AB113D-D250...-E3KD40-..575V_140G-K2_18kA | C | CB | Allen-Bradley | 140G-K2*3-D40 | 600 | 3 | 18 | 400 | - | 600 | 3 | 18 | 242 FLA | 250 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 600 | 3 | 18 | 242 | 250
|  | OLR | Allen-Bradley | 193-EC*HG | 600 | 3 | 18 | 60-302 | -
AB113D-D300...-E3KD40-..200V_140G-K6_65kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 200 | 3 | 65 | 400 | - | 200 | 3 | 65 | 285 FLA | 100 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 200 | 3 | 18 | 285 | 100
|  | OLR | Allen-Bradley | 193-EC*JG | 200 | 3 | 18 | 84-420 | -
AB113D-D300...-E3KD40-..200V_140G-K3_35kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 200 | 3 | 35 | 400 | - | 200 | 3 | 35 | 285 FLA | 100 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 200 | 3 | 18 | 285 | 100
|  | OLR | Allen-Bradley | 193-EC*JG | 200 | 3 | 18 | 84-420 | -
AB113D-D300...-E3KD40-..200V_140G-K2_25kA | C | CB | Allen-Bradley | 140G-K2*3-D40 | 200 | 3 | 25 | 400 | - | 200 | 3 | 25 | 285 FLA | 100 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 200 | 3 | 18 | 285 | 100
|  | OLR | Allen-Bradley | 193-EC*JG | 200 | 3 | 18 | 84-420 | -
AB113D-D300...-E3KD40-..230V_140G-K6_65kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 230 | 3 | 65 | 400 | - | 230 | 3 | 65 | 312 FLA | 125 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 230 | 3 | 18 | 312 | 125
|  | OLR | Allen-Bradley | 193-EC*JG | 230 | 3 | 18 | 84-420 | -
AB113D-D300...-E3KD40-..230V_140G-K3_35kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 230 | 3 | 35 | 400 | - | 230 | 3 | 35 | 312 FLA | 125 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 230 | 3 | 18 | 312 | 125
|  | OLR | Allen-Bradley | 193-EC*JG | 230 | 3 | 18 | 84-420 | -
AB113D-D300...-E3KD40-..230V_140G-K2_25kA | C | CB | Allen-Bradley | 140G-K2*3-D40 | 230 | 3 | 25 | 400 | - | 230 | 3 | 25 | 312 FLA | 125 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 230 | 3 | 18 | 312 | 125
|  | OLR | Allen-Bradley | 193-EC*JG | 230 | 3 | 18 | 84-420 | -
AB113D-D300...-E3KD40-..460V_140G-K6_65kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 480 | 3 | 65 | 400 | - | 480 | 3 | 65 | 302 FLA | 250 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 480 | 3 | 18 | 302 | 250
|  | OLR | Allen-Bradley | 193-EC*JG | 480 | 3 | 18 | 84-420 | -
AB113D-D300...-E3KD40-..460V_140G-K3_35kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 480 | 3 | 35 | 400 | - | 480 | 3 | 35 | 302 FLA | 250 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 480 | 3 | 18 | 302 | 250
|  | OLR | Allen-Bradley | 193-EC*JG | 480 | 3 | 18 | 84-420 | -
AB113D-D300...-E3KD40-..460V_140G-K2_25kA | C | CB | Allen-Bradley | 140G-K2*3-D40 | 480 | 3 | 25 | 400 | - | 480 | 3 | 25 | 302 FLA | 250 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 480 | 3 | 18 | 302 | 250
|  | OLR | Allen-Bradley | 193-EC*JG | 480 | 3 | 18 | 84-420 | -
AB113D-D300...-E3KD40-..575V_140G-K6_30kA | C | CB | Allen-Bradley | 140G-K6*3-D40 | 600 | 3 | 30 | 400 | - | 600 | 3 | 30 | 289 FLA | 300 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 600 | 3 | 18 | 289 | 300
|  | OLR | Allen-Bradley | 193-EC*JG | 600 | 3 | 18 | 84-420 | -
AB113D-D300...-E3KD40-..575V_140G-K3_25kA | C | CB | Allen-Bradley | 140G-K3*3-D40 | 600 | 3 | 25 | 400 | - | 600 | 3 | 25 | 289 FLA | 300 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 600 | 3 | 18 | 289 | 300
|  | OLR | Allen-Bradley | 193-EC*JG | 600 | 3 | 18 | 84-420 | -
AB113D-D300...-E3KD40-..575V_140G-K2_18kA | C | CB | Allen-Bradley | 140G-K2*3-D40 | 600 | 3 | 18 | 400 | - | 600 | 3 | 18 | 289 FLA | 300 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 600 | 3 | 18 | 289 | 300
|  | OLR | Allen-Bradley | 193-EC*JG | 600 | 3 | 18 | 84-420 | -
AB113D-D420...-E3LD80-..200V_140G-M6_65kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 200 | 3 | 65 | 800 | - | 200 | 3 | 65 | 414 FLA | 150 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 200 | 3 | 18 | 414 | 150
|  | OLR | Allen-Bradley | 193-EC*JG | 200 | 3 | 18 | 84-420 | -
AB113D-D420...-E3LD80-..200V_140G-M5_50kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 200 | 3 | 50 | 800 | - | 200 | 3 | 50 | 414 FLA | 150 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 200 | 3 | 18 | 414 | 150
|  | OLR | Allen-Bradley | 193-EC*JG | 200 | 3 | 18 | 84-420 | -
AB113D-D420...-E3LD80-..230V_140G-M6_65kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 230 | 3 | 65 | 800 | - | 230 | 3 | 65 | 420 FLA / 2520 LRA | 175 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 230 | 3 | 18 | 420 | 175
|  | OLR | Allen-Bradley | 193-EC*JG | 230 | 3 | 18 | 84-420 | -
AB113D-D420...-E3LD80-..230V_140G-M5_50kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 230 | 3 | 50 | 800 | - | 230 | 3 | 50 | 420 FLA / 2520 LRA | 175 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 230 | 3 | 18 | 420 | 175
|  | OLR | Allen-Bradley | 193-EC*JG | 230 | 3 | 18 | 84-420 | -
AB113D-D420...-E3LD80-..460V_140G-M6_65kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 480 | 3 | 65 | 800 | - | 480 | 3 | 65 | 414 FLA | 350 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 480 | 3 | 18 | 414 | 350
|  | OLR | Allen-Bradley | 193-EC*JG | 480 | 3 | 18 | 84-420 | -
AB113D-D420...-E3LD80-..460V_140G-M5_50kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 480 | 3 | 50 | 800 | - | 480 | 3 | 50 | 414 FLA | 350 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 480 | 3 | 18 | 414 | 350
|  | OLR | Allen-Bradley | 193-EC*JG | 480 | 3 | 18 | 84-420 | -
AB113D-D420...-E3LD80-..575V_140G-M6_42kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 600 | 3 | 42 | 800 | - | 600 | 3 | 42 | 382 FLA | 400 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 600 | 3 | 18 | 382 | 400
|  | OLR | Allen-Bradley | 193-EC*JG | 600 | 3 | 18 | 84-420 | -
AB113D-D420...-E3LD80-..575V_140G-M5_42kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 600 | 3 | 42 | 800 | - | 600 | 3 | 42 | 382 FLA | 400 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 600 | 3 | 18 | 382 | 400
|  | OLR | Allen-Bradley | 193-EC*JG | 600 | 3 | 18 | 84-420 | -
AB113D-D630...-E3MD80-..200V_140G-M6_65kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 200 | 3 | 65 | 800 | - | 200 | 3 | 65 | 552 FLA | 200 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 200 | 3 | 18 | 552 | 200
|  | OLR | Allen-Bradley | 193-EC*KH | 200 | 3 | 18 | 125-630 | -
AB113D-D630...-E3MD80-..200V_140G-M5_50kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 200 | 3 | 50 | 800 | - | 200 | 3 | 50 | 552 FLA | 200 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 200 | 3 | 18 | 552 | 200
|  | OLR | Allen-Bradley | 193-EC*KH | 200 | 3 | 18 | 125-630 | -
AB113D-D630...-E3MD80-..230V_140G-M6_65kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 230 | 3 | 65 | 800 | - | 230 | 3 | 65 | 604 FLA / 4832 LRA | 250 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 230 | 3 | 18 | 604 | 250
|  | OLR | Allen-Bradley | 193-EC*KH | 230 | 3 | 18 | 125-630 | -
AB113D-D630...-E3MD80-..230V_140G-M5_50kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 230 | 3 | 50 | 800 | - | 230 | 3 | 50 | 604 FLA / 4832 LRA | 250 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 230 | 3 | 18 | 604 | 250
|  | OLR | Allen-Bradley | 193-EC*KH | 230 | 3 | 18 | 125-630 | -
AB113D-D630...-E3MD80-..460V_140G-M6_65kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 480 | 3 | 65 | 800 | - | 480 | 3 | 65 | 590 FLA | 500 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 480 | 3 | 18 | 590 | 500
|  | OLR | Allen-Bradley | 193-EC*KH | 480 | 3 | 18 | 125-630 | -
AB113D-D630...-E3MD80-..460V_140G-M5_50kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 480 | 3 | 50 | 800 | - | 480 | 3 | 50 | 590 FLA | 500 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 480 | 3 | 18 | 590 | 500
|  | OLR | Allen-Bradley | 193-EC*KH | 480 | 3 | 18 | 125-630 | -
AB113D-D630...-E3MD80-..575V_140G-M6_42kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 600 | 3 | 42 | 800 | - | 600 | 3 | 42 | 562 FLA / 4496 LRA | 600 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 600 | 3 | 18 | 562 | 600
|  | OLR | Allen-Bradley | 193-EC*KH | 600 | 3 | 18 | 125-630 | -
AB113D-D630...-E3MD80-..575V_140G-M5_42kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 600 | 3 | 42 | 800 | - | 600 | 3 | 42 | 562 FLA / 4496 LRA | 600 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 600 | 3 | 18 | 562 | 600
|  | OLR | Allen-Bradley | 193-EC*KH | 600 | 3 | 18 | 125-630 | -
AB113D-D860...-E3MD80-..200V_140G-M6_65kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 200 | 3 | 65 | 800 | - | 200 | 3 | 65 | 695 FLA / 5560 LRA | 250 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 200 | 3 | 42 | 695 | 250
|  | OLR | Allen-Bradley | 193-EC*LH | 200 | 3 | 42 | 172-860 | -
AB113D-D860...-E3MD80-..200V_140G-M5_50kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 200 | 3 | 50 | 800 | - | 200 | 3 | 50 | 695 FLA / 5560 LRA | 250 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 200 | 3 | 42 | 695 | 250
|  | OLR | Allen-Bradley | 193-EC*LH | 200 | 3 | 42 | 172-860 | -
AB113D-D860...-E3MD80-..230V_140G-M6_65kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 230 | 3 | 65 | 800 | - | 230 | 3 | 65 | 722 FLA / 5776 LRA | 300 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 230 | 3 | 42 | 722 | 300
|  | OLR | Allen-Bradley | 193-EC*LH | 230 | 3 | 42 | 172-860 | -
AB113D-D860...-E3MD80-..230V_140G-M5_50kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 230 | 3 | 50 | 800 | - | 230 | 3 | 50 | 722 FLA / 5776 LRA | 300 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 230 | 3 | 42 | 722 | 300
|  | OLR | Allen-Bradley | 193-EC*LH | 230 | 3 | 42 | 172-860 | -
AB113D-D860...-E3MD80-..460V_140G-M6_65kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 480 | 3 | 65 | 800 | - | 480 | 3 | 65 | 702 FLA / 5616 LRA | 600 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 480 | 3 | 42 | 702 | 600
|  | OLR | Allen-Bradley | 193-EC*LH | 480 | 3 | 42 | 172-860 | -
AB113D-D860...-E3MD80-..460V_140G-M5_50kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 480 | 3 | 50 | 800 | - | 480 | 3 | 50 | 702 FLA / 5616 LRA | 600 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 480 | 3 | 42 | 702 | 600
|  | OLR | Allen-Bradley | 193-EC*LH | 480 | 3 | 42 | 172-860 | -
AB113D-D860...-E3MD80-..575V_140G-M6_42kA | C | CB | Allen-Bradley | 140G-M6*3-D80 | 600 | 3 | 42 | 800 | - | 600 | 3 | 42 | 651 FLA / 5208 LRA | 700 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 600 | 3 | 42 | 651 | 700
|  | OLR | Allen-Bradley | 193-EC*LH | 600 | 3 | 42 | 172-860 | -
AB113D-D860...-E3MD80-..575V_140G-M5_42kA | C | CB | Allen-Bradley | 140G-M5*3-D80 | 600 | 3 | 42 | 800 | - | 600 | 3 | 42 | 651 FLA / 5208 LRA | 700 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 600 | 3 | 42 | 651 | 700
|  | OLR | Allen-Bradley | 193-EC*LH | 600 | 3 | 42 | 172-860 | -
AB113D-C30...-E300EC30-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 200 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C30 | 200 | 3 | 35 | 30 | - | 200 | 3 | 35 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 200 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C30 | 200 | 3 | 25 | 30 | - | 200 | 3 | 25 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 200 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 230 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C30 | 230 | 3 | 35 | 30 | - | 230 | 3 | 35 | 22 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 230 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C30 | 230 | 3 | 25 | 30 | - | 230 | 3 | 25 | 22 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 230 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 480 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C30 | 480 | 3 | 35 | 30 | - | 480 | 3 | 35 | 27 FLA | 20 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 480 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C30 | 480 | 3 | 25 | 30 | - | 480 | 3 | 25 | 27 FLA | 20 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 480 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-C30 | 600 | 3 | 25 | 30 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 600 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..575V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C30 | 600 | 3 | 18 | 30 | - | 600 | 3 | 18 | 27 FLA | 25 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 600 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-C30 | 600 | 3 | 14 | 30 | - | 600 | 3 | 14 | 27 FLA | 25 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 600 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 200 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 200 | 3 | 35 | 50 | - | 200 | 3 | 35 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 200 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 200 | 3 | 25 | 50 | - | 200 | 3 | 25 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 200 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 230 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 230 | 3 | 35 | 50 | - | 230 | 3 | 35 | 28 FLA | 10 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 230 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 230 | 3 | 25 | 50 | - | 230 | 3 | 25 | 28 FLA | 10 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 230 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 480 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 480 | 3 | 35 | 50 | - | 480 | 3 | 35 | 27 FLA | 20 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 480 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 480 | 3 | 25 | 50 | - | 480 | 3 | 25 | 27 FLA | 20 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 480 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 600 | 3 | 25 | 50 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 600 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..575V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 600 | 3 | 18 | 50 | - | 600 | 3 | 18 | 27 FLA | 25 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 600 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 600 | 3 | 14 | 50 | - | 600 | 3 | 14 | 27 FLA | 25 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 600 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..200V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 200 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..200V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C30 | 200 | 3 | 35 | 30 | - | 200 | 3 | 35 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 200 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..200V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C30 | 200 | 3 | 25 | 30 | - | 200 | 3 | 25 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 200 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..230V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 230 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..230V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C30 | 230 | 3 | 35 | 30 | - | 230 | 3 | 35 | 22 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 230 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..230V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C30 | 230 | 3 | 25 | 30 | - | 230 | 3 | 25 | 22 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 230 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..460V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 480 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..460V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C30 | 480 | 3 | 35 | 30 | - | 480 | 3 | 35 | 27 FLA | 20 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 480 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..460V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C30 | 480 | 3 | 25 | 30 | - | 480 | 3 | 25 | 27 FLA | 20 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 480 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..575V_140G-H6_25kA-T | C | CB | Allen-Bradley | 140G-H6*3-C30 | 600 | 3 | 25 | 30 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 600 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..575V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C30 | 600 | 3 | 18 | 30 | - | 600 | 3 | 18 | 27 FLA | 25 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 600 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC30-..575V_140G-H2_14kA-T | C | CB | Allen-Bradley | 140G-H2*3-C30 | 600 | 3 | 14 | 30 | - | 600 | 3 | 14 | 27 FLA | 25 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 600 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..200V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 200 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..200V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C50 | 200 | 3 | 35 | 50 | - | 200 | 3 | 35 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 200 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..200V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C50 | 200 | 3 | 25 | 50 | - | 200 | 3 | 25 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 200 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..230V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 230 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..230V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C50 | 230 | 3 | 35 | 50 | - | 230 | 3 | 35 | 28 FLA | 10 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 230 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..230V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C50 | 230 | 3 | 25 | 50 | - | 230 | 3 | 25 | 28 FLA | 10 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 230 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..460V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 480 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..460V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C50 | 480 | 3 | 35 | 50 | - | 480 | 3 | 35 | 27 FLA | 20 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 480 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..460V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C50 | 480 | 3 | 25 | 50 | - | 480 | 3 | 25 | 27 FLA | 20 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 480 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..575V_140G-H6_25kA-T | C | CB | Allen-Bradley | 140G-H6*3-C50 | 600 | 3 | 25 | 50 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 600 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..575V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C50 | 600 | 3 | 18 | 50 | - | 600 | 3 | 18 | 27 FLA | 25 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 600 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300EC50-..575V_140G-H2_14kA-T | C | CB | Allen-Bradley | 140G-H2*3-C50 | 600 | 3 | 14 | 50 | - | 600 | 3 | 14 | 27 FLA | 25 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 600 | 3 | 5 | 0.5-30 | -
AB113D-C30...-E300FC30-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC30-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C30 | 200 | 3 | 35 | 30 | - | 200 | 3 | 35 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC30-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C30 | 200 | 3 | 25 | 30 | - | 200 | 3 | 25 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC30-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC30-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C30 | 230 | 3 | 35 | 30 | - | 230 | 3 | 35 | 22 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC30-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C30 | 230 | 3 | 25 | 30 | - | 230 | 3 | 25 | 22 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC30-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC30-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C30 | 480 | 3 | 35 | 30 | - | 480 | 3 | 35 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC30-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C30 | 480 | 3 | 25 | 30 | - | 480 | 3 | 25 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC30-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-C30 | 600 | 3 | 25 | 30 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC30-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-C30 | 600 | 3 | 18 | 30 | - | 600 | 3 | 18 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC30-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-C30 | 600 | 3 | 14 | 30 | - | 600 | 3 | 14 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC50-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC50-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 200 | 3 | 35 | 50 | - | 200 | 3 | 35 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC50-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 200 | 3 | 25 | 50 | - | 200 | 3 | 25 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC50-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC50-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 230 | 3 | 35 | 50 | - | 230 | 3 | 35 | 28 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC50-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 230 | 3 | 25 | 50 | - | 230 | 3 | 25 | 28 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC50-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC50-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 480 | 3 | 35 | 50 | - | 480 | 3 | 35 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC50-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 480 | 3 | 25 | 50 | - | 480 | 3 | 25 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC50-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 600 | 3 | 25 | 50 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC50-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 600 | 3 | 18 | 50 | - | 600 | 3 | 18 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC50-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 600 | 3 | 14 | 50 | - | 600 | 3 | 14 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C37...-E300FC50-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C37...-E300FC50-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 200 | 3 | 35 | 50 | - | 200 | 3 | 35 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C37...-E300FC50-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 200 | 3 | 25 | 50 | - | 200 | 3 | 25 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C37...-E300FC50-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C37...-E300FC50-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 230 | 3 | 35 | 50 | - | 230 | 3 | 35 | 28 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C37...-E300FC50-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 230 | 3 | 25 | 50 | - | 230 | 3 | 25 | 28 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C37...-E300FC50-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C37...-E300FC50-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 480 | 3 | 35 | 50 | - | 480 | 3 | 35 | 34 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C37...-E300FC50-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 480 | 3 | 25 | 50 | - | 480 | 3 | 25 | 34 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C37...-E300FC50-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-C50 | 600 | 3 | 25 | 50 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C37...-E300FC50-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-C50 | 600 | 3 | 18 | 50 | - | 600 | 3 | 18 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C37...-E300FC50-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-C50 | 600 | 3 | 14 | 50 | - | 600 | 3 | 14 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C43...-E300FC80-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C43...-E300FC80-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 200 | 3 | 35 | 80 | - | 200 | 3 | 35 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C43...-E300FC80-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 200 | 3 | 25 | 80 | - | 200 | 3 | 25 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C43...-E300FC80-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C43...-E300FC80-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 230 | 3 | 35 | 80 | - | 230 | 3 | 35 | 42 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C43...-E300FC80-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 230 | 3 | 25 | 80 | - | 230 | 3 | 25 | 42 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C43...-E300FC80-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C43...-E300FC80-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 480 | 3 | 35 | 80 | - | 480 | 3 | 35 | 40 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C43...-E300FC80-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 480 | 3 | 25 | 80 | - | 480 | 3 | 25 | 40 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C43...-E300FC80-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C43...-E300FC80-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 600 | 3 | 18 | 80 | - | 600 | 3 | 18 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C43...-E300FC80-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 600 | 3 | 14 | 80 | - | 600 | 3 | 14 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C55...-E300FC80-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C55...-E300FC80-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 200 | 3 | 35 | 80 | - | 200 | 3 | 35 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C55...-E300FC80-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 200 | 3 | 25 | 80 | - | 200 | 3 | 25 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C55...-E300FC80-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C55...-E300FC80-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 230 | 3 | 35 | 80 | - | 230 | 3 | 35 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C55...-E300FC80-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 230 | 3 | 25 | 80 | - | 230 | 3 | 25 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C55...-E300FC80-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C55...-E300FC80-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 480 | 3 | 35 | 80 | - | 480 | 3 | 35 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C55...-E300FC80-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 480 | 3 | 25 | 80 | - | 480 | 3 | 25 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C55...-E300FC80-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C55...-E300FC80-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-C80 | 600 | 3 | 18 | 80 | - | 600 | 3 | 18 | 41 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C55...-E300FC80-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-C80 | 600 | 3 | 14 | 80 | - | 600 | 3 | 14 | 41 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C60...-E300GD12-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C60...-E300GD12-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C60...-E300GD12-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C60...-E300GD12-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C60...-E300GD12-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C60...-E300GD12-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C60...-E300GD12-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C60...-E300GD12-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C60...-E300GD12-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C60...-E300GD12-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C60...-E300GD12-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 600 | 3 | 18 | 125 | - | 600 | 3 | 18 | 52 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C60...-E300GD12-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 600 | 3 | 14 | 125 | - | 600 | 3 | 14 | 52 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C72...-E300GD12-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C72...-E300GD12-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 62.1 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C72...-E300GD12-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 62.1 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C72...-E300GD12-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 68 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C72...-E300GD12-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 68 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C72...-E300GD12-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 68 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C72...-E300GD12-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C72...-E300GD12-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 65 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C72...-E300GD12-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 65 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C72...-E300GD12-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C72...-E300GD12-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 600 | 3 | 18 | 125 | - | 600 | 3 | 18 | 62 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C72...-E300GD12-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 600 | 3 | 14 | 125 | - | 600 | 3 | 14 | 62 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C85...-E300GD12-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C85...-E300GD12-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 78.2 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C85...-E300GD12-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 78.2 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C85...-E300GD12-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C85...-E300GD12-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 80 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C85...-E300GD12-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 80 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C85...-E300GD12-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C85...-E300GD12-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 77 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C85...-E300GD12-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 77 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C85...-E300GD12-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C85...-E300GD12-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 600 | 3 | 18 | 125 | - | 600 | 3 | 18 | 62 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C85...-E300GD12-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 600 | 3 | 14 | 125 | - | 600 | 3 | 14 | 62 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C97...-E300GD12-..200V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C97...-E300GD12-..200V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 92 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C97...-E300GD12-..200V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 92 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C97...-E300GD12-..230V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C97...-E300GD12-..230V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 80 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C97...-E300GD12-..230V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 80 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C97...-E300GD12-..460V_140G-H6_65kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C97...-E300GD12-..460V_140G-H3_35kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 96 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C97...-E300GD12-..460V_140G-H2_25kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 96 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C97...-E300GD12-..575V_140G-H6_25kA | C | CB | Allen-Bradley | 140G-H6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C97...-E300GD12-..575V_140G-H3_18kA | C | CB | Allen-Bradley | 140G-H3*3-D12 | 600 | 3 | 18 | 125 | - | 600 | 3 | 18 | 77 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C97...-E300GD12-..575V_140G-H2_14kA | C | CB | Allen-Bradley | 140G-H2*3-D12 | 600 | 3 | 14 | 125 | - | 600 | 3 | 14 | 77 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C30G...-E300EC30-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300EC30-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C30 | 200 | 3 | 35 | 30 | - | 200 | 3 | 35 | 17.5 FLA | 5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300EC30-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C30 | 200 | 3 | 25 | 30 | - | 200 | 3 | 25 | 17.5 FLA | 5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300EC30-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300EC30-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C30 | 230 | 3 | 35 | 30 | - | 230 | 3 | 35 | 22 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300EC30-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C30 | 230 | 3 | 25 | 30 | - | 230 | 3 | 25 | 22 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300EC30-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300EC30-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C30 | 480 | 3 | 35 | 30 | - | 480 | 3 | 35 | 21 FLA | 15 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300EC30-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C30 | 480 | 3 | 25 | 30 | - | 480 | 3 | 25 | 21 FLA | 15 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300EC30-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-C30 | 600Y/347 | 3 | 25 | 30 | - | 600Y/347 | 3 | 25 | 22 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300EC30-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-C30 | 600Y/347 | 3 | 14 | 30 | - | 600Y/347 | 3 | 14 | 22 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300EC30-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-C30 | 600Y/347 | 3 | 10 | 30 | - | 600Y/347 | 3 | 10 | 22 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300FC50-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300FC50-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 200 | 3 | 35 | 50 | - | 200 | 3 | 35 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300FC50-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 200 | 3 | 25 | 50 | - | 200 | 3 | 25 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300FC50-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300FC50-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 230 | 3 | 35 | 50 | - | 230 | 3 | 35 | 28 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300FC50-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 230 | 3 | 25 | 50 | - | 230 | 3 | 25 | 28 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300FC50-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300FC50-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 480 | 3 | 35 | 50 | - | 480 | 3 | 35 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300FC50-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 480 | 3 | 25 | 50 | - | 480 | 3 | 25 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300FC50-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 600Y/347 | 3 | 25 | 50 | - | 600Y/347 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300FC50-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 600Y/347 | 3 | 14 | 50 | - | 600Y/347 | 3 | 14 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C30G...-E300FC50-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 600Y/347 | 3 | 10 | 50 | - | 600Y/347 | 3 | 10 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C37G...-E300FC50-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C37G...-E300FC50-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 200 | 3 | 35 | 50 | - | 200 | 3 | 35 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C37G...-E300FC50-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 200 | 3 | 25 | 50 | - | 200 | 3 | 25 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C37G...-E300FC50-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C37G...-E300FC50-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 230 | 3 | 35 | 50 | - | 230 | 3 | 35 | 28 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C37G...-E300FC50-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 230 | 3 | 25 | 50 | - | 230 | 3 | 25 | 28 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C37G...-E300FC50-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C37G...-E300FC50-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 480 | 3 | 35 | 50 | - | 480 | 3 | 35 | 34 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C37G...-E300FC50-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 480 | 3 | 25 | 50 | - | 480 | 3 | 25 | 34 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C37G...-E300FC50-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-C50 | 600Y/347 | 3 | 25 | 50 | - | 600Y/347 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C37G...-E300FC50-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-C50 | 600Y/347 | 3 | 14 | 50 | - | 600Y/347 | 3 | 14 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C37G...-E300FC50-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-C50 | 600Y/347 | 3 | 10 | 50 | - | 600Y/347 | 3 | 10 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C43G...-E300FC50-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C43G...-E300FC50-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 200 | 3 | 35 | 80 | - | 200 | 3 | 35 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C43G...-E300FC50-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 200 | 3 | 25 | 80 | - | 200 | 3 | 25 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C43G...-E300FC50-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C43G...-E300FC50-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 230 | 3 | 35 | 80 | - | 230 | 3 | 35 | 42 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C43G...-E300FC50-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 230 | 3 | 25 | 80 | - | 230 | 3 | 25 | 42 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C43G...-E300FC50-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C43G...-E300FC50-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 480 | 3 | 35 | 80 | - | 480 | 3 | 35 | 40 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C43G...-E300FC50-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 480 | 3 | 25 | 80 | - | 480 | 3 | 25 | 40 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C43G...-E300FC50-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 600Y/347 | 3 | 25 | 80 | - | 600Y/347 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C43G...-E300FC50-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 600Y/347 | 3 | 14 | 80 | - | 600Y/347 | 3 | 14 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C43G...-E300FC50-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 600Y/347 | 3 | 10 | 80 | - | 600Y/347 | 3 | 10 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C55G...-E300FC80-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C55G...-E300FC80-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 200 | 3 | 35 | 80 | - | 200 | 3 | 35 | 48.3 FLA | 15 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C55G...-E300FC80-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 200 | 3 | 25 | 80 | - | 200 | 3 | 25 | 48.3 FLA | 15 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C55G...-E300FC80-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C55G...-E300FC80-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 230 | 3 | 35 | 80 | - | 230 | 3 | 35 | 54 FLA | 20 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C55G...-E300FC80-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 230 | 3 | 25 | 80 | - | 230 | 3 | 25 | 54 FLA | 20 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C55G...-E300FC80-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C55G...-E300FC80-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-C80 | 480 | 3 | 35 | 80 | - | 480 | 3 | 35 | 52 FLA | 40 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C55G...-E300FC80-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-C80 | 480 | 3 | 25 | 80 | - | 480 | 3 | 25 | 52 FLA | 40 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C60G...-E300GD12-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C60G...-E300GD12-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C60G...-E300GD12-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C60G...-E300GD12-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C60G...-E300GD12-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C60G...-E300GD12-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C60G...-E300GD12-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C60G...-E300GD12-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C60G...-E300GD12-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C60G...-E300GD12-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 600Y/347 | 3 | 25 | 125 | - | 600Y/347 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C60G...-E300GD12-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 600Y/347 | 3 | 14 | 125 | - | 600Y/347 | 3 | 14 | 52 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C60G...-E300GD12-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 600Y/347 | 3 | 10 | 125 | - | 600Y/347 | 3 | 10 | 52 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C72G...-E300GD12-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C72G...-E300GD12-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 62.1 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C72G...-E300GD12-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 62.1 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C72G...-E300GD12-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 68 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C72G...-E300GD12-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 68 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C72G...-E300GD12-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 68 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C72G...-E300GD12-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C72G...-E300GD12-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 65 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C72G...-E300GD12-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 65 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C72G...-E300GD12-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 600Y/347 | 3 | 25 | 125 | - | 600Y/347 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C72G...-E300GD12-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 600Y/347 | 3 | 14 | 125 | - | 600Y/347 | 3 | 14 | 62 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C72G...-E300GD12-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 600Y/347 | 3 | 10 | 125 | - | 600Y/347 | 3 | 10 | 62 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C85G...-E300GD12-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C85G...-E300GD12-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 78.2 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C85G...-E300GD12-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 78.2 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C85G...-E300GD12-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C85G...-E300GD12-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 80 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C85G...-E300GD12-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 80 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C85G...-E300GD12-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C85G...-E300GD12-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 77 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C85G...-E300GD12-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 77 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C85G...-E300GD12-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 600Y/347 | 3 | 25 | 125 | - | 600Y/347 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C85G...-E300GD12-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 600Y/347 | 3 | 14 | 125 | - | 600Y/347 | 3 | 14 | 62 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C85G...-E300GD12-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 600Y/347 | 3 | 10 | 125 | - | 600Y/347 | 3 | 10 | 62 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C97G...-E300VD12-..200V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C97G...-E300VD12-..200V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 200 | 3 | 35 | 125 | - | 200 | 3 | 35 | 92 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C97G...-E300GD12-..200V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 200 | 3 | 25 | 125 | - | 200 | 3 | 25 | 92 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C97G...-E300GD12-..230V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C97G...-E300GD12-..230V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 230 | 3 | 35 | 125 | - | 230 | 3 | 35 | 80 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C97G...-E300GD12-..230V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 230 | 3 | 25 | 125 | - | 230 | 3 | 25 | 80 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C97G...-E300GD12-..460V_140G-G6_65kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C97G...-E300GD12-..460V_140G-G3_35kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 480 | 3 | 35 | 125 | - | 480 | 3 | 35 | 96 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C97G...-E300GD12-..460V_140G-G2_25kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 480 | 3 | 25 | 125 | - | 480 | 3 | 25 | 96 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C97G...-E300GD12-..575V_140G-G6_25kA | C | CB | Allen-Bradley | 140G-G6*3-D12 | 600Y/347 | 3 | 25 | 125 | - | 600Y/347 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C97G...-E300GD12-..575V_140G-G3_14kA | C | CB | Allen-Bradley | 140G-G3*3-D12 | 600Y/347 | 3 | 14 | 125 | - | 600Y/347 | 3 | 14 | 77 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C97G...-E300GD12-..575V_140G-G2_10kA | C | CB | Allen-Bradley | 140G-G2*3-D12 | 600Y/347 | 3 | 10 | 125 | - | 600Y/347 | 3 | 10 | 77 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C30...-E300FC30-..200V_140G-HC6_65KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC30-..230V_140G-HC6_65KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC30-..460V_140G-HC6_65KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC30-..575V_140G-HC6_25KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C30 | 600 | 3 | 25 | 30 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC50-..200V_140G-HC6_65KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC50-..230V_140G-HC6_65KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC50-..460V_140G-HC6_65KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC50-..575V_140G-HC6_25KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 600 | 3 | 25 | 50 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C37...-E300FC50-..200V_140G-HC6_65KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C37...-E300FC50-..230V_140G-HC6_65KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C37...-E300FC50-..460V_140G-HC6_65KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C37...-E300FC50-..575V_140G-HC6_25KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 600 | 3 | 25 | 50 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C43...-E300FC80-..200V_140G-HC6_65KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C43...-E300FC80-..230V_140G-HC6_65KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C43...-E300FC80-..460V_140G-HC6_65KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C43...-E300FC80-..575V_140G-HC6_25KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C55...-E300GC80-..200V_140G-HC6_65KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C55...-E300GC80-..230V_140G-HC6_65KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C55...-E300GC80-..460V_140G-HC6_65KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C55...-E300GC80-..575V_140G-HC6_25KCA-T | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C30...-E300EC30-..200V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C30...-E300EC30-..200V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C30 | 200 | 3 | 35 | 30 | - | 200 | 3 | 35 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C30...-E300EC30-..200V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C30 | 200 | 3 | 25 | 30 | - | 200 | 3 | 25 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C30...-E300EC30-..230V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C30...-E300EC30-..230V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C30 | 230 | 3 | 35 | 30 | - | 230 | 3 | 35 | 22 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C30...-E300EC30-..230V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C30 | 230 | 3 | 25 | 30 | - | 230 | 3 | 25 | 22 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C30...-E300EC30-..460V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C30...-E300EC30-..460V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C30 | 480 | 3 | 35 | 30 | - | 480 | 3 | 35 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C30...-E300EC30-..460V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C30 | 480 | 3 | 25 | 30 | - | 480 | 3 | 25 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C30...-E300EC30-..575V_140G-H6_25kA-T | C | CB | Allen-Bradley | 140G-H6*3-C30 | 600 | 3 | 25 | 30 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C30...-E300EC30-..575V_140G-H3_18kA-T | C | CB | Allen-Bradley | 140G-H3*3-C30 | 600 | 3 | 18 | 30 | - | 600 | 3 | 18 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C30...-E300EC30-..575V_140G-H2_14kA-T | C | CB | Allen-Bradley | 140G-H2*3-C30 | 600 | 3 | 14 | 30 | - | 600 | 3 | 14 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC50-..200V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC50-..200V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C50 | 200 | 3 | 35 | 50 | - | 200 | 3 | 35 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC50-..200V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C50 | 200 | 3 | 25 | 50 | - | 200 | 3 | 25 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC50-..230V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC50-..230V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C50 | 230 | 3 | 35 | 50 | - | 230 | 3 | 35 | 28 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC50-..230V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C50 | 230 | 3 | 25 | 50 | - | 230 | 3 | 25 | 28 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC50-..460V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC50-..460V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C50 | 480 | 3 | 35 | 50 | - | 480 | 3 | 35 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC50-..460V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C50 | 480 | 3 | 25 | 50 | - | 480 | 3 | 25 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC50-..575V_140G-H6_25kA-T | C | CB | Allen-Bradley | 140G-H6*3-C50 | 600 | 3 | 25 | 50 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC50-..575V_140G-H3_18kA-T | C | CB | Allen-Bradley | 140G-H3*3-C50 | 600 | 3 | 18 | 50 | - | 600 | 3 | 18 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C30...-E300FC50-..575V_140G-H2_14kA-T | C | CB | Allen-Bradley | 140G-H2*3-C50 | 600 | 3 | 14 | 50 | - | 600 | 3 | 14 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C37...-E300FC50-..200V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C37...-E300FC50-..200V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C50 | 200 | 3 | 35 | 50 | - | 200 | 3 | 35 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C37...-E300FC50-..200V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C50 | 200 | 3 | 25 | 50 | - | 200 | 3 | 25 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C37...-E300FC50-..230V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C37...-E300FC50-..230V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C50 | 230 | 3 | 35 | 50 | - | 230 | 3 | 35 | 28 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C37...-E300FC50-..230V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C50 | 230 | 3 | 25 | 50 | - | 230 | 3 | 25 | 28 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C37...-E300FC50-..460V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C37...-E300FC50-..460V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C50 | 480 | 3 | 35 | 50 | - | 480 | 3 | 35 | 34 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C37...-E300FC50-..460V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C50 | 480 | 3 | 25 | 50 | - | 480 | 3 | 25 | 34 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C37...-E300FC50-..575V_140G-H6_25kA-T | C | CB | Allen-Bradley | 140G-H6*3-C50 | 600 | 3 | 25 | 50 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C37...-E300FC50-..575V_140G-H3_18kA-T | C | CB | Allen-Bradley | 140G-H3*3-C50 | 600 | 3 | 18 | 50 | - | 600 | 3 | 18 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C37...-E300FC50-..575V_140G-H2_14kA-T | C | CB | Allen-Bradley | 140G-H2*3-C50 | 600 | 3 | 14 | 50 | - | 600 | 3 | 14 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C43...-E300FC80-..200V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C43...-E300FC80-..200V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C80 | 200 | 3 | 35 | 80 | - | 200 | 3 | 35 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C43...-E300FC80-..200V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C80 | 200 | 3 | 25 | 80 | - | 200 | 3 | 25 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C43...-E300FC80-..230V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C43...-E300FC80-..230V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C80 | 230 | 3 | 35 | 80 | - | 230 | 3 | 35 | 42 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C43...-E300FC80-..230V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C80 | 230 | 3 | 25 | 80 | - | 230 | 3 | 25 | 42 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C43...-E300FC80-..460V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C43...-E300FC80-..460V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C80 | 480 | 3 | 35 | 80 | - | 480 | 3 | 35 | 40 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C43...-E300FC80-..460V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C80 | 480 | 3 | 25 | 80 | - | 480 | 3 | 25 | 40 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C43...-E300FC80-..575V_140G-H6_25kA-T | C | CB | Allen-Bradley | 140G-H6*3-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C43...-E300FC80-..575V_140G-H3_18kA-T | C | CB | Allen-Bradley | 140G-H3*3-C80 | 600 | 3 | 18 | 80 | - | 600 | 3 | 18 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C43...-E300FC80-..575V_140G-H2_14kA-T | C | CB | Allen-Bradley | 140G-H2*3-C80 | 600 | 3 | 14 | 80 | - | 600 | 3 | 14 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C55...-E300GC80-..200V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C55...-E300GC80-..200V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C80 | 200 | 3 | 35 | 80 | - | 200 | 3 | 35 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C55...-E300GC80-..200V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C80 | 200 | 3 | 25 | 80 | - | 200 | 3 | 25 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C55...-E300GC80-..230V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C55...-E300GC80-..230V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C80 | 230 | 3 | 35 | 80 | - | 230 | 3 | 35 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C55...-E300GC80-..230V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C80 | 230 | 3 | 25 | 80 | - | 230 | 3 | 25 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C55...-E300GC80-..460V_140G-H6_65kA-T | C | CB | Allen-Bradley | 140G-H6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C55...-E300GC80-..460V_140G-H3_35kA-T | C | CB | Allen-Bradley | 140G-H3*3-C80 | 480 | 3 | 35 | 80 | - | 480 | 3 | 35 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C55...-E300GC80-..460V_140G-H2_25kA-T | C | CB | Allen-Bradley | 140G-H2*3-C80 | 480 | 3 | 25 | 80 | - | 480 | 3 | 25 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C55...-E300GC80-..575V_140G-H6_25kA-T | C | CB | Allen-Bradley | 140G-H6*3-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C55...-E300GC80-..575V_140G-H3_18kA-T | C | CB | Allen-Bradley | 140G-H3*3-C80 | 600 | 3 | 18 | 80 | - | 600 | 3 | 18 | 41 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C55...-E300GC80-..575V_140G-H2_14kA-T | C | CB | Allen-Bradley | 140G-H2*3-C80 | 600 | 3 | 14 | 80 | - | 600 | 3 | 14 | 41 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC30-..200V_140G-G6_65kA-T | C | CB | Allen-Bradley | 140G-G6*3-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC30-..200V_140G-G3_35kA-T | C | CB | Allen-Bradley | 140G-G3*3-C30 | 200 | 3 | 35 | 30 | - | 200 | 3 | 35 | 17.5 FLA | 5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC30-..200V_140G-G2_25kA-T | C | CB | Allen-Bradley | 140G-G2*3-C30 | 200 | 3 | 25 | 30 | - | 200 | 3 | 25 | 17.5 FLA | 5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC30-..230V_140G-G6_65kA-T | C | CB | Allen-Bradley | 140G-G6*3-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC30-..230V_140G-G3_35kA-T | C | CB | Allen-Bradley | 140G-G3*3-C30 | 230 | 3 | 35 | 30 | - | 230 | 3 | 35 | 22 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC30-..230V_140G-G2_25kA-T | C | CB | Allen-Bradley | 140G-G2*3-C30 | 230 | 3 | 25 | 30 | - | 230 | 3 | 25 | 22 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC30-..460V_140G-G6_65kA-T | C | CB | Allen-Bradley | 140G-G6*3-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC30-..460V_140G-G3_35kA-T | C | CB | Allen-Bradley | 140G-G3*3-C30 | 480 | 3 | 35 | 30 | - | 480 | 3 | 35 | 21 FLA | 15 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC30-..460V_140G-G2_25kA-T | C | CB | Allen-Bradley | 140G-G2*3-C30 | 480 | 3 | 25 | 30 | - | 480 | 3 | 25 | 21 FLA | 15 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC30-..575V_140G-G6_25kA-T | C | CB | Allen-Bradley | 140G-G6*3-C30 | 600Y/347 | 3 | 25 | 30 | - | 600Y/347 | 3 | 25 | 22 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC30-..575V_140G-G3_14kA-T | C | CB | Allen-Bradley | 140G-G3*3-C30 | 600Y/347 | 3 | 14 | 30 | - | 600Y/347 | 3 | 14 | 22 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC30-..575V_140G-G2_10kA-T | C | CB | Allen-Bradley | 140G-G2*3-C30 | 600Y/347 | 3 | 10 | 30 | - | 600Y/347 | 3 | 10 | 22 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC50-..200V_140G-G6_65kA-T | C | CB | Allen-Bradley | 140G-G6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC50-..200V_140G-G3_35kA-T | C | CB | Allen-Bradley | 140G-G3*3-C50 | 200 | 3 | 35 | 50 | - | 200 | 3 | 35 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC50-..200V_140G-G2_25kA-T | C | CB | Allen-Bradley | 140G-G2*3-C50 | 200 | 3 | 25 | 50 | - | 200 | 3 | 25 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC50-..230V_140G-G6_65kA-T | C | CB | Allen-Bradley | 140G-G6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC50-..230V_140G-G3_35kA-T | C | CB | Allen-Bradley | 140G-G3*3-C50 | 230 | 3 | 35 | 50 | - | 230 | 3 | 35 | 28 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC50-..230V_140G-G2_25kA-T | C | CB | Allen-Bradley | 140G-G2*3-C50 | 230 | 3 | 25 | 50 | - | 230 | 3 | 25 | 28 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC50-..460V_140G-G6_65kA-T | C | CB | Allen-Bradley | 140G-G6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC50-..460V_140G-G3_35kA-T | C | CB | Allen-Bradley | 140G-G3*3-C50 | 480 | 3 | 35 | 50 | - | 480 | 3 | 35 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC50-..460V_140G-G2_25kA-T | C | CB | Allen-Bradley | 140G-G2*3-C50 | 480 | 3 | 25 | 50 | - | 480 | 3 | 25 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC50-..575V_140G-G6_25kA-T | C | CB | Allen-Bradley | 140G-G6*3-C50 | 600Y/347 | 3 | 25 | 50 | - | 600Y/347 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC50-..575V_140G-G3_14kA-T | C | CB | Allen-Bradley | 140G-G3*3-C50 | 600Y/347 | 3 | 14 | 50 | - | 600Y/347 | 3 | 14 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C30G...-E300FC50-..575V_140G-G2_10kA-T | C | CB | Allen-Bradley | 140G-G2*3-C50 | 600Y/347 | 3 | 10 | 50 | - | 600Y/347 | 3 | 10 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C37G...-E300FC50-..200V_140G-G6_65kA-T | C | CB | Allen-Bradley | 140G-G6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C37G...-E300FC50-..200V_140G-G3_35kA-T | C | CB | Allen-Bradley | 140G-G3*3-C50 | 200 | 3 | 35 | 50 | - | 200 | 3 | 35 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C37G...-E300FC50-..200V_140G-G2_25kA-T | C | CB | Allen-Bradley | 140G-G2*3-C50 | 200 | 3 | 25 | 50 | - | 200 | 3 | 25 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C37G...-E300FC50-..230V_140G-G6_65kA-T | C | CB | Allen-Bradley | 140G-G6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C37G...-E300FC50-..230V_140G-G3_35kA-T | C | CB | Allen-Bradley | 140G-G3*3-C50 | 230 | 3 | 35 | 50 | - | 230 | 3 | 35 | 28 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C37G...-E300FC50-..230V_140G-G2_25kA-T | C | CB | Allen-Bradley | 140G-G2*3-C50 | 230 | 3 | 25 | 50 | - | 230 | 3 | 25 | 28 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C37G...-E300FC50-..460V_140G-G6_65kA-T | C | CB | Allen-Bradley | 140G-G6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C37G...-E300FC50-..460V_140G-G3_35kA-T | C | CB | Allen-Bradley | 140G-G3*3-C50 | 480 | 3 | 35 | 50 | - | 480 | 3 | 35 | 34 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C37G...-E300FC50-..460V_140G-G2_25kA-T | C | CB | Allen-Bradley | 140G-G2*3-C50 | 480 | 3 | 25 | 50 | - | 480 | 3 | 25 | 34 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C37G...-E300FC50-..575V_140G-G6_25kA-T | C | CB | Allen-Bradley | 140G-G6*3-C50 | 600Y/347 | 3 | 25 | 50 | - | 600Y/347 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C37G...-E300FC50-..575V_140G-G3_14kA-T | C | CB | Allen-Bradley | 140G-G3*3-C50 | 600Y/347 | 3 | 14 | 50 | - | 600Y/347 | 3 | 14 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C37G...-E300FC50-..575V_140G-G2_10kA-T | C | CB | Allen-Bradley | 140G-G2*3-C50 | 600Y/347 | 3 | 10 | 50 | - | 600Y/347 | 3 | 10 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C43G...-E300FC50-..200V_140G-G6_65kA-T | C | CB | Allen-Bradley | 140G-G6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C43G...-E300FC50-..200V_140G-G3_35kA-T | C | CB | Allen-Bradley | 140G-G3*3-C80 | 200 | 3 | 35 | 80 | - | 200 | 3 | 35 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C43G...-E300FC50-..200V_140G-G2_25kA-T | C | CB | Allen-Bradley | 140G-G2*3-C80 | 200 | 3 | 25 | 80 | - | 200 | 3 | 25 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C43G...-E300FC50-..230V_140G-G6_65kA-T | C | CB | Allen-Bradley | 140G-G6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C43G...-E300FC50-..230V_140G-G3_35kA-T | C | CB | Allen-Bradley | 140G-G3*3-C80 | 230 | 3 | 35 | 80 | - | 230 | 3 | 35 | 42 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C43G...-E300FC50-..230V_140G-G2_25kA-T | C | CB | Allen-Bradley | 140G-G2*3-C80 | 230 | 3 | 25 | 80 | - | 230 | 3 | 25 | 42 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C43G...-E300FC50-..460V_140G-G6_65kA-T | C | CB | Allen-Bradley | 140G-G6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C43G...-E300FC50-..460V_140G-G3_35kA-T | C | CB | Allen-Bradley | 140G-G3*3-C80 | 480 | 3 | 35 | 80 | - | 480 | 3 | 35 | 40 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C43G...-E300FC50-..460V_140G-G2_25kA-T | C | CB | Allen-Bradley | 140G-G2*3-C80 | 480 | 3 | 25 | 80 | - | 480 | 3 | 25 | 40 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C43G...-E300FC50-..575V_140G-G6_25kA-T | C | CB | Allen-Bradley | 140G-G6*3-C80 | 600Y/347 | 3 | 25 | 80 | - | 600Y/347 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C43G...-E300FC50-..575V_140G-G3_14kA-T | C | CB | Allen-Bradley | 140G-G3*3-C80 | 600Y/347 | 3 | 14 | 80 | - | 600Y/347 | 3 | 14 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C43G...-E300FC50-..575V_140G-G2_10kA-T | C | CB | Allen-Bradley | 140G-G2*3-C80 | 600Y/347 | 3 | 10 | 80 | - | 600Y/347 | 3 | 10 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113D-C55G...-E300GC80-..200V_140G-G6_65kA-T | C | CB | Allen-Bradley | 140G-G6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C55G...-E300GC80-..200V_140G-G3_35kA-T | C | CB | Allen-Bradley | 140G-G3*3-C80 | 200 | 3 | 35 | 80 | - | 200 | 3 | 35 | 48.3 FLA | 15 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C55G...-E300GC80-..200V_140G-G2_25kA-T | C | CB | Allen-Bradley | 140G-G2*3-C80 | 200 | 3 | 25 | 80 | - | 200 | 3 | 25 | 48.3 FLA | 15 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113D-C55G...-E300GC80-..230V_140G-G6_65kA-T | C | CB | Allen-Bradley | 140G-G6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C55G...-E300GC80-..230V_140G-G3_35kA-T | C | CB | Allen-Bradley | 140G-G3*3-C80 | 230 | 3 | 35 | 80 | - | 230 | 3 | 35 | 54 FLA | 20 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C55G...-E300GC80-..230V_140G-G2_25kA-T | C | CB | Allen-Bradley | 140G-G2*3-C80 | 230 | 3 | 25 | 80 | - | 230 | 3 | 25 | 54 FLA | 20 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113D-C55G...-E300GC80-..460V_140G-G6_65kA-T | C | CB | Allen-Bradley | 140G-G6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C55G...-E300GC80-..460V_140G-G3_35kA-T | C | CB | Allen-Bradley | 140G-G3*3-C80 | 480 | 3 | 35 | 80 | - | 480 | 3 | 35 | 52 FLA | 40 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C55G...-E300GC80-..460V_140G-G2_25kA-T | C | CB | Allen-Bradley | 140G-G2*3-C80 | 480 | 3 | 25 | 80 | - | 480 | 3 | 25 | 52 FLA | 40 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113D-C30...-E1FC30-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC30-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC30-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC30-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-C30 | 600 | 3 | 25 | 30 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC50-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC50-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC50-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C30...-E1FC50-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 600 | 3 | 25 | 50 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C37...-E1FC50-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C37...-E1FC50-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C37...-E1FC50-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C37...-E1FC50-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 600 | 3 | 25 | 50 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C43...-E1FC80-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113D-C43...-E1FC80-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113D-C43...-E1FC80-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113D-C43...-E1FC80-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113D-C55...-E1GC80-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 5 | 18-90 | -
AB113D-C55...-E1GC80-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 5 | 18-90 | -
AB113D-C55...-E1GC80-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 5 | 18-90 | -
AB113D-C55...-E1GC80-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 5 | 18-90 | -
AB113D-C60...-E1GD12-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C60...-E1GD12-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C60...-E1GD12-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C60...-E1GD12-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C72...-E1GD12-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C72...-E1GD12-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 68 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C72...-E1GD12-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C72...-E1GD12-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C85...-E1GD12-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113D-C85...-E1GD12-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113D-C85...-E1GD12-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113D-C85...-E1GD12-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113D-C97...-E1VD12-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EEVE | 200 | 3 | 10 | 60-120 | -
AB113D-C97...-E1VD12-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EEVE | 230 | 3 | 10 | 60-120 | -
AB113D-C97...-E1VD12-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EEVE | 480 | 3 | 10 | 60-120 | -
AB113D-C97...-E1VD12-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-EEVE | 600 | 3 | 10 | 60-120 | -
AB113D-D115...-E1HCD25-..200V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 92 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EEHF | 200 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HCD25-..230V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 104 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-EEHF | 230 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HCD25-..460V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 96 FLA | 75 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EEHF | 480 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HCD25-..575V_140G-JC6_25KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 99 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-EEHF | 600 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HCD25-..200V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 120 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-EEHF | 200 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HCD25-..230V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 130 FLA | 50 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-EEHF | 230 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HCD25-..460V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 124 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-EEHF | 480 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HCD25-..575V_140G-JC6_25KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 125 FLA | 125 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-EEHF | 600 | 3 | 10 | 30-150 | -
AB113D-D180...-E1JCD25-..200V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 150 FLA | 50 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 200 | 3 | 10 | 150 | 50
|  | OLR | Allen-Bradley | 193-EEJF | 200 | 3 | 10 | 40-200 | -
AB113D-D180...-E1JCD25-..230V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 154 FLA | 60 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 230 | 3 | 10 | 154 | 60
|  | OLR | Allen-Bradley | 193-EEJF | 230 | 3 | 10 | 40-200 | -
AB113D-D180...-E1JCD25-..460V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 180 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 480 | 3 | 10 | 180 | 150
|  | OLR | Allen-Bradley | 193-EEJF | 480 | 3 | 10 | 40-200 | -
AB113D-D180...-E1JCD25-..575V_140G-JC6_25KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 144 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 600 | 3 | 10 | 144 | 150
|  | OLR | Allen-Bradley | 193-EEJF | 600 | 3 | 10 | 40-200 | -
AB113D-D210...-E1KCD40-..200V_140G-KC6_65KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 200 | 3 | 65 | 400 | - | 200 | 3 | 65 | 177 FLA | 60 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 200 | 3 | 18 | 177 | 60
|  | OLR | Allen-Bradley | 193-EEKG | 200 | 3 | 18 | 60-300 | -
AB113D-D210...-E1KCD40-..230V_140G-KC6_65KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 230 | 3 | 65 | 400 | - | 230 | 3 | 65 | 192 FLA | 75 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 230 | 3 | 18 | 192 | 75
|  | OLR | Allen-Bradley | 193-EEKG | 230 | 3 | 18 | 60-300 | -
AB113D-D210...-E1KCD40-..460V_140G-KC6_65KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 480 | 3 | 65 | 400 | - | 480 | 3 | 65 | 180 FLA | 150 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 480 | 3 | 18 | 180 | 150
|  | OLR | Allen-Bradley | 193-EEKG | 480 | 3 | 18 | 60-300 | -
AB113D-D210...-E1KCD40-..575V_140G-KC6_30KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 600 | 3 | 30 | 400 | - | 600 | 3 | 30 | 192 FLA | 200 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 600 | 3 | 18 | 192 | 200
|  | OLR | Allen-Bradley | 193-EEKG | 600 | 3 | 18 | 60-300 | -
AB113D-D250...-E1KCD40-..200V_140G-KC6_65KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 200 | 3 | 65 | 400 | - | 200 | 3 | 65 | 221 FLA | 75 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 200 | 3 | 18 | 221 | 75
|  | OLR | Allen-Bradley | 193-EEKG | 200 | 3 | 18 | 60-300 | -
AB113D-D250...-E1KCD40-..230V_140G-KC6_65KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 230 | 3 | 65 | 400 | - | 230 | 3 | 65 | 248 FLA | 100 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 230 | 3 | 18 | 248 | 100
|  | OLR | Allen-Bradley | 193-EEKG | 230 | 3 | 18 | 60-300 | -
AB113D-D250...-E1KCD40-..460V_140G-KC6_65KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 480 | 3 | 65 | 400 | - | 480 | 3 | 65 | 240 FLA | 200 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 480 | 3 | 18 | 240 | 200
|  | OLR | Allen-Bradley | 193-EEKG | 480 | 3 | 18 | 60-300 | -
AB113D-D250...-E1KCD40-..575V_140G-KC6_30KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 600 | 3 | 30 | 400 | - | 600 | 3 | 30 | 242 FLA | 250 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 600 | 3 | 18 | 242 | 250
|  | OLR | Allen-Bradley | 193-EEKG | 600 | 3 | 18 | 60-300 | -
AB113D-D300...-E1KCD40-..200V_140G-KC6_65KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 200 | 3 | 65 | 400 | - | 200 | 3 | 65 | 285 FLA | 100 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 200 | 3 | 18 | 285 | 100
|  | OLR | Allen-Bradley | 193-EELG | 200 | 3 | 18 | 100-500 | -
AB113D-D300...-E1KCD40-..230V_140G-KC6_65KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 230 | 3 | 65 | 400 | - | 230 | 3 | 65 | 312 FLA | 125 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 230 | 3 | 18 | 312 | 125
|  | OLR | Allen-Bradley | 193-EELG | 230 | 3 | 18 | 100-500 | -
AB113D-D300...-E1KCD40-..460V_140G-KC6_65KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 480 | 3 | 65 | 400 | - | 480 | 3 | 65 | 302 FLA | 250 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 480 | 3 | 18 | 302 | 250
|  | OLR | Allen-Bradley | 193-EELG | 480 | 3 | 18 | 100-500 | -
AB113D-D300...-E1KCD40-..575V_140G-KC6_30KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 600 | 3 | 30 | 400 | - | 600 | 3 | 30 | 289 FLA | 300 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 600 | 3 | 18 | 289 | 300
|  | OLR | Allen-Bradley | 193-EELG | 600 | 3 | 18 | 100-500 | -
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number [1] | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP rating | Enclosure Volume, CU inches
AB113D-C30...-E3EC30-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C30...-E3EC30-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C30...-E3EC30-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C30...-E3EC30-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-C30 | 600 | 3 | 25 | 30 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C30...-E3FC50-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C30...-E3FC50-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C30...-E3FC50-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C30...-E3FC50-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 600 | 3 | 25 | 50 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C37...-E3FC50-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C37...-E3FC50-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C37...-E3FC50-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C37...-E3FC50-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 600 | 3 | 25 | 50 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C43...-E3FC80-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113D-C43...-E3FC80-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113D-C43...-E3FC80-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113D-C43...-E3FC80-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113D-C55...-E3GC80-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 5 | 18-90 | -
AB113D-C55...-E3GC80-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 5 | 18-90 | -
AB113D-C55...-E3GC80-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 5 | 18-90 | -
AB113D-C55...-E3GC80-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 5 | 18-90 | -
AB113D-C60...-E3GD12-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C60...-E3GD12-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C60...-E3GD12-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C60...-E3GD12-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C72...-E3GD12-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C72...-E3GD12-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 68 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C72...-E3GD12-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C72...-E3GD12-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C85...-E3GD12-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113D-C85...-E3GD12-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113D-C85...-E3GD12-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113D-C85...-E3GD12-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113D-C97...-E3VD12-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-C97...-E3VD12-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-C97...-E3VD12-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-C97...-E3VD12-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HCD25-..200V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 92 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HCD25-..230V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 104 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HCD25-..460V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 96 FLA | 75 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HCD25-..575V_140G-JC6_25KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 99 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HCD25-..200V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 120 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HCD25-..230V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 130 FLA | 50 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HCD25-..460V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 124 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HCD25-..575V_140G-JC6_25KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 125 FLA | 125 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-D180...-E3JCD25-..200V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 150 FLA | 50 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 200 | 3 | 10 | 150 | 50
|  | OLR | Allen-Bradley | 193-EC*GF | 200 | 3 | 10 | 42-210 | -
AB113D-D180...-E3JCD25-..230V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 154 FLA | 60 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 230 | 3 | 10 | 154 | 60
|  | OLR | Allen-Bradley | 193-EC*GF | 230 | 3 | 10 | 42-210 | -
AB113D-D180...-E3JCD25-..460V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 180 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 480 | 3 | 10 | 180 | 150
|  | OLR | Allen-Bradley | 193-EC*GF | 480 | 3 | 10 | 42-210 | -
AB113D-D180...-E3JCD25-..575V_140G-JC6_25KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 144 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 600 | 3 | 10 | 144 | 150
|  | OLR | Allen-Bradley | 193-EC*GF | 600 | 3 | 10 | 42-210 | -
AB113D-D210...-E3KCD40-..200V_140G-KC6_65KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 200 | 3 | 65 | 400 | - | 200 | 3 | 65 | 177 FLA | 60 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 200 | 3 | 18 | 177 | 60
|  | OLR | Allen-Bradley | 193-EC*HG | 200 | 3 | 18 | 60-302 | -
AB113D-D210...-E3KCD40-..230V_140G-KC6_65KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 230 | 3 | 65 | 400 | - | 230 | 3 | 65 | 192 FLA | 75 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 230 | 3 | 18 | 192 | 75
|  | OLR | Allen-Bradley | 193-EC*HG | 230 | 3 | 18 | 60-302 | -
AB113D-D210...-E3KCD40-..460V_140G-KC6_65KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 480 | 3 | 65 | 400 | - | 480 | 3 | 65 | 180 FLA | 150 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 480 | 3 | 18 | 180 | 150
|  | OLR | Allen-Bradley | 193-EC*HG | 480 | 3 | 18 | 60-302 | -
AB113D-D210...-E3KCD40-..575V_140G-KC6_30KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 600 | 3 | 30 | 400 | - | 600 | 3 | 30 | 192 FLA | 200 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 600 | 3 | 18 | 192 | 200
|  | OLR | Allen-Bradley | 193-EC*HG | 600 | 3 | 18 | 60-302 | -
AB113D-D250...-E3KCD40-..200V_140G-KC6_65KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 200 | 3 | 65 | 400 | - | 200 | 3 | 65 | 221 FLA | 75 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 200 | 3 | 18 | 221 | 75
|  | OLR | Allen-Bradley | 193-EC*HG | 200 | 3 | 18 | 60-302 | -
AB113D-D250...-E3KCD40-..230V_140G-KC6_65KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 230 | 3 | 65 | 400 | - | 230 | 3 | 65 | 248 FLA | 100 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 230 | 3 | 18 | 248 | 100
|  | OLR | Allen-Bradley | 193-EC*HG | 230 | 3 | 18 | 60-302 | -
AB113D-D250...-E3KCD40-..460V_140G-KC6_65KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 480 | 3 | 65 | 400 | - | 480 | 3 | 65 | 240 FLA | 200 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 480 | 3 | 18 | 240 | 200
|  | OLR | Allen-Bradley | 193-EC*HG | 480 | 3 | 18 | 60-302 | -
AB113D-D250...-E3KCD40-..575V_140G-KC6_30KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 600 | 3 | 30 | 400 | - | 600 | 3 | 30 | 242 FLA | 250 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 600 | 3 | 18 | 242 | 250
|  | OLR | Allen-Bradley | 193-EC*HG | 600 | 3 | 18 | 60-302 | -
AB113D-D300...-E3KCD40-..200V_140G-KC6_65KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 200 | 3 | 65 | 400 | - | 200 | 3 | 65 | 285 FLA | 100 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 200 | 3 | 18 | 285 | 100
|  | OLR | Allen-Bradley | 193-EC*JG | 200 | 3 | 18 | 84-420 | -
AB113D-D300...-E3KCD40-..230V_140G-KC6_65KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 230 | 3 | 65 | 400 | - | 230 | 3 | 65 | 312 FLA | 125 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 230 | 3 | 18 | 312 | 125
|  | OLR | Allen-Bradley | 193-EC*JG | 230 | 3 | 18 | 84-420 | -
AB113D-D300...-E3KCD40-..460V_140G-KC6_65KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 480 | 3 | 65 | 400 | - | 480 | 3 | 65 | 302 FLA | 250 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 480 | 3 | 18 | 302 | 250
|  | OLR | Allen-Bradley | 193-EC*JG | 480 | 3 | 18 | 84-420 | -
AB113D-D300...-E3KCD40-..575V_140G-KC6_30KCA | C | CB | Allen-Bradley | 140G-KC6*3-D40 | 600 | 3 | 30 | 400 | - | 600 | 3 | 30 | 289 FLA | 300 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 600 | 3 | 18 | 289 | 300
|  | OLR | Allen-Bradley | 193-EC*JG | 600 | 3 | 18 | 84-420 | -
AB113D-C30...-E300FC30-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC30-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC30-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC30-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-C30 | 600 | 3 | 25 | 30 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC50-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC50-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC50-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C30...-E300FC50-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 600 | 3 | 25 | 50 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C37...-E300FC50-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 200 | 3 | 65 | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C37...-E300FC50-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 230 | 3 | 65 | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C37...-E300FC50-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 480 | 3 | 65 | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C37...-E300FC50-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-C50 | 600 | 3 | 25 | 50 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C43...-E300FC80-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C43...-E300FC80-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C43...-E300FC80-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C43...-E300FC80-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C55...-E300FC80-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 200 | 3 | 65 | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113D-C55...-E300FC80-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 230 | 3 | 65 | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113D-C55...-E300FC80-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 480 | 3 | 65 | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113D-C55...-E300FC80-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113D-C60...-E300GD12-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C60...-E300GD12-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C60...-E300GD12-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C60...-E300GD12-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C72...-E300GD12-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C72...-E300GD12-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 68 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C72...-E300GD12-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C72...-E300GD12-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C85...-E300GD12-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C85...-E300GD12-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C85...-E300GD12-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C85...-E300GD12-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-C97...-E300VD12-..200V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 200 | 3 | 65 | 125 | - | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113D-C97...-E300VD12-..230V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 230 | 3 | 65 | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113D-C97...-E300VD12-..460V_140G-HC6_65KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 480 | 3 | 65 | 125 | - | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113D-C97...-E300VD12-..575V_140G-HC6_25KCA | C | CB | Allen-Bradley | 140G-HC6*3-D12 | 600 | 3 | 25 | 125 | - | 600 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113D-D115...-E300VD12-..200V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 120 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113D-D115...-E300VD12-..230V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 104 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113D-D115...-E300VD12-..460V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113D-D115...-E300VD12-..575V_140G-JC6_25KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 99 FLA | 100 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113D-D140...-E300VD12-..200V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 120 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113D-D140...-E300VD12-..230V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 130 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113D-D140...-E300VD12-..460V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 124 FLA | 100 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113D-D140...-E300VD12-..575V_140G-JC6_25KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 125 FLA | 125 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113D-D180...-E300VD12-..200V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 150 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 200 | 3 | 10 | 150 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113D-D180...-E300VD12-..230V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 154 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 230 | 3 | 10 | 154 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113D-D180...-E300VD12-..460V_140G-JC6_65KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 156 FLA | 150 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 480 | 3 | 10 | 156 | 150
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113D-D180...-E300VD12-..575V_140G-JC6_25KCA | C | CB | Allen-Bradley | 140G-JC6*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 144 FLA | 150 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 600 | 3 | 10 | 144 | 150
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113D-D115...-E300VD12-..200V_140G-J6_65KCA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 120 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113D-D115...-E300VD12-..200V_140G-J3_35KCA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 200 | 3 | 35 | 250 | - | 200 | 3 | 35 | 120 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113D-D115...-E300VD12-..200V_140G-J2_25KCA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 200 | 3 | 25 | 250 | - | 200 | 3 | 25 | 120 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113D-D115...-E300VD12-..230V_140G-J6_65KCA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 104 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113D-D115...-E300VD12-..230V_140G-J3_35KCA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 230 | 3 | 35 | 250 | - | 230 | 3 | 35 | 104 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113D-D115...-E300VD12-..230V_140G-J2_25KCA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 230 | 3 | 25 | 250 | - | 230 | 3 | 25 | 104 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113D-D115...-E300VD12-..460V_140G-J6_65KCA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113D-D115...-E300VD12-..460V_140G-J3_35KCA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 480 | 3 | 35 | 250 | - | 480 | 3 | 35 | 96 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113D-D115...-E300VD12-..460V_140G-J2_25KCA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 480 | 3 | 25 | 250 | - | 480 | 3 | 25 | 96 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113D-D115...-E300VD12-..575V_140G-J6_25KCA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 99 FLA | 100 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113D-D115...-E300VD12-..575V_140G-J3_18KCA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 600 | 3 | 18 | 250 | - | 600 | 3 | 18 | 99 FLA | 100 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113D-D115...-E300VD12-..575V_140G-J2_14KCA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 600 | 3 | 14 | 250 | - | 600 | 3 | 14 | 99 FLA | 100 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113D-D140...-E300VD12-..200V_140G-J6_65KCA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 120 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113D-D140...-E300VD12-..200V_140G-J3_35KCA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 200 | 3 | 35 | 250 | - | 200 | 3 | 35 | 120 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113D-D140...-E300VD12-..200V_140G-J2_25KCA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 200 | 3 | 25 | 250 | - | 200 | 3 | 25 | 120 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113D-D140...-E300VD12-..230V_140G-J6_65KCA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 130 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113D-D140...-E300VD12-..230V_140G-J3_35KCA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 230 | 3 | 35 | 250 | - | 230 | 3 | 35 | 130 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113D-D140...-E300VD12-..230V_140G-J2_25KCA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 230 | 3 | 25 | 250 | - | 230 | 3 | 25 | 130 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113D-D140...-E300VD12-..460V_140G-J6_65KCA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 124 FLA | 100 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113D-D140...-E300VD12-..460V_140G-J3_35KCA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 480 | 3 | 35 | 250 | - | 480 | 3 | 35 | 124 FLA | 100 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113D-D140...-E300VD12-..460V_140G-J2_25KCA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 480 | 3 | 25 | 250 | - | 480 | 3 | 25 | 124 FLA | 100 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113D-D140...-E300VD12-..575V_140G-J6_25KCA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 125 FLA | 125 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113D-D140...-E300VD12-..575V_140G-J3_18KCA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 600 | 3 | 18 | 250 | - | 600 | 3 | 18 | 125 FLA | 125 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113D-D140...-E300VD12-..575V_140G-J2_14KCA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 600 | 3 | 14 | 250 | - | 600 | 3 | 14 | 125 FLA | 125 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113D-D180...-E300VD12-..200V_140G-J6_65KCA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 150 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 200 | 3 | 10 | 150 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113D-D180...-E300VD12-..200V_140G-J3_35KCA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 200 | 3 | 35 | 250 | - | 200 | 3 | 35 | 150 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 200 | 3 | 10 | 150 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113D-D180...-E300VD12-..200V_140G-J2_25KCA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 200 | 3 | 25 | 250 | - | 200 | 3 | 25 | 150 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 200 | 3 | 10 | 150 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113D-D180...-E300VD12-..230V_140G-J6_65KCA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 154 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 230 | 3 | 10 | 154 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113D-D180...-E300VD12-..230V_140G-J3_35KCA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 230 | 3 | 35 | 250 | - | 230 | 3 | 35 | 154 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 230 | 3 | 10 | 154 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113D-D180...-E300VD12-..230V_140G-J2_25KCA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 230 | 3 | 25 | 250 | - | 230 | 3 | 25 | 154 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 230 | 3 | 10 | 154 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113D-D180...-E300VD12-..460V_140G-J6_65KCA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 156 FLA | 150 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 480 | 3 | 10 | 156 | 150
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113D-D180...-E300VD12-..460V_140G-J3_35KCA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 480 | 3 | 35 | 250 | - | 480 | 3 | 35 | 156 FLA | 150 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 480 | 3 | 10 | 156 | 150
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113D-D180...-E300VD12-..460V_140G-J2_25KCA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 480 | 3 | 25 | 250 | - | 480 | 3 | 25 | 156 FLA | 150 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 480 | 3 | 10 | 156 | 150
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113D-D180...-E300VD12-..575V_140G-J6_25KCA | C | CB | Allen-Bradley | 140G-J6*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 144 FLA | 150 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 600 | 3 | 10 | 144 | 150
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113D-D180...-E300VD12-..575V_140G-J3_18KCA | C | CB | Allen-Bradley | 140G-J3*3-D25 | 600 | 3 | 18 | 250 | - | 600 | 3 | 18 | 144 FLA | 150 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 600 | 3 | 10 | 144 | 150
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113D-D180...-E300VD12-..575V_140G-J2_14KCA | C | CB | Allen-Bradley | 140G-J2*3-D25 | 600 | 3 | 14 | 250 | - | 600 | 3 | 14 | 144 FLA | 150 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 600 | 3 | 10 | 144 | 150
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113D-D115...-E1HD15-..200V | D | ICB | Allen-Bradley | 140M-I3*3-D15 | 200 | 3 | 35 | 150 | - | 200 | 3 | 35 | 92 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EEHF | 200 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HD15-..230V | D | ICB | Allen-Bradley | 140M-I3*3-D15 | 230 | 3 | 35 | 150 | - | 230 | 3 | 35 | 104 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-EEHF | 230 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HD15-..460V | D | ICB | Allen-Bradley | 140M-I3*3-D15 | 480 | 3 | 35 | 150 | - | 480 | 3 | 35 | 96 FLA | 75 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EEHF | 480 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HD15-..575V | D | ICB | Allen-Bradley | 140M-I3*3-D15 | 600Y/347 | 3 | 35 | 150 | - | 600Y/347 | 3 | 10 | 99 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-EEHF | 600 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD15-..200V | D | ICB | Allen-Bradley | 140M-I3*3-D15 | 200 | 3 | 35 | 150 | - | 200 | 3 | 35 | 120 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-EEHF | 200 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD15-..230V | D | ICB | Allen-Bradley | 140M-I3*3-D15 | 230 | 3 | 35 | 150 | - | 230 | 3 | 35 | 130 FLA | 50 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-EEHF | 230 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD15-..460V | D | ICB | Allen-Bradley | 140M-I3*3-D15 | 480 | 3 | 35 | 150 | - | 480 | 3 | 35 | 124 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-EEHF | 480 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD15-..575V | D | ICB | Allen-Bradley | 140M-I3*3-D15 | 600Y/347 | 3 | 35 | 150 | - | 600Y/347 | 3 | 10 | 125 FLA | 125 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-EEHF | 600 | 3 | 10 | 30-150 | -
AB113D-D115...-E3HD15-..200V | D | ICB | Allen-Bradley | 140M-I3*3-D15 | 200 | 3 | 35 | 150 | - | 200 | 3 | 35 | 92 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HD15-..230V | D | ICB | Allen-Bradley | 140M-I3*3-D15 | 230 | 3 | 35 | 150 | - | 230 | 3 | 35 | 104 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HD15-..460V | D | ICB | Allen-Bradley | 140M-I3*3-D15 | 480 | 3 | 35 | 150 | - | 480 | 3 | 35 | 96 FLA | 75 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HD15-..575V | D | ICB | Allen-Bradley | 140M-I3*3-D15 | 600Y/347 | 3 | 35 | 150 | - | 600Y/347 | 3 | 10 | 99 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD15-..200V | D | ICB | Allen-Bradley | 140M-I3*3-D15 | 200 | 3 | 35 | 150 | - | 200 | 3 | 35 | 120 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD15-..230V | D | ICB | Allen-Bradley | 140M-I3*3-D15 | 230 | 3 | 35 | 150 | - | 230 | 3 | 35 | 130 FLA | 50 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD15-..460V | D | ICB | Allen-Bradley | 140M-I3*3-D15 | 480 | 3 | 35 | 150 | - | 480 | 3 | 35 | 124 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD15-..575V | D | ICB | Allen-Bradley | 140M-I3*3-D15 | 600Y/347 | 3 | 35 | 150 | - | 600Y/347 | 3 | 10 | 125 FLA | 125 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-D115G...-E300VD15-..200V | D | CB | Allen-Bradley | 140M-I3*3-D15 | 200 | 3 | 35 | 150 | - | 200 | 3 | 35 | 120 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113D-D115G...-E300VD15-..230V | D | CB | Allen-Bradley | 140M-I3*3-D15 | 230 | 3 | 35 | 150 | - | 230 | 3 | 35 | 104 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113D-D115G...-E300VD15-..460V | D | CB | Allen-Bradley | 140M-I3*3-D15 | 480 | 3 | 35 | 150 | - | 480 | 3 | 35 | 96 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113D-D115G...-E300VD15-..575V | D | CB | Allen-Bradley | 140M-I3*3-D15 | 600Y/347 | 3 | 35 | 150 | - | 600Y/347 | 3 | 10 | 99 FLA | 100 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113D-D140G...-E300VD15-..200V | D | CB | Allen-Bradley | 140M-I3*3-D15 | 200 | 3 | 35 | 150 | - | 200 | 3 | 35 | 120 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113D-D140G...-E300VD15-..230V | D | CB | Allen-Bradley | 140M-I3*3-D15 | 230 | 3 | 35 | 150 | - | 230 | 3 | 35 | 130 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113D-D140G...-E300VD15-..460V | D | CB | Allen-Bradley | 140M-I3*3-D15 | 480 | 3 | 35 | 150 | - | 480 | 3 | 35 | 124 FLA | 100 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113D-D140G...-E300VD15-..575V | D | CB | Allen-Bradley | 140M-I3*3-D15 | 600Y/347 | 3 | 35 | 150 | - | 600Y/347 | 3 | 10 | 125 FLA | 125 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113D-D115...-E1HD15-..200V | D | ICB | Allen-Bradley | 140M-I2*3-D15 | 200 | 3 | 25 | 150 | - | 200 | 3 | 25 | 92 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EEHF | 200 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HD15-..230V | D | ICB | Allen-Bradley | 140M-I2*3-D15 | 230 | 3 | 25 | 150 | - | 230 | 3 | 25 | 104 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-EEHF | 230 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HD15-..460V | D | ICB | Allen-Bradley | 140M-I2*3-D15 | 480 | 3 | 25 | 150 | - | 480 | 3 | 25 | 96 FLA | 75 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EEHF | 480 | 3 | 10 | 30-150 | -
AB113D-D115...-E1HD15-..575V | D | ICB | Allen-Bradley | 140M-I2*3-D15 | 600Y/347 | 3 | 25 | 150 | - | 600Y/347 | 3 | 10 | 99 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-EEHF | 600 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD15-..200V | D | ICB | Allen-Bradley | 140M-I2*3-D15 | 200 | 3 | 25 | 150 | - | 200 | 3 | 25 | 120 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-EEHF | 200 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD15-..230V | D | ICB | Allen-Bradley | 140M-I2*3-D15 | 230 | 3 | 25 | 150 | - | 230 | 3 | 25 | 130 FLA | 50 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-EEHF | 230 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD15-..460V | D | ICB | Allen-Bradley | 140M-I2*3-D15 | 480 | 3 | 25 | 150 | - | 480 | 3 | 25 | 124 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-EEHF | 480 | 3 | 10 | 30-150 | -
AB113D-D140...-E1HD15-..575V | D | ICB | Allen-Bradley | 140M-I2*3-D15 | 600Y/347 | 3 | 25 | 150 | - | 600Y/347 | 3 | 10 | 125 FLA | 125 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-EEHF | 600 | 3 | 10 | 30-150 | -
AB113D-D115...-E3HD15-..200V | D | ICB | Allen-Bradley | 140M-I2*3-D15 | 200 | 3 | 25 | 150 | - | 200 | 3 | 25 | 92 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HD15-..230V | D | ICB | Allen-Bradley | 140M-I2*3-D15 | 230 | 3 | 25 | 150 | - | 230 | 3 | 25 | 104 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HD15-..460V | D | ICB | Allen-Bradley | 140M-I2*3-D15 | 480 | 3 | 25 | 150 | - | 480 | 3 | 25 | 96 FLA | 75 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-D115...-E3HD15-..575V | D | ICB | Allen-Bradley | 140M-I2*3-D15 | 600Y/347 | 3 | 25 | 150 | - | 600Y/347 | 3 | 10 | 99 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD15-..200V | D | ICB | Allen-Bradley | 140M-I2*3-D15 | 200 | 3 | 25 | 150 | - | 200 | 3 | 25 | 120 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD15-..230V | D | ICB | Allen-Bradley | 140M-I2*3-D15 | 230 | 3 | 25 | 150 | - | 230 | 3 | 25 | 130 FLA | 50 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD15-..460V | D | ICB | Allen-Bradley | 140M-I2*3-D15 | 480 | 3 | 25 | 150 | - | 480 | 3 | 25 | 124 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113D-D140...-E3HD15-..575V | D | ICB | Allen-Bradley | 140M-I2*3-D15 | 600Y/347 | 3 | 25 | 150 | - | 600Y/347 | 3 | 10 | 125 FLA | 125 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113D-D115G...-E300VD15-..200V | D | CB | Allen-Bradley | 140M-I2*3-D15 | 200 | 3 | 25 | 150 | - | 200 | 3 | 25 | 120 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113D-D115G...-E300VD15-..230V | D | CB | Allen-Bradley | 140M-I2*3-D15 | 230 | 3 | 25 | 150 | - | 230 | 3 | 25 | 104 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113D-D115G...-E300VD15-..460V | D | CB | Allen-Bradley | 140M-I2*3-D15 | 480 | 3 | 25 | 150 | - | 480 | 3 | 25 | 96 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113D-D115G...-E300VD15-..575V | D | CB | Allen-Bradley | 140M-I2*3-D15 | 600Y/347 | 3 | 25 | 150 | - | 600Y/347 | 3 | 10 | 99 FLA | 100 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113D-D140G...-E300VD15-..200V | D | CB | Allen-Bradley | 140M-I2*3-D15 | 200 | 3 | 25 | 150 | - | 200 | 3 | 25 | 120 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113D-D140G...-E300VD15-..230V | D | CB | Allen-Bradley | 140M-I2*3-D15 | 230 | 3 | 25 | 150 | - | 230 | 3 | 25 | 130 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113D-D140G...-E300VD15-..460V | D | CB | Allen-Bradley | 140M-I2*3-D15 | 480 | 3 | 25 | 150 | - | 480 | 3 | 25 | 124 FLA | 100 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113D-D140G...-E300VD15-..575V | D | CB | Allen-Bradley | 140M-I2*3-D15 | 600Y/347 | 3 | 25 | 150 | - | 600Y/347 | 3 | 10 | 125 FLA | 125 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -

## Const. D w MCP (113H) Series B
[16 empty] | Issued: | 2014-07-07
[16 empty] | Last Revised: | 2020-12-10
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number [1] | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP rating | Enclosure Volume, CU inches
AB113H-C30...-E1EB30-..200V | D | ICB | Allen-Bradley | 140MG-H8P-B30 | 200 | 3 | --- | 3 | - | 200 | 3 | 65 | 2.5 FLA | 0.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EECB | 200 | 3 | 5 | 1-5 | -
AB113H-C30...-E1EB30-..230V | D | ICB | Allen-Bradley | 140MG-H8P-B30 | 230 | 3 | --- | 3 | - | 230 | 3 | 65 | 2.2 FLA | 0.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EECB | 230 | 3 | 5 | 1-5 | -
AB113H-C30...-E1EB30-..460V | D | ICB | Allen-Bradley | 140MG-H8P-B30 | 480 | 3 | --- | 3 | - | 480 | 3 | 65 | 3.0 FLA | 1.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EECB | 480 | 3 | 5 | 1-5 | -
AB113H-C30...-E1EB30-..575V | D | ICB | Allen-Bradley | 140MG-H8P-B30 | 600 | 3 | --- | 3 | - | 600 | 3 | 25 | 2.7 FLA | 2 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EECB | 600 | 3 | 5 | 1-5 | -
AB113H-C30...-E1FB70-..200V | D | ICB | Allen-Bradley | 140MG-H8P-B70 | 200 | 3 | --- | 7 | - | 200 | 3 | 65 | 6.9 FLA | 1.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEDD | 200 | 3 | 5 | 3.2-16 | -
AB113H-C30...-E1FB70-..230V | D | ICB | Allen-Bradley | 140MG-H8P-B70 | 230 | 3 | --- | 7 | - | 230 | 3 | 65 | 6.8 FLA | 2 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEDD | 230 | 3 | 5 | 3.2-16 | -
AB113H-C30...-E1FB70-..460V | D | ICB | Allen-Bradley | 140MG-H8P-B70 | 480 | 3 | --- | 7 | - | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEDD | 480 | 3 | 5 | 3.2-16 | -
AB113H-C30...-E1FB70-..575V | D | ICB | Allen-Bradley | 140MG-H8P-B70 | 600 | 3 | --- | 7 | - | 600 | 3 | 25 | 6.1 FLA | 5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEDD | 600 | 3 | 5 | 3.2-16 | -
AB113H-C30...-E1EC15-..200V | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | --- | 15 | - | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEED | 200 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC15-..230V | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | --- | 15 | - | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEED | 230 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC15-..460V | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | --- | 15 | - | 480 | 3 | 65 | 14.0 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEED | 480 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC15-..575V | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | --- | 15 | - | 600 | 3 | 25 | 11.0 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEED | 600 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1FC30-..200V | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | --- | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113H-C30...-E1FC30-..230V | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | --- | 30 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113H-C30...-E1FC30-..460V | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | --- | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113H-C30...-E1FC30-..575V | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | --- | 30 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113H-C30...-E1FC50-..200V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | --- | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113H-C30...-E1FC50-..230V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | --- | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113H-C30...-E1FC50-..460V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | --- | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113H-C30...-E1FC50-..575V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | --- | 50 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113H-C37...-E1FC50-..200V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | --- | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113H-C37...-E1FC50-..230V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | --- | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113H-C37...-E1FC50-..460V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | --- | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113H-C37...-E1FC50-..575V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | --- | 50 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113H-C43...-E1FC80-..200V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 200 | 3 | --- | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113H-C43...-E1FC80-..230V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 230 | 3 | --- | 80 | - | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113H-C43...-E1FC80-..460V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 480 | 3 | --- | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113H-C43...-E1FC80-..575V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 600 | 3 | --- | 80 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113H-C55...-E1GC80-..200V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 200 | 3 | --- | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 5 | 18-90 | -
AB113H-C55...-E1GC80-..230V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 230 | 3 | --- | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 5 | 18-90 | -
AB113H-C55...-E1GC80-..460V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 480 | 3 | --- | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 5 | 18-90 | -
AB113H-C55...-E1GC80-..575V | D | CB | Allen-Bradley | 140MG-H8P-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 5 | 18-90 | -
AB113H-C60...-E1GD12-..200V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113H-C60...-E1GD12-..230V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113H-C60...-E1GD12-..460V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113H-C60...-E1GD12-..575V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | --- | 125 | - | 600 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113H-C72...-E1GD12-..200V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113H-C72...-E1GD12-..230V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 68 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113H-C72...-E1GD12-..460V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113H-C72...-E1GD12-..575V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | --- | 125 | - | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113H-C85...-E1GD12-..200V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113H-C85...-E1GD12-..230V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113H-C85...-E1GD12-..460V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113H-C85...-E1GD12-..575V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | --- | 125 | - | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113H-C97...-E1VD12-..200V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EEVE | 200 | 3 | 10 | 60-120 | -
AB113H-C97...-E1VD12-..230V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EEVE | 230 | 3 | 10 | 60-120 | -
AB113H-C97...-E1VD12-..460V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EEVE | 480 | 3 | 10 | 60-120 | -
AB113H-C97...-E1VD12-..575V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | --- | 125 | - | 600 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-EEVE | 600 | 3 | 10 | 60-120 | -
AB113H-C30G...-E1ECB30-..200V | D | ICB | Allen-Bradley | 140MG-G8P-B30 | 200 | 3 | --- | 3 | - | 200 | 3 | 65 | 2.5 FLA | 0.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EECB | 200 | 3 | 5 | 1-5 | -
AB113H-C30G...-E1EB30-..230V | D | ICB | Allen-Bradley | 140MG-G8P-B30 | 230 | 3 | --- | 3 | - | 230 | 3 | 65 | 2.2 FLA | 0.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EECB | 230 | 3 | 5 | 1-5 | -
AB113H-C30G...-E1EB30-..460V | D | ICB | Allen-Bradley | 140MG-G8P-B30 | 480 | 3 | --- | 3 | - | 480 | 3 | 65 | 3.0 FLA | 1.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EECB | 480 | 3 | 5 | 1-5 | -
AB113H-C30G...-E1EB30-..575V | D | ICB | Allen-Bradley | 140MG-G8P-B30 | 600Y/347 | 3 | --- | 3 | - | 600Y/347 | 3 | 25 | 2.7 FLA | 2 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EECB | 600 | 3 | 5 | 1-5 | -
AB113H-C30G...-E1FB70-..200V | D | ICB | Allen-Bradley | 140MG-G8P-B70 | 200 | 3 | --- | 7 | - | 200 | 3 | 65 | 6.9 FLA | 1.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEDD | 200 | 3 | 5 | 3.2-16 | -
AB113H-C30G...-E1FB70-..230V | D | ICB | Allen-Bradley | 140MG-G8P-B70 | 230 | 3 | --- | 7 | - | 230 | 3 | 65 | 6.8 FLA | 2 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEDD | 230 | 3 | 5 | 3.2-16 | -
AB113H-C30G...-E1FB70-..460V | D | ICB | Allen-Bradley | 140MG-G8P-B70 | 480 | 3 | --- | 7 | - | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEDD | 480 | 3 | 5 | 3.2-16 | -
AB113H-C30G...-E1FB70-..575V | D | ICB | Allen-Bradley | 140MG-G8P-B70 | 600Y/347 | 3 | --- | 7 | - | 600Y/347 | 3 | 25 | 6.1 FLA | 5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEDD | 600 | 3 | 5 | 3.2-16 | -
AB113H-C30G...-E1EC15-..200V | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | --- | 15 | - | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEED | 200 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC15-..230V | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | --- | 15 | - | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEED | 230 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC15-..460V | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | --- | 15 | - | 480 | 3 | 65 | 14.0 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEED | 480 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC15-..575V | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 600Y/347 | 3 | --- | 15 | - | 600Y/347 | 3 | 25 | 11.0 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEED | 600 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1FC30-..200V | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | --- | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113H-C30G...-E1FC30-..230V | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | --- | 30 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113H-C30G...-E1FC30-..460V | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | --- | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113H-C30G...-E1FC30-..575V | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 600Y/347 | 3 | --- | 30 | - | 600Y/347 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113H-C30G...-E1FC50-..200V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | --- | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113H-C30G...-E1FC50-..230V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | --- | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113H-C30G...-E1FC50-..460V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | --- | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113H-C30G...-E1FC50-..575V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 600Y/347 | 3 | --- | 50 | - | 600Y/347 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113H-C37G...-E1FC50-..200V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | --- | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113H-C37G...-E1FC50-..230V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | --- | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113H-C37G...-E1FC50-..460V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | --- | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113H-C37G...-E1FC50-..575V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 600Y/347 | 3 | --- | 50 | - | 600Y/347 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113H-C43G...-E1FC80-..200V | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 200 | 3 | --- | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EEFD | 200 | 3 | 5 | 9-45 | -
AB113H-C43G...-E1FC80-..230V | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 230 | 3 | --- | 80 | - | 230 | 3 | 65 | 42 FLA | 15 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-EEFD | 230 | 3 | 5 | 9-45 | -
AB113H-C43G...-E1FC80-..460V | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 480 | 3 | --- | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 480 | 3 | 5 | 9-45 | -
AB113H-C43G...-E1FC50-..575V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 600Y/347 | 3 | --- | 50 | - | 600Y/347 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EEFD | 600 | 3 | 5 | 9-45 | -
AB113H-C55G...-E1GC80-..200V | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 200 | 3 | --- | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 5 | 18-90 | -
AB113H-C55G...-E1GC80-..230V | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 230 | 3 | --- | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 5 | 18-90 | -
AB113H-C55G...-E1GC80-..460V | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 480 | 3 | --- | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 5 | 18-90 | -
AB113H-C60G...-E1GD12-..200V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113H-C60G...-E1GD12-..230V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113H-C60G...-E1GD12-..460V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113H-C60G...-E1GD12-..575V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 600Y/347 | 3 | --- | 125 | - | 600Y/347 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113H-C72G...-E1GD12-..200V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113H-C72G...-E1GD12-..230V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 68 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113H-C72G...-E1GD12-..460V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113H-C72G...-E1GD12-..575V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 600Y/347 | 3 | --- | 125 | - | 600Y/347 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113H-C85G...-E1GD12-..200V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-EEGE | 200 | 3 | 10 | 18-90 | -
AB113H-C85G...-E1GD12-..230V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EEGE | 230 | 3 | 10 | 18-90 | -
AB113H-C85G...-E1GD12-..460V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 480 | 3 | 10 | 18-90 | -
AB113H-C85G...-E1GD12-..575V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 600Y/347 | 3 | --- | 125 | - | 600Y/347 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EEGE | 600 | 3 | 10 | 18-90 | -
AB113H-C97G...-E1VD12-..200V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EEVE | 200 | 3 | 10 | 60-120 | -
AB113H-C97G...-E1VD12-..230V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EEVE | 230 | 3 | 10 | 60-120 | -
AB113H-C97G...-E1VD12-..460V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EEVE | 480 | 3 | 10 | 60-120 | -
AB113H-C97G...-E1VD12-..575V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 600Y/347 | 3 | --- | 125 | - | 600Y/347 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-EEVE | 600 | 3 | 10 | 60-120 | -
AB113H-D115...-E1HD25-..200V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 200 | 3 | --- | 250 | - | 200 | 3 | 65 | 92 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EEHF | 200 | 3 | 10 | 30-150 | -
AB113H-D115...-E1HD25-..230V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 230 | 3 | --- | 250 | - | 230 | 3 | 65 | 104 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-EEHF | 230 | 3 | 10 | 30-150 | -
AB113H-D115...-E1HD25-..460V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 480 | 3 | --- | 250 | - | 480 | 3 | 65 | 96 FLA | 75 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EEHF | 480 | 3 | 10 | 30-150 | -
AB113H-D115...-E1HD25-..575V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 600 | 3 | --- | 250 | - | 600 | 3 | 25 | 99 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-EEHF | 600 | 3 | 10 | 30-150 | -
AB113H-D140...-E1HD25-..200V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 200 | 3 | --- | 250 | - | 200 | 3 | 65 | 120 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-EEHF | 200 | 3 | 10 | 30-150 | -
AB113H-D140...-E1HD25-..230V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 230 | 3 | --- | 250 | - | 230 | 3 | 65 | 130 FLA | 50 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-EEHF | 230 | 3 | 10 | 30-150 | -
AB113H-D140...-E1HD25-..460V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 480 | 3 | --- | 250 | - | 480 | 3 | 65 | 124 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-EEHF | 480 | 3 | 10 | 30-150 | -
AB113H-D140...-E1HD25-..575V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 600 | 3 | --- | 250 | - | 600 | 3 | 25 | 125 FLA | 125 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-EEHF | 600 | 3 | 10 | 30-150 | -
AB113H-D180...-E1JD25-..200V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 200 | 3 | --- | 250 | - | 200 | 3 | 65 | 150 FLA | 50 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 200 | 3 | 10 | 150 | 50
|  | OLR | Allen-Bradley | 193-EEJF | 200 | 3 | 10 | 40-200 | -
AB113H-D180...-E1JD25-..230V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 230 | 3 | --- | 250 | - | 230 | 3 | 65 | 154 FLA | 60 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 230 | 3 | 10 | 154 | 60
|  | OLR | Allen-Bradley | 193-EEJF | 230 | 3 | 10 | 40-200 | -
AB113H-D180...-E1JD25-..460V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 480 | 3 | --- | 250 | - | 480 | 3 | 65 | 180 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 480 | 3 | 10 | 180 | 150
|  | OLR | Allen-Bradley | 193-EEJF | 480 | 3 | 10 | 40-200 | -
AB113H-D180...-E1JD25-..575V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 600 | 3 | --- | 250 | - | 600 | 3 | 25 | 144 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 600 | 3 | 10 | 144 | 150
|  | OLR | Allen-Bradley | 193-EEJF | 600 | 3 | 10 | 40-200 | -
AB113H-D210...-E1KD40-..200V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 200 | 3 | --- | 400 | - | 200 | 3 | 65 | 177 FLA | 60 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 200 | 3 | 18 | 177 | 60
|  | OLR | Allen-Bradley | 193-EEKG | 200 | 3 | 18 | 60-300 | -
AB113H-D210...-E1KD40-..230V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 230 | 3 | --- | 400 | - | 230 | 3 | 65 | 192 FLA | 75 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 230 | 3 | 18 | 192 | 75
|  | OLR | Allen-Bradley | 193-EEKG | 230 | 3 | 18 | 60-300 | -
AB113H-D210...-E1KD40-..460V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 480 | 3 | --- | 400 | - | 480 | 3 | 65 | 180 FLA | 150 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 480 | 3 | 18 | 180 | 150
|  | OLR | Allen-Bradley | 193-EEKG | 480 | 3 | 18 | 60-300 | -
AB113H-D210...-E1KD40-..575V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 600 | 3 | --- | 400 | - | 600 | 3 | 30 | 192 FLA | 200 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 600 | 3 | 18 | 192 | 200
|  | OLR | Allen-Bradley | 193-EEKG | 600 | 3 | 18 | 60-300 | -
AB113H-D250...-E1KD40-..200V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 200 | 3 | --- | 400 | - | 200 | 3 | 65 | 221 FLA | 75 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 200 | 3 | 18 | 221 | 75
|  | OLR | Allen-Bradley | 193-EEKG | 200 | 3 | 18 | 60-300 | -
AB113H-D250...-E1KD40-..230V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 230 | 3 | --- | 400 | - | 230 | 3 | 65 | 248 FLA | 100 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 230 | 3 | 18 | 248 | 100
|  | OLR | Allen-Bradley | 193-EEKG | 230 | 3 | 18 | 60-300 | -
AB113H-D250...-E1KD40-..460V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 480 | 3 | --- | 400 | - | 480 | 3 | 65 | 240 FLA | 200 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 480 | 3 | 18 | 240 | 200
|  | OLR | Allen-Bradley | 193-EEKG | 480 | 3 | 18 | 60-300 | -
AB113H-D250...-E1KD40-..575V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 600 | 3 | --- | 400 | - | 600 | 3 | 30 | 242 FLA | 250 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 600 | 3 | 18 | 242 | 250
|  | OLR | Allen-Bradley | 193-EEKG | 600 | 3 | 18 | 60-300 | -
AB113H-D300...-E1KD40-..200V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 200 | 3 | --- | 400 | - | 200 | 3 | 65 | 285 FLA | 100 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 200 | 3 | 18 | 285 | 100
|  | OLR | Allen-Bradley | 193-EELG | 200 | 3 | 18 | 100-500 | -
AB113H-D300...-E1KD40-..230V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 230 | 3 | --- | 400 | - | 230 | 3 | 65 | 312 FLA | 125 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 230 | 3 | 18 | 312 | 125
|  | OLR | Allen-Bradley | 193-EELG | 230 | 3 | 18 | 100-500 | -
AB113H-D300...-E1KD40-..460V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 480 | 3 | --- | 400 | - | 480 | 3 | 65 | 302 FLA | 250 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 480 | 3 | 18 | 302 | 250
|  | OLR | Allen-Bradley | 193-EELG | 480 | 3 | 18 | 100-500 | -
AB113H-D300...-E1KD40-..575V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 600 | 3 | --- | 400 | - | 600 | 3 | 30 | 289 FLA | 300 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 600 | 3 | 18 | 289 | 300
|  | OLR | Allen-Bradley | 193-EELG | 600 | 3 | 18 | 100-500 | -
AB113H-D420...-E1LD80-..200V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 200 | 3 | --- | 800 | - | 200 | 3 | 42 | 414 FLA | 150 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 200 | 3 | 18 | 414 | 150
|  | OLR | Allen-Bradley | 193-EELG | 200 | 3 | 18 | 100-500 | -
AB113H-D420...-E1LD80-..230V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 230 | 3 | --- | 800 | - | 230 | 3 | 42 | 420 FLA / 2520LRA | 175 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 230 | 3 | 18 | 420 | 175
|  | OLR | Allen-Bradley | 193-EELG | 230 | 3 | 18 | 100-500 | -
AB113H-D420...-E1LD80-..460V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 480 | 3 | --- | 800 | - | 480 | 3 | 42 | 414 FLA | 350 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 480 | 3 | 18 | 414 | 350
|  | OLR | Allen-Bradley | 193-EELG | 480 | 3 | 18 | 100-500 | -
AB113H-D420...-E1LD80-..575V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 600 | 3 | --- | 800 | - | 600 | 3 | 25 | 382 FLA | 400 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 600 | 3 | 18 | 382 | 400
|  | OLR | Allen-Bradley | 193-EELG | 600 | 3 | 18 | 100-500 | -
AB113H-D630...-E1MD80-..200V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 200 | 3 | --- | 800 | - | 200 | 3 | 65 | 552 FLA | 200 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 200 | 3 | 18 | 552 | 200
|  | OLR | Allen-Bradley | 193-EENH | 200 | 3 | 18 | 160-800 | -
AB113H-D630...-E1MD80-..230V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 230 | 3 | --- | 800 | - | 230 | 3 | 65 | 604 FLA / 4832LRA | 250 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 230 | 3 | 18 | 604 | 250
|  | OLR | Allen-Bradley | 193-EENH | 230 | 3 | 18 | 160-800 | -
AB113H-D630...-E1MD80-..460V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 480 | 3 | --- | 800 | - | 480 | 3 | 65 | 590 FLA | 500 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 480 | 3 | 18 | 590 | 500
|  | OLR | Allen-Bradley | 193-EENH | 480 | 3 | 18 | 160-800 | -
AB113H-D630...-E1MD80-..575V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 600 | 3 | --- | 800 | - | 600 | 3 | 42 | 562 FLA / 4496LRA | 600 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 600 | 3 | 18 | 562 | 600
|  | OLR | Allen-Bradley | 193-EENH | 600 | 3 | 18 | 160-800 | -
AB113H-D860...-E1MD80-..200V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 200 | 3 | --- | 800 | - | 200 | 3 | 65 | 695 FLA / 5560LRA | 250 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 200 | 3 | 42 | 695 | 250
|  | OLR | Allen-Bradley | 193-EENH | 200 | 3 | 42 | 160-800 | -
AB113H-D860...-E1MD80-..230V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 230 | 3 | --- | 800 | - | 230 | 3 | 65 | 722 FLA / 5776LRA | 300 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 230 | 3 | 42 | 722 | 300
|  | OLR | Allen-Bradley | 193-EENH | 230 | 3 | 42 | 160-800 | -
AB113H-D860...-E1MD80-..460V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 480 | 3 | --- | 800 | - | 480 | 3 | 65 | 702 FLA / 5616LRA | 600 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 480 | 3 | 42 | 702 | 600
|  | OLR | Allen-Bradley | 193-EENH | 480 | 3 | 42 | 160-800 | -
AB113H-D860...-E1MD80-..575V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 600 | 3 | --- | 800 | - | 600 | 3 | 42 | 651 FLA / 5208LRA | 700 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 600 | 3 | 42 | 651 | 700
|  | OLR | Allen-Bradley | 193-EENH | 600 | 3 | 42 | 160-800 | -
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number [1] | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP rating | Enclosure Volume, CU inches
AB113H-C30...-E3EB30-..200V | D | ICB | Allen-Bradley | 140MG-H8P-B30 | 200 | 3 | --- | 3 | - | 200 | 3 | 65 | 2.5 FLA | 0.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*AD | 200 | 3 | 5 | 1-5 | -
AB113H-C30...-E3EB30-..230V | D | ICB | Allen-Bradley | 140MG-H8P-B30 | 230 | 3 | --- | 3 | - | 230 | 3 | 65 | 2.2 FLA | 0.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*AD | 230 | 3 | 5 | 1-5 | -
AB113H-C30...-E3EB30-..460V | D | ICB | Allen-Bradley | 140MG-H8P-B30 | 480 | 3 | --- | 3 | - | 480 | 3 | 65 | 3.0 FLA | 1.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*AD | 480 | 3 | 5 | 1-5 | -
AB113H-C30...-E3EB30-..575V | D | ICB | Allen-Bradley | 140MG-H8P-B30 | 600 | 3 | --- | 3 | - | 600 | 3 | 25 | 2.7 FLA | 2 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*AD | 600 | 3 | 5 | 1-5 | -
AB113H-C30...-E3FB70-..200V | D | ICB | Allen-Bradley | 140MG-H8P-B70 | 200 | 3 | --- | 7 | - | 200 | 3 | 65 | 6.9 FLA | 1.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*BD | 200 | 3 | 5 | 3-15 | -
AB113H-C30...-E3FB70-..230V | D | ICB | Allen-Bradley | 140MG-H8P-B70 | 230 | 3 | --- | 7 | - | 230 | 3 | 65 | 6.8 FLA | 2 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*BD | 230 | 3 | 5 | 3-15 | -
AB113H-C30...-E3FB70-..460V | D | ICB | Allen-Bradley | 140MG-H8P-B70 | 480 | 3 | --- | 7 | - | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*BD | 480 | 3 | 5 | 3-15 | -
AB113H-C30...-E3FB70-..575V | D | ICB | Allen-Bradley | 140MG-H8P-B70 | 600 | 3 | --- | 7 | - | 600 | 3 | 25 | 6.1 FLA | 5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*BD | 600 | 3 | 5 | 3-15 | -
AB113H-C30...-E3EC15-..200V | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | --- | 15 | - | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*CD | 200 | 3 | 5 | 5-25 | -
AB113H-C30...-E3EC15-..230V | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | --- | 15 | - | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*CD | 230 | 3 | 5 | 5-25 | -
AB113H-C30...-E3EC15-..460V | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | --- | 15 | - | 480 | 3 | 65 | 14.0 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*CD | 480 | 3 | 5 | 5-25 | -
AB113H-C30...-E3EC15-..575V | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | --- | 15 | - | 600 | 3 | 25 | 11.0 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*CD | 600 | 3 | 5 | 5-25 | -
AB113H-C30...-E3EC30-..200V | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | --- | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113H-C30...-E3EC30-..230V | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | --- | 30 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113H-C30...-E3EC30-..460V | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | --- | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113H-C30...-E3EC30-..575V | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | --- | 30 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113H-C30...-E3FC50-..200V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | --- | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113H-C30...-E3FC50-..230V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | --- | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113H-C30...-E3FC50-..460V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | --- | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113H-C30...-E3FC50-..575V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | --- | 50 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113H-C37...-E3FC50-..200V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | --- | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113H-C37...-E3FC50-..230V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | --- | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113H-C37...-E3FC50-..460V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | --- | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113H-C37...-E3FC50-..575V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | --- | 50 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113H-C43...-E3FC80-..200V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 200 | 3 | --- | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113H-C43...-E3FC80-..230V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 230 | 3 | --- | 80 | - | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113H-C43...-E3FC80-..460V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 480 | 3 | --- | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113H-C43...-E3FC80-..575V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 600 | 3 | --- | 80 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113H-C55...-E3GC80-..200V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 200 | 3 | --- | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 5 | 18-90 | -
AB113H-C55...-E3GC80-..230V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 230 | 3 | --- | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 5 | 18-90 | -
AB113H-C55...-E3GC80-..460V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 480 | 3 | --- | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 5 | 18-90 | -
AB113H-C55...-E3GC80-..575V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 600 | 3 | --- | 80 | - | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 5 | 18-90 | -
AB113H-C60...-E3GD12-..200V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113H-C60...-E3GD12-..230V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113H-C60...-E3GD12-..460V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113H-C60...-E3GD12-..575V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | --- | 125 | - | 600 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113H-C72...-E3GD12-..200V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113H-C72...-E3GD12-..230V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 68 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113H-C72...-E3GD12-..460V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113H-C72...-E3GD12-..575V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | --- | 125 | - | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113H-C85...-E3GD12-..200V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113H-C85...-E3GD12-..230V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113H-C85...-E3GD12-..460V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113H-C85...-E3GD12-..575V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | --- | 125 | - | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113H-C97...-E3VD12-..200V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113H-C97...-E3VD12-..230V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113H-C97...-E3VD12-..460V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113H-C97...-E3VD12-..575V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | --- | 125 | - | 600 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113H-C30G...-E3EB30-..200V | D | ICB | Allen-Bradley | 140MG-G8P-B30 | 200 | 3 | --- | 3 | - | 200 | 3 | 65 | 2.5 FLA | 0.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*AD | 200 | 3 | 5 | 1-5 | -
AB113H-C30G...-E3EB30-..230V | D | ICB | Allen-Bradley | 140MG-G8P-B30 | 230 | 3 | --- | 3 | - | 230 | 3 | 65 | 2.2 FLA | 0.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*AD | 230 | 3 | 5 | 1-5 | -
AB113H-C30G...-E3EB30-..460V | D | ICB | Allen-Bradley | 140MG-G8P-B30 | 480 | 3 | --- | 3 | - | 480 | 3 | 65 | 3.0 FLA | 1.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*AD | 480 | 3 | 5 | 1-5 | -
AB113H-C30G...-E3EB30-..575V | D | ICB | Allen-Bradley | 140MG-G8P-B30 | 600Y/347 | 3 | --- | 3 | - | 600Y/347 | 3 | 25 | 2.7 FLA | 2 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*AD | 600 | 3 | 5 | 1-5 | -
AB113H-C30G...-E3FB70-..200V | D | ICB | Allen-Bradley | 140MG-G8P-B70 | 200 | 3 | --- | 7 | - | 200 | 3 | 65 | 6.9 FLA | 1.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*BD | 200 | 3 | 5 | 3-15 | -
AB113H-C30G...-E3FB70-..230V | D | ICB | Allen-Bradley | 140MG-G8P-B70 | 230 | 3 | --- | 7 | - | 230 | 3 | 65 | 6.8 FLA | 2 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*BD | 230 | 3 | 5 | 3-15 | -
AB113H-C30G...-E3FB70-..460V | D | ICB | Allen-Bradley | 140MG-G8P-B70 | 480 | 3 | --- | 7 | - | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*BD | 480 | 3 | 5 | 3-15 | -
AB113H-C30G...-E3FB70-..575V | D | ICB | Allen-Bradley | 140MG-G8P-B70 | 600Y/347 | 3 | --- | 7 | - | 600Y/347 | 3 | 25 | 6.1 FLA | 5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*BD | 600 | 3 | 5 | 3-15 | -
AB113H-C30G...-E3EC15-..200V | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | --- | 15 | - | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*CD | 200 | 3 | 5 | 5-25 | -
AB113H-C30G...-E3EC15-..230V | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | --- | 15 | - | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*CD | 230 | 3 | 5 | 5-25 | -
AB113H-C30G...-E3EC15-..460V | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | --- | 15 | - | 480 | 3 | 65 | 14.0 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*CD | 480 | 3 | 5 | 5-25 | -
AB113H-C30G...-E3EC15-..575V | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 600Y/347 | 3 | --- | 15 | - | 600Y/347 | 3 | 25 | 11.0 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*CD | 600 | 3 | 5 | 5-25 | -
AB113H-C30G...-E3EC30-..200V | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | --- | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113H-C30G...-E3EC30-..230V | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | --- | 30 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113H-C30G...-E3EC30-..460V | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | --- | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113H-C30G...-E3EC30-..575V | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 600Y/347 | 3 | --- | 30 | - | 600Y/347 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113H-C30G...-E3FC50-..200V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | --- | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113H-C30G...-E3FC50-..230V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | --- | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113H-C30G...-E3FC50-..460V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | --- | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113H-C30G...-E3FC50-..575V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 600Y/347 | 3 | --- | 50 | - | 600Y/347 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113H-C37G...-E3FC50-..200V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | --- | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113H-C37G...-E3FC50-..230V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | --- | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113H-C37G...-E3FC50-..460V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | --- | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113H-C37G...-E3FC50-..575V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 600Y/347 | 3 | --- | 50 | - | 600Y/347 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113H-C43G...-E3FC80-..200V | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 200 | 3 | --- | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-EC*DD | 200 | 3 | 5 | 9-45 | -
AB113H-C43G...-E3FC80-..230V | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 230 | 3 | --- | 80 | - | 230 | 3 | 65 | 42 FLA | 15 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-EC*DD | 230 | 3 | 5 | 9-45 | -
AB113H-C43G...-E3FC80-..460V | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 480 | 3 | --- | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 480 | 3 | 5 | 9-45 | -
AB113H-C43G...-E3FC50-..575V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 600Y/347 | 3 | --- | 50 | - | 600Y/347 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-EC*DD | 600 | 3 | 5 | 9-45 | -
AB113H-C55G...-E3GC80-..200V | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 200 | 3 | --- | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 5 | 18-90 | -
AB113H-CG...-E3GC80-..230V | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 230 | 3 | --- | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 5 | 18-90 | -
AB113H-C55G...-E3GC80-..460V | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 480 | 3 | --- | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 5 | 18-90 | -
AB113H-C60G...-E3GD12-..200V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113H-C60G...-E3GD12-..230V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113H-C60G...-E3GD12-..460V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113H-C60G...-E3GD12-..575V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 600Y/347 | 3 | --- | 125 | - | 600Y/347 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113H-C72G...-E3GD12-..200V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113H-C72G...-E3GD12-..230V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 68 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113H-C72G...-E3GD12-..460V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113H-C72G...-E3GD12-..575V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 600Y/347 | 3 | --- | 125 | - | 600Y/347 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113H-C85G...-E3GD12-..200V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-EC*EE | 200 | 3 | 10 | 18-90 | -
AB113H-C85G...-E3GD12-..230V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EC*EE | 230 | 3 | 10 | 18-90 | -
AB113H-C85G...-E3GD12-..460V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 480 | 3 | 10 | 18-90 | -
AB113H-C85G...-E3GD12-..575V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 600Y/347 | 3 | --- | 125 | - | 600Y/347 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-EC*EE | 600 | 3 | 10 | 18-90 | -
AB113H-C97G...-E3VD12-..200V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113H-C97G...-E3VD12-..230V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113H-C97G...-E3VD12-..460V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113H-C97G...-E3VD12-..575V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 600Y/347 | 3 | --- | 125 | - | 600Y/347 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113H-D115...-E3HD25-..200V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 200 | 3 | --- | 250 | - | 200 | 3 | 65 | 92 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113H-D115...-E3HD25-..230V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 230 | 3 | --- | 250 | - | 230 | 3 | 65 | 104 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113H-D115...-E3HD25-..460V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 480 | 3 | --- | 250 | - | 480 | 3 | 65 | 96 FLA | 75 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113H-D115...-E3HD25-..575V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 600 | 3 | --- | 250 | - | 600 | 3 | 25 | 99 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113H-D140...-E3HD25-..200V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 200 | 3 | --- | 250 | - | 200 | 3 | 65 | 120 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113H-D140...-E3HD25-..230V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 230 | 3 | --- | 250 | - | 230 | 3 | 65 | 130 FLA | 50 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113H-D140...-E3HD25-..460V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 480 | 3 | --- | 250 | - | 480 | 3 | 65 | 124 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113H-D140...-E3HD25-..575V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 600 | 3 | --- | 250 | - | 600 | 3 | 25 | 125 FLA | 125 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113H-D180...-E3JD25-..200V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 200 | 3 | --- | 250 | - | 200 | 3 | 65 | 150 FLA | 50 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 200 | 3 | 10 | 150 | 50
|  | OLR | Allen-Bradley | 193-EC*GF | 200 | 3 | 10 | 42-210 | -
AB113H-D180...-E3JD25-..230V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 230 | 3 | --- | 250 | - | 230 | 3 | 65 | 154 FLA | 60 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 230 | 3 | 10 | 154 | 60
|  | OLR | Allen-Bradley | 193-EC*GF | 230 | 3 | 10 | 42-210 | -
AB113H-D180...-E3JD25-..460V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 480 | 3 | --- | 250 | - | 480 | 3 | 65 | 180 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 480 | 3 | 10 | 180 | 150
|  | OLR | Allen-Bradley | 193-EC*GF | 480 | 3 | 10 | 42-210 | -
AB113H-D180...-E3JD25-..575V | D | ICB | Allen-Bradley | 140MG-J8P-D25 | 600 | 3 | --- | 250 | - | 600 | 3 | 25 | 144 FLA | 150 | 10800 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 600 | 3 | 10 | 144 | 150
|  | OLR | Allen-Bradley | 193-EC*GF | 600 | 3 | 10 | 42-210 | -
AB113H-D210...-E3KD40-..200V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 200 | 3 | --- | 400 | - | 200 | 3 | 65 | 177 FLA | 60 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 200 | 3 | 18 | 177 | 60
|  | OLR | Allen-Bradley | 193-EC*HG | 200 | 3 | 18 | 60-302 | -
AB113H-D210...-E3KD40-..230V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 230 | 3 | --- | 400 | - | 230 | 3 | 65 | 192 FLA | 75 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 230 | 3 | 18 | 192 | 75
|  | OLR | Allen-Bradley | 193-EC*HG | 230 | 3 | 18 | 60-302 | -
AB113H-D210...-E3KD40-..460V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 480 | 3 | --- | 400 | - | 480 | 3 | 65 | 180 FLA | 150 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 480 | 3 | 18 | 180 | 150
|  | OLR | Allen-Bradley | 193-EC*HG | 480 | 3 | 18 | 60-302 | -
AB113H-D210...-E3KD40-..575V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 600 | 3 | --- | 400 | - | 600 | 3 | 30 | 192 FLA | 200 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D210 | 600 | 3 | 18 | 192 | 200
|  | OLR | Allen-Bradley | 193-EC*HG | 600 | 3 | 18 | 60-302 | -
AB113H-D250...-E3KD40-..200V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 200 | 3 | --- | 400 | - | 200 | 3 | 65 | 221 FLA | 75 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 200 | 3 | 18 | 221 | 75
|  | OLR | Allen-Bradley | 193-EC*HG | 200 | 3 | 18 | 60-302 | -
AB113H-D250...-E3KD40-..230V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 230 | 3 | --- | 400 | - | 230 | 3 | 65 | 248 FLA | 100 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 230 | 3 | 18 | 248 | 100
|  | OLR | Allen-Bradley | 193-EC*HG | 230 | 3 | 18 | 60-302 | -
AB113H-D250...-E3KD40-..460V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 480 | 3 | --- | 400 | - | 480 | 3 | 65 | 240 FLA | 200 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 480 | 3 | 18 | 240 | 200
|  | OLR | Allen-Bradley | 193-EC*HG | 480 | 3 | 18 | 60-302 | -
AB113H-D250...-E3KD40-..575V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 600 | 3 | --- | 400 | - | 600 | 3 | 30 | 242 FLA | 250 | 18144 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D250 | 600 | 3 | 18 | 242 | 250
|  | OLR | Allen-Bradley | 193-EC*HG | 600 | 3 | 18 | 60-302 | -
AB113H-D300...-E3KD40-..200V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 200 | 3 | --- | 400 | - | 200 | 3 | 65 | 285 FLA | 100 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 200 | 3 | 18 | 285 | 100
|  | OLR | Allen-Bradley | 193-EC*JG | 200 | 3 | 18 | 84-420 | -
AB113H-D300...-E3KD40-..230V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 230 | 3 | --- | 400 | - | 230 | 3 | 65 | 312 FLA | 125 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 230 | 3 | 18 | 312 | 125
|  | OLR | Allen-Bradley | 193-EC*JG | 230 | 3 | 18 | 84-420 | -
AB113H-D300...-E3KD40-..460V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 480 | 3 | --- | 400 | - | 480 | 3 | 65 | 302 FLA | 250 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 480 | 3 | 18 | 302 | 250
|  | OLR | Allen-Bradley | 193-EC*JG | 480 | 3 | 18 | 84-420 | -
AB113H-D300...-E3KD40-..575V | D | ICB | Allen-Bradley | 140MG-K8P-D40 | 600 | 3 | --- | 400 | - | 600 | 3 | 30 | 289 FLA | 300 | 18144 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D300 | 600 | 3 | 18 | 289 | 300
|  | OLR | Allen-Bradley | 193-EC*JG | 600 | 3 | 18 | 84-420 | -
AB113H-D420...-E3LD80-..200V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 200 | 3 | --- | 800 | - | 200 | 3 | 42 | 414 FLA | 150 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 200 | 3 | 18 | 414 | 150
|  | OLR | Allen-Bradley | 193-EC*JG | 200 | 3 | 18 | 84-420 | -
AB113H-D420...-E3LD80-..230V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 230 | 3 | --- | 800 | - | 230 | 3 | 42 | 420 FLA / 2520LRA | 175 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 230 | 3 | 18 | 420 | 175
|  | OLR | Allen-Bradley | 193-EC*JG | 230 | 3 | 18 | 84-420 | -
AB113H-D420...-E3LD80-..460V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 480 | 3 | --- | 800 | - | 480 | 3 | 42 | 414 FLA | 350 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 480 | 3 | 18 | 414 | 350
|  | OLR | Allen-Bradley | 193-EC*JG | 480 | 3 | 18 | 84-420 | -
AB113H-D420...-E3LD80-..575V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 600 | 3 | --- | 800 | - | 600 | 3 | 25 | 382 FLA | 400 | 23520 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D420 | 600 | 3 | 18 | 382 | 400
|  | OLR | Allen-Bradley | 193-EC*JG | 600 | 3 | 18 | 84-420 | -
AB113H-D630...-E3MD80-..200V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 200 | 3 | --- | 800 | - | 200 | 3 | 65 | 552 FLA | 200 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 200 | 3 | 18 | 552 | 200
|  | OLR | Allen-Bradley | 193-EC*KH | 200 | 3 | 18 | 125-630 | -
AB113H-D630...-E3MD80-..230V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 230 | 3 | --- | 800 | - | 230 | 3 | 65 | 604 FLA / 4832LRA | 250 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 230 | 3 | 18 | 604 | 250
|  | OLR | Allen-Bradley | 193-EC*KH | 230 | 3 | 18 | 125-630 | -
AB113H-D630...-E3MD80-..460V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 480 | 3 | --- | 800 | - | 480 | 3 | 65 | 590 FLA | 500 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 480 | 3 | 18 | 590 | 500
|  | OLR | Allen-Bradley | 193-EC*KH | 480 | 3 | 18 | 125-630 | -
AB113H-D630...-E3MD80-..575V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 600 | 3 | --- | 800 | - | 600 | 3 | 42 | 562 FLA / 4496LRA | 600 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D630 | 600 | 3 | 18 | 562 | 600
|  | OLR | Allen-Bradley | 193-EC*KH | 600 | 3 | 18 | 125-630 | -
AB113H-D860...-E3MD80-..200V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 200 | 3 | --- | 800 | - | 200 | 3 | 65 | 695 FLA / 5560LRA | 250 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 200 | 3 | 42 | 695 | 250
|  | OLR | Allen-Bradley | 193-EC*LH | 200 | 3 | 42 | 172-860 | -
AB113H-D860...-E3MD80-..230V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 230 | 3 | --- | 800 | - | 230 | 3 | 65 | 722 FLA / 5776LRA | 300 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 230 | 3 | 42 | 722 | 300
|  | OLR | Allen-Bradley | 193-EC*LH | 230 | 3 | 42 | 172-860 | -
AB113H-D860...-E3MD80-..460V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 480 | 3 | --- | 800 | - | 480 | 3 | 65 | 702 FLA / 5616LRA | 600 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 480 | 3 | 42 | 702 | 600
|  | OLR | Allen-Bradley | 193-EC*LH | 480 | 3 | 42 | 172-860 | -
AB113H-D860...-E3MD80-..575V | D | ICB | Allen-Bradley | 140MG-M8P-D80 | 600 | 3 | --- | 800 | - | 600 | 3 | 42 | 651 FLA / 5208LRA | 700 | 39692 | 1,5,6 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D860 | 600 | 3 | 42 | 651 | 700
|  | OLR | Allen-Bradley | 193-EC*LH | 600 | 3 | 42 | 172-860 | -
AB113H-C30...-E300EB30-..200V | D | CB | Allen-Bradley | 140MG-H8P-B30 | 200 | 3 | 65 | 3 | - | 200 | 3 | 65 | 2.5 FLA | 0.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 200 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EB30-..230V | D | CB | Allen-Bradley | 140MG-H8P-B30 | 230 | 3 | 65 | 3 | - | 230 | 3 | 65 | 2.2 FLA | 0.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 230 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EB30-..460V | D | CB | Allen-Bradley | 140MG-H8P-B30 | 480 | 3 | 65 | 3 | - | 480 | 3 | 65 | 3.0 FLA | 1.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 480 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EB30-..575V | D | CB | Allen-Bradley | 140MG-H8P-B30 | 600 | 3 | 25 | 3 | - | 600 | 3 | 25 | 2.7 FLA | 2 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 600 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EB70-..200V | D | CB | Allen-Bradley | 140MG-H8P-B70 | 200 | 3 | 65 | 7 | - | 200 | 3 | 65 | 6.9 FLA | 1.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 200 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EB70-..230V | D | CB | Allen-Bradley | 140MG-H8P-B70 | 230 | 3 | 65 | 7 | - | 230 | 3 | 65 | 6.8 FLA | 2 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 230 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EB70-..460V | D | CB | Allen-Bradley | 140MG-H8P-B70 | 480 | 3 | 65 | 7 | - | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 480 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EB70-..575V | D | CB | Allen-Bradley | 140MG-H8P-B70 | 600 | 3 | 25 | 7 | - | 600 | 3 | 25 | 6.1 FLA | 5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 600 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EC15-..200V | D | CB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | 65 | 15 | - | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 200 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EC15-..230V | D | CB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | 65 | 15 | - | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 230 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EC15-..460V | D | CB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | 65 | 15 | - | 480 | 3 | 65 | 14.0 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 480 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EC15-..575V | D | CB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | 25 | 15 | - | 600 | 3 | 25 | 11.0 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 600 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EC30-..200V | D | CB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113H-C30...-E300EC30-..230V | D | CB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113H-C30...-E300EC30-..460V | D | CB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113H-C30...-E300EC30-..575V | D | CB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | 25 | 30 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113H-C30...-E300EC30-..200V | D | CB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 200 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EC30-..230V | D | CB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 230 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EC30-..460V | D | CB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 480 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EC30-..575V | D | CB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | 25 | 30 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 600 | 3 | 5 | 0.5-30 | -
AB113H-C37...-E300FC50-..200V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | --- | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113H-C37...-E300FC50-..230V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | --- | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113H-C37...-E300FC50-..460V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | --- | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113H-C37...-E300FC50-..575V | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | --- | 50 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113H-C43...-E300FC80-..200V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 200 | 3 | --- | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113H-C43...-E300FC80-..230V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 230 | 3 | --- | 80 | - | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113H-C43...-E300FC80-..460V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 480 | 3 | --- | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113H-C43...-E300FC80-..575V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 600 | 3 | --- | 80 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113H-C55...-E300GC80-..200V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 200 | 3 | --- | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113H-C55...-E300GC80-..230V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 230 | 3 | --- | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113H-C55...-E300GC80-..460V | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 480 | 3 | --- | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113H-C55...-E300GC80-..575V | D | CB | Allen-Bradley | 140MG-H8P-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113H-C60...-E300GD12-..200V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113H-C60...-E300GD12-..230V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113H-C60...-E300GD12-..460V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113H-C60...-E300GD12-..575V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | --- | 125 | - | 600 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113H-C72...-E300GD12-..200V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113H-C72...-E300GD12-..230V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 68 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113H-C72...-E300GD12-..460V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113H-C72...-E300GD12-..575V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | --- | 125 | - | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113H-C85...-E300GD12-..200V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113H-C85...-E300GD12-..230V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113H-C85...-E300GD12-..460V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113H-C85...-E300GD12-..575V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | --- | 125 | - | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113H-C97...-E300VD12-..200V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113H-C97...-E300VD12-..230V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113H-C97...-E300VD12-..460V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113H-C97...-E300VD12-..575V | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | --- | 125 | - | 600 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113H-C30G...-E300EB30-..200V | D | CB | Allen-Bradley | 140MG-G8P-B30 | 200 | 3 | 65 | 3 | - | 200 | 3 | 65 | 2.5 FLA | 0.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 200 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EB30-..230V | D | CB | Allen-Bradley | 140MG-G8P-B30 | 230 | 3 | 65 | 3 | - | 230 | 3 | 65 | 2.2 FLA | 0.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 230 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EB30-..460V | D | CB | Allen-Bradley | 140MG-G8P-B30 | 480 | 3 | 65 | 3 | - | 480 | 3 | 65 | 3.0 FLA | 1.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 480 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EB30-..575V | D | CB | Allen-Bradley | 140MG-G8P-B30 | 600Y/347 | 3 | 25 | 3 | - | 600Y/347 | 3 | 25 | 2.7 FLA | 2 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 600 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EB70-..200V | D | CB | Allen-Bradley | 140MG-G8P-B70 | 200 | 3 | 65 | 7 | - | 200 | 3 | 65 | 6.9 FLA | 1.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 200 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EB70-..230V | D | CB | Allen-Bradley | 140MG-G8P-B70 | 230 | 3 | 65 | 7 | - | 230 | 3 | 65 | 6.8 FLA | 2 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 230 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EB70-..460V | D | CB | Allen-Bradley | 140MG-G8P-B70 | 480 | 3 | 65 | 7 | - | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 480 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EB70-..575V | D | CB | Allen-Bradley | 140MG-G8P-B70 | 600Y/347 | 3 | 25 | 7 | - | 600Y/347 | 3 | 25 | 6.1 FLA | 5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 600 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC15-..200V | D | CB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | 65 | 15 | - | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 200 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC15-..230V | D | CB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | 65 | 15 | - | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 230 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC15-..460V | D | CB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | 65 | 15 | - | 480 | 3 | 65 | 14.0 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 480 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC15-..575V | D | CB | Allen-Bradley | 140MG-G8P-C15 | 600Y/347 | 3 | 25 | 15 | - | 600Y/347 | 3 | 25 | 11.0 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 600 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC30-..200V | D | CB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 200 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC30-..230V | D | CB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 230 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC30-..460V | D | CB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 480 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC30-..575V | D | CB | Allen-Bradley | 140MG-G8P-C30 | 600Y/347 | 3 | 25 | 30 | - | 600Y/347 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 600 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC50-..200V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | --- | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 200 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC50-..230V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | --- | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 230 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC50-..460V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | --- | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 480 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC50-..575V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 600Y/347 | 3 | --- | 50 | - | 600Y/347 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-C55 | 600 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EB30-..200V-T | D | CB | Allen-Bradley | 140MG-H8P-B30 | 200 | 3 | 65 | 3 | - | 200 | 3 | 65 | 2.5 FLA | 0.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 200 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EB30-..230V-T | D | CB | Allen-Bradley | 140MG-H8P-B30 | 230 | 3 | 65 | 3 | - | 230 | 3 | 65 | 2.2 FLA | 0.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 230 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EB30-..460V-T | D | CB | Allen-Bradley | 140MG-H8P-B30 | 480 | 3 | 65 | 3 | - | 480 | 3 | 65 | 3.0 FLA | 1.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 480 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EB30-..575V-T | D | CB | Allen-Bradley | 140MG-H8P-B30 | 600 | 3 | 25 | 3 | - | 600 | 3 | 25 | 2.7 FLA | 2 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 600 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EB70-..200V-T | D | CB | Allen-Bradley | 140MG-H8P-B70 | 200 | 3 | 65 | 7 | - | 200 | 3 | 65 | 6.9 FLA | 1.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 200 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EB70-..230V-T | D | CB | Allen-Bradley | 140MG-H8P-B70 | 230 | 3 | 65 | 7 | - | 230 | 3 | 65 | 6.8 FLA | 2 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 230 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EB70-..460V-T | D | CB | Allen-Bradley | 140MG-H8P-B70 | 480 | 3 | 65 | 7 | - | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 480 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EB70-..575V-T | D | CB | Allen-Bradley | 140MG-H8P-B70 | 600 | 3 | 25 | 7 | - | 600 | 3 | 25 | 6.1 FLA | 5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 600 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EC15-..200V-T | D | CB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | 65 | 15 | - | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 200 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EC15-..230V-T | D | CB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | 65 | 15 | - | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 230 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EC15-..460V-T | D | CB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | 65 | 15 | - | 480 | 3 | 65 | 14.0 FLA | 10 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 480 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EC15-..575V-T | D | CB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | 25 | 15 | - | 600 | 3 | 25 | 11.0 FLA | 10 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 600 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EC30-..200V-T | D | CB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 200 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EC30-..230V-T | D | CB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 230 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EC30-..460V-T | D | CB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 480 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EC30-..575V-T | D | CB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | 25 | 30 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 600 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EB30-..200V-T | D | CB | Allen-Bradley | 140MG-G8P-B30 | 200 | 3 | 65 | 3 | - | 200 | 3 | 65 | 2.5 FLA | 0.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 200 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EB30-..230V-T | D | CB | Allen-Bradley | 140MG-G8P-B30 | 230 | 3 | 65 | 3 | - | 230 | 3 | 65 | 2.2 FLA | 0.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 230 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EB30-..460V-T | D | CB | Allen-Bradley | 140MG-G8P-B30 | 480 | 3 | 65 | 3 | - | 480 | 3 | 65 | 3.0 FLA | 1.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 480 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EB30-..575V-T | D | CB | Allen-Bradley | 140MG-G8P-B30 | 600Y/347 | 3 | 25 | 3 | - | 600Y/347 | 3 | 25 | 2.7 FLA | 2 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 600 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EB70-..200V-T | D | CB | Allen-Bradley | 140MG-G8P-B70 | 200 | 3 | 65 | 7 | - | 200 | 3 | 65 | 6.9 FLA | 1.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 200 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EB70-..230V-T | D | CB | Allen-Bradley | 140MG-G8P-B70 | 230 | 3 | 65 | 7 | - | 230 | 3 | 65 | 6.8 FLA | 2 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 230 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EB70-..460V-T | D | CB | Allen-Bradley | 140MG-G8P-B70 | 480 | 3 | 65 | 7 | - | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 480 | 3 | 5 | 0.5-23 | -
AB113H-C30G...-E300EB70-..575V-T | D | CB | Allen-Bradley | 140MG-G8P-B70 | 600Y/347 | 3 | 25 | 7 | - | 600Y/347 | 3 | 25 | 6.1 FLA | 5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 600 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC15-..200V-T | D | CB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | 65 | 15 | - | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 200 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC15-..230V-T | D | CB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | 65 | 15 | - | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 230 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC15-..460V-T | D | CB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | 65 | 15 | - | 480 | 3 | 65 | 14.0 FLA | 10 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 480 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC15-..575V-T | D | CB | Allen-Bradley | 140MG-G8P-C15 | 600Y/347 | 3 | 25 | 15 | - | 600Y/347 | 3 | 25 | 11.0 FLA | 10 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 600 | 3 | 5 | 0.5-23 | -
AB113H-C30G...-E300EC30-..200V-T | D | CB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 200 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC30-..230V-T | D | CB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 230 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC30-..460V-T | D | CB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 480 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC30-..575V-T | D | CB | Allen-Bradley | 140MG-G8P-C30 | 600Y/347 | 3 | 25 | 30 | - | 600Y/347 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 600 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC50-..200V-T | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | --- | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 200 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC50-..230V-T | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | --- | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 230 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC50-..460V-T | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | --- | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 480 | 3 | 5 | 0.5-30 | -
AB113H-C30G...-E300EC50-..575V-T | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 600Y/347 | 3 | --- | 50 | - | 600Y/347 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8, | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-30A-T | 600 | 3 | 5 | 0.5-30 | -
AB113H-C30...-E300EC30-..200V-T | D | CB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113H-C30...-E300EC30-..230V-T | D | CB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113H-C30...-E300EC30-..460V-T | D | CB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113H-C30...-E300EC30-..575V-T | D | CB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | 25 | 30 | - | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113H-C37...-E300FC50-..200V-T | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | --- | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113H-C37...-E300FC50-..230V-T | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | --- | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113H-C37...-E300FC50-..460V-T | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | --- | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113H-C37...-E300FC50-..575V-T | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | --- | 50 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113H-C43...-E300FC80-..200V-T | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 200 | 3 | --- | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113H-C43...-E300FC80-..230V-T | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 230 | 3 | --- | 80 | - | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113H-C43...-E300FC80-..460V-T | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 480 | 3 | --- | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113H-C43...-E300FC80-..575V-T | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 600 | 3 | --- | 80 | - | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113H-C55...-E300GC80-..200V-T | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 200 | 3 | --- | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113H-C55...-E300GC80-..230V-T | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 230 | 3 | --- | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113H-C55...-E300GC80-..460V-T | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 480 | 3 | --- | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113H-C55...-E300GC80-..575V-T | D | CB | Allen-Bradley | 140MG-H8P-C80 | 600 | 3 | 25 | 80 | - | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113H-C30G...-E300EC30-..200V-T | D | CB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113H-C30G...-E300EC30-..230V-T | D | CB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113H-C30G...-E300EC30-..460V-T | D | CB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113H-C30G...-E300EC30-..575V-T | D | CB | Allen-Bradley | 140MG-G8P-C30 | 600Y/347 | 3 | 25 | 30 | - | 600Y/347 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113H-C30G...-E300FC50-..200V-T | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | --- | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113H-C30G...-E300FC50-..230V-T | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | --- | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113H-C30G...-E300FC50-..460V-T | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | --- | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113H-C30G...-E300FC50-..575V-T | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 600Y/347 | 3 | --- | 50 | - | 600Y/347 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113H-C37G...-E300FC50-..200V-T | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | --- | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113H-C37G...-E300FC50-..230V-T | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | --- | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113H-C37G...-E300FC50-..460V-T | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | --- | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113H-C37G...-E300FC50-..575V-T | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 600Y/347 | 3 | --- | 50 | - | 600Y/347 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113H-C43G...-E300FC80-..200V-T | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 200 | 3 | --- | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113H-C43G...-E300FC80-..230V-T | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 230 | 3 | --- | 80 | - | 230 | 3 | 65 | 42 FLA | 15 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113H-C43G...-E300FC80-..460V-T | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 480 | 3 | --- | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113H-C43G...-E300FC50-..575V-T | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 600Y/347 | 3 | --- | 50 | - | 600Y/347 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 600 | 3 | 5 | 6-60 | -
AB113H-C55G...-E300GC80-..200V-T | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 200 | 3 | --- | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 200 | 3 | 5 | 6-60 | -
AB113H-C55G...-E300GC80-..230V-T | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 230 | 3 | --- | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 230 | 3 | 5 | 6-60 | -
AB113H-C55G...-E300GC80-..460V-T | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 480 | 3 | --- | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-T | 480 | 3 | 5 | 6-60 | -
AB113H-C30G...-E300EC30-..200V | D | CB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | 65 | 30 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113H-C30G...-E300EC30-..230V | D | CB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | 65 | 30 | - | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113H-C30G...-E300EC30-..460V | D | CB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | 65 | 30 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113H-C30G...-E300EC30-..575V | D | CB | Allen-Bradley | 140MG-G8P-C30 | 600Y/347 | 3 | 25 | 30 | - | 600Y/347 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113H-C30G...-E300FC50-..200V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | --- | 50 | - | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113H-C30G...-E300FC50-..230V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | --- | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113H-C30G...-E300FC50-..460V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | --- | 50 | - | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113H-C30G...-E300FC50-..575V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 600Y/347 | 3 | --- | 50 | - | 600Y/347 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113H-C37G...-E300FC50-..200V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | --- | 50 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113H-C37G...-E300FC50-..230V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | --- | 50 | - | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113H-C37G...-E300FC50-..460V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | --- | 50 | - | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113H-C37G...-E300FC50-..575V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 600Y/347 | 3 | --- | 50 | - | 600Y/347 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113H-C43G...-E300FC80-..200V | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 200 | 3 | --- | 80 | - | 200 | 3 | 65 | 32.2 FLA | 10 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113H-C43G...-E300FC80-..230V | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 230 | 3 | --- | 80 | - | 230 | 3 | 65 | 42 FLA | 15 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113H-C43G...-E300FC80-..460V | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 480 | 3 | --- | 80 | - | 480 | 3 | 65 | 40 FLA | 30 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113H-C43G...-E300FC50-..575V | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 600Y/347 | 3 | --- | 50 | - | 600Y/347 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 600 | 3 | 5 | 6-54 | -
AB113H-C55G...-E300GC80-..200V | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 200 | 3 | --- | 80 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 200 | 3 | 5 | 6-54 | -
AB113H-C55G...-E300GC80-..230V | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 230 | 3 | --- | 80 | - | 230 | 3 | 65 | 54 FLA | 20 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 230 | 3 | 5 | 6-54 | -
AB113H-C55G...-E300GC80-..460V | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 480 | 3 | --- | 80 | - | 480 | 3 | 65 | 52 FLA | 40 | 10800 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-60A-C55 | 480 | 3 | 5 | 6-54 | -
AB113H-C60G...-E300GD12-..200V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113H-C60G...-E300GD12-..230V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113H-C60G...-E300GD12-..460V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113H-C60G...-E300GD12-..575V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 600Y/347 | 3 | --- | 125 | - | 600Y/347 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113H-C72G...-E300GD12-..200V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113H-C72G...-E300GD12-..230V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 68 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113H-C72G...-E300GD12-..460V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113H-C72G...-E300GD12-..575V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 600Y/347 | 3 | --- | 125 | - | 600Y/347 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113H-C85G...-E300GD12-..200V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113H-C85G...-E300GD12-..230V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113H-C85G...-E300GD12-..460V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113H-C85G...-E300GD12-..575V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 600Y/347 | 3 | --- | 125 | - | 600Y/347 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113H-C97G...-E300VD12-..200V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | --- | 125 | - | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 200 | 3 | 10 | 10-97 | -
AB113H-C97G...-E300VD12-..230V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | --- | 125 | - | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 230 | 3 | 10 | 10-97 | -
AB113H-C97G...-E300VD12-..460V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | --- | 125 | - | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 480 | 3 | 10 | 10-97 | -
AB113H-C97G...-E300VD12-..575V | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 600Y/347 | 3 | --- | 125 | - | 600Y/347 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-100A-C97 | 600 | 3 | 10 | 10-97 | -
AB113H-D115G...-E300VD12-..200V | D | CB | Allen-Bradley | 140MG-J8*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 120 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113H-D115G...-E300VD12-..230V | D | CB | Allen-Bradley | 140MG-J8*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 104 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113H-D115G...-E300VD12-..460V | D | CB | Allen-Bradley | 140MG-J8*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113H-D115G...-E300VD12-..575V | D | CB | Allen-Bradley | 140MG-J8*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 99 FLA | 100 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113H-D140G...-E300VD12-..200V | D | CB | Allen-Bradley | 140MG-J8*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 120 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113H-D140G...-E300VD12-..230V | D | CB | Allen-Bradley | 140MG-J8*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 130 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113H-D140G...-E300VD12-..460V | D | CB | Allen-Bradley | 140MG-J8*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 124 FLA | 100 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113H-D140G...-E300VD12-..575V | D | CB | Allen-Bradley | 140MG-J8*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 125 FLA | 125 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113H-D180G...-E300VD12-..200V | D | CB | Allen-Bradley | 140MG-J8*3-D25 | 200 | 3 | 65 | 250 | - | 200 | 3 | 65 | 150 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 200 | 3 | 10 | 150 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113H-D180G...-E300VD12-..230V | D | CB | Allen-Bradley | 140MG-J8*3-D25 | 230 | 3 | 65 | 250 | - | 230 | 3 | 65 | 154 FLA | 60 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 230 | 3 | 10 | 154 | 60
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113H-D180G...-E300VD12-..460V | D | CB | Allen-Bradley | 140MG-J8*3-D25 | 480 | 3 | 65 | 250 | - | 480 | 3 | 65 | 156 FLA | 150 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 480 | 3 | 10 | 156 | 150
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113H-D180G...-E300VD12-..575V | D | CB | Allen-Bradley | 140MG-J8*3-D25 | 600 | 3 | 25 | 250 | - | 600 | 3 | 25 | 144 FLA | 150 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D180 | 600 | 3 | 10 | 144 | 150
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113H-D115...-E1HD15-..200V | D | ICB | Allen-Bradley | 140MG-I8P-D15 | 200 | 3 | --- | 150 | - | 200 | 3 | 35 | 92 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EEHF | 200 | 3 | 10 | 30-150 | -
AB113H-D115...-E1HD15-..230V | D | ICB | Allen-Bradley | 140MG-I8P-D15 | 230 | 3 | --- | 150 | - | 230 | 3 | 35 | 104 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-EEHF | 230 | 3 | 10 | 30-150 | -
AB113H-D115...-E1HD15-..460V | D | ICB | Allen-Bradley | 140MG-I8P-D15 | 480 | 3 | --- | 150 | - | 480 | 3 | 35 | 96 FLA | 75 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EEHF | 480 | 3 | 10 | 30-150 | -
AB113H-D115...-E1HD15-..575V | D | ICB | Allen-Bradley | 140MG-I8P-D15 | 600Y/347 | 3 | --- | 150 | - | 600Y/347 | 3 | 10 | 99 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-EEHF | 600 | 3 | 10 | 30-150 | -
AB113H-D140...-E1HD15-..200V | D | ICB | Allen-Bradley | 140MG-I8P-D15 | 200 | 3 | --- | 150 | - | 200 | 3 | 35 | 120 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-EEHF | 200 | 3 | 10 | 30-150 | -
AB113H-D140...-E1HD15-..230V | D | ICB | Allen-Bradley | 140MG-I8P-D15 | 230 | 3 | --- | 150 | - | 230 | 3 | 35 | 130 FLA | 50 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-EEHF | 230 | 3 | 10 | 30-150 | -
AB113H-D140...-E1HD15-..460V | D | ICB | Allen-Bradley | 140MG-I8P-D15 | 480 | 3 | --- | 150 | - | 480 | 3 | 35 | 124 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-EEHF | 480 | 3 | 10 | 30-150 | -
AB113H-D140...-E1HD15-..575V | D | ICB | Allen-Bradley | 140MG-I8P-D15 | 600Y/347 | 3 | --- | 150 | - | 600Y/347 | 3 | 10 | 125 FLA | 125 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-EEHF | 600 | 3 | 10 | 30-150 | -
AB113H-D115...-E3HD15-..200V | D | ICB | Allen-Bradley | 140MG-I8P-D15 | 200 | 3 | --- | 150 | - | 200 | 3 | 35 | 92 FLA | 30 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 92 | 30
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113H-D115...-E3HD15-..230V | D | ICB | Allen-Bradley | 140MG-I8P-D15 | 230 | 3 | --- | 150 | - | 230 | 3 | 35 | 104 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113H-D115...-E3HD15-..460V | D | ICB | Allen-Bradley | 140MG-I8P-D15 | 480 | 3 | --- | 150 | - | 480 | 3 | 35 | 96 FLA | 75 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113H-D115...-E3HD15-..575V | D | ICB | Allen-Bradley | 140MG-I8P-D15 | 600Y/347 | 3 | --- | 150 | - | 600Y/347 | 3 | 10 | 99 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113H-D140...-E3HD15-..200V | D | ICB | Allen-Bradley | 140MG-I8P-D15 | 200 | 3 | --- | 150 | - | 200 | 3 | 35 | 120 FLA | 40 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-EC*FF | 200 | 3 | 10 | 28-140 | -
AB113H-D140...-E3HD15-..230V | D | ICB | Allen-Bradley | 140MG-I8P-D15 | 230 | 3 | --- | 150 | - | 230 | 3 | 35 | 130 FLA | 50 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-EC*FF | 230 | 3 | 10 | 28-140 | -
AB113H-D140...-E3HD15-..460V | D | ICB | Allen-Bradley | 140MG-I8P-D15 | 480 | 3 | --- | 150 | - | 480 | 3 | 35 | 124 FLA | 100 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-EC*FF | 480 | 3 | 10 | 28-140 | -
AB113H-D140...-E3HD15-..575V | D | ICB | Allen-Bradley | 140MG-I8P-D15 | 600Y/347 | 3 | --- | 150 | - | 600Y/347 | 3 | 10 | 125 FLA | 125 | 10800 | 1,5,6,7 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-EC*FF | 600 | 3 | 10 | 28-140 | -
AB113H-D115G...-E300VD15-..200V | D | CB | Allen-Bradley | 140MG-I8*3-D15 | 200 | 3 | 65 | 150 | - | 200 | 3 | 35 | 120 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113H-D115G...-E300VD15-..230V | D | CB | Allen-Bradley | 140MG-I8*3-D15 | 230 | 3 | 65 | 150 | - | 230 | 3 | 35 | 104 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113H-D115G...-E300VD15-..460V | D | CB | Allen-Bradley | 140MG-I8*3-D15 | 480 | 3 | 65 | 150 | - | 480 | 3 | 35 | 96 FLA | 75 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113H-D115G...-E300VD15-..575V | D | CB | Allen-Bradley | 140MG-I8*3-D15 | 600Y/347 | 3 | 25 | 150 | - | 600Y/347 | 3 | 10 | 99 FLA | 100 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
AB113H-D140G...-E300VD15-..200V | D | CB | Allen-Bradley | 140MG-I8*3-D15 | 200 | 3 | 65 | 150 | - | 200 | 3 | 35 | 120 FLA | 40 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 200 | 3 | 10 | 20-200 | -
AB113H-D140G...-E300VD15-..230V | D | CB | Allen-Bradley | 140MG-I8*3-D15 | 230 | 3 | 65 | 150 | - | 230 | 3 | 35 | 130 FLA | 50 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 230 | 3 | 10 | 20-200 | -
AB113H-D140G...-E300VD15-..460V | D | CB | Allen-Bradley | 140MG-I8*3-D15 | 480 | 3 | 65 | 150 | - | 480 | 3 | 35 | 124 FLA | 100 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 480 | 3 | 10 | 20-200 | -
AB113H-D140G...-E300VD15-..575V | D | CB | Allen-Bradley | 140MG-I8*3-D15 | 600Y/347 | 3 | 25 | 150 | - | 600Y/347 | 3 | 10 | 125 FLA | 125 | 3840 | 1,5,6,7,8 | E125316 Vol 1 Sec 7
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
|  | OLR | Allen-Bradley | 193-ESM-###-200A-D180 | 600 | 3 | 10 | 20-200 | -
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & OLR shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the OLR heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type C & D Combination Motor Controllers).
(6) = The enclosure shall have the minimum number of hinges and latches as tabulated below:
(8) = Part numbers 193-ESM-###-30A-C23, 193-ESM-###-60A-C55, and 193-ESM-###-100A-C97 are sensing modules only. The complete overload relay consists of one sensing module, one control module, and one communication module, which can be factory or field assembled. The associated control module part numbers are 193-EIO-63-24D, 193-EIO-43-120 or 193-EIO-43-240, and the communication module is 193-ECM-ETR.
|  | Database ID Nos. |  | No. of Hinges | No. of Latches
|  | AB113H-C30… |  | 2 | 2
|  | AB113H-C37… |  | 2 | 2
|  | AB113H-C43… |  | 2 | 2
|  | AB113H-C55… |  | 2 | 2
|  | AB113H-C60… |  | 2 | 2
|  | AB113H-C72… |  | 2 | 2
|  | AB113H-C85… |  | 2 | 2
|  | AB113H-C97… |  | 2 | 2
|  | AB113H-D115… |  | 2 | 2
|  | AB113H-D140… |  | 2 | 2
|  | AB113H-D180… |  | 2 | 2
|  | AB113H-D210… |  | 3 | 2
|  | AB113H-D250… |  | 3 | 2
|  | AB113H-D300… |  | 3 | 2
|  | AB113H-D420… |  | 3 | 3
|  | AB113H-D630… |  | Continuous | 8
|  | AB113H-D860… |  | Continuous | 8
(7) = Specific conductor size required for internal wiring between components as tabulated below:
|  | Database ID Nos. |  | Contactor Model | Max AWG
|  | AB113H-C37… |  | 100-C37 | 8
|  | AB113H-C43… |  | 100-C43 | 8
|  | AB113H-C55… |  | 100-C55 | 6
|  | AB113H-C60… |  | 100-C60 | 6
|  | AB113H-C72… |  | 100-C72 | 4
|  | AB113H-C85… |  | 100-C85 | 4
|  | AB113H-C97… |  | 100-C97 | 3
|  | AB113H-D115 |  | 100-D115 | 2
|  | AB113H-D140 |  | 100-D140 | 1
|  | AB113H-D250 |  | 100-D250 | (2) 1

## 113J and 193T1
[16 empty] | Issued: | 2017-10-10
[16 empty] | Revised: | 2023-04-19
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number [1] | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP rating | Enclosure Volume, CU inches
AB113J-C30...-C25H-..200V | C | MPCB | Allen-Bradley | 140MG-H8E-C25 | 200 | 3 | --- | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 17.5 | 5
AB113J-C30...-C25H-..230V | C | MPCB | Allen-Bradley | 140MG-H8E-C25 | 230 | 3 | --- | 25 | - | 230 | 3 | 65 | 22 | 7.5 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 22 | 7.5
AB113J-C30...-C25H-..480V | C | MPCB | Allen-Bradley | 140MG-H8E-C25 | 480 | 3 | --- | 25 | - | 480 | 3 | 65 | 21 | 15 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 21 | 15
AB113J-C30...-C25H-..575V | C | MPCB | Allen-Bradley | 140MG-H8E-C25 | 600 | 3 | --- | 25 | - | 600 | 3 | 25 | 22 | 20 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 22 | 20
AB113J-C30...-C60H-..200V | C | MPCB | Allen-Bradley | 140MG-H8E-C60 | 200 | 3 | --- | 60 | - | 200 | 3 | 65 | 11 | 7.5 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 11 | 7.5
AB113J-C30...-C60H-..230V | C | MPCB | Allen-Bradley | 140MG-H8E-C60 | 230 | 3 | --- | 60 | - | 230 | 3 | 65 | 25.3 | 10 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 25.3 | 10
AB113J-C30...-C60H-..480V | C | MPCB | Allen-Bradley | 140MG-H8E-C60 | 480 | 3 | --- | 60 | - | 480 | 3 | 65 | 27 | 20 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
AB113J-C30...-C60H-..600V | C | MPCB | Allen-Bradley | 140MG-H8E-C60 | 600 | 3 | --- | 60 | - | 600 | 3 | 25 | 27 | 25 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
AB113J-C37...-C60H-..200V | C | MPCB | Allen-Bradley | 140MG-H8E-C60 | 200 | 3 | --- | 60 | - | 200 | 3 | 65 | 32.2 | 10 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
AB113J-C37...-C60H-..230V | C | MPCB | Allen-Bradley | 140MG-H8E-C60 | 230 | 3 | --- | 60 | - | 230 | 3 | 65 | 28 | 10 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
AB113J-C37...-C60H-..460V | C | MPCB | Allen-Bradley | 140MG-H8E-C60 | 480 | 3 | --- | 60 | - | 480 | 3 | 65 | 34 | 25 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
AB113J-C37...-C60H-..575V | C | MPCB | Allen-Bradley | 140MG-H8E-C60 | 600 | 3 | --- | 60 | - | 600 | 3 | 25 | 32 | 30 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
AB113J-C43...-C60H-..200V | C | MPCB | Allen-Bradley | 140MG-H8E-C60 | 200 | 3 | --- | 60 | - | 200 | 3 | 65 | 32.3 | 10 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
AB113J-C43...-C60H-..230V | C | MPCB | Allen-Bradley | 140MG-H8E-C60 | 230 | 3 | --- | 60 | - | 230 | 3 | 65 | 42 | 15 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
AB113J-C43...-C60H-..460V | C | MPCB | Allen-Bradley | 140MG-H8E-C60 | 480 | 3 | --- | 60 | - | 480 | 3 | 65 | 40 | 30 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
AB113J-C43...-C60H-..575V | C | MPCB | Allen-Bradley | 140MG-H8E-C60 | 600 | 3 | --- | 60 | - | 600 | 3 | 25 | 32 | 30 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
AB113J-C55...-C60H-..200V | C | MPCB | Allen-Bradley | 140MG-H8E-C60 | 200 | 3 | --- | 60 | - | 200 | 3 | 65 | 48.3 | 15 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
AB113J-C55...-C60H-..230V | C | MPCB | Allen-Bradley | 140MG-H8E-C60 | 230 | 3 | --- | 60 | - | 230 | 3 | 65 | 54 | 20 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
AB113J-C55...-C60H-..460V | C | MPCB | Allen-Bradley | 140MG-H8E-C60 | 480 | 3 | --- | 60 | - | 480 | 3 | 65 | 52 | 40 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
AB113J-C55...-C60H-..575V | C | CB | Allen-Bradley | 140MG-H8E-C60 | 600 | 3 | 25 | 60 | - | 600 | 3 | 25 | 41 | 40 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
AB113J-C60...-D10H-..200V | C | MPCB | Allen-Bradley | 140MG-H8E-D10 | 200 | 3 | --- | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
AB113J-C60...-D10H-..230V | C | MPCB | Allen-Bradley | 140MG-H8E-D10 | 230 | 3 | --- | 100 | - | 230 | 3 | 65 | 54 | 20 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
AB113J-C60...-D10H-..460V | C | MPCB | Allen-Bradley | 140MG-H8E-D10 | 480 | 3 | --- | 100 | - | 480 | 3 | 65 | 52 | 40 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
AB113J-C60...-D10H-..575V | C | MPCB | Allen-Bradley | 140MG-H8E-D10 | 600 | 3 | --- | 100 | - | 600 | 3 | 25 | 52 | 50 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
AB113J-C72...-D10H-..200V | C | MPCB | Allen-Bradley | 140MG-H8E-D10 | 200 | 3 | --- | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
AB113J-C72...-D10H-..230V | C | MPCB | Allen-Bradley | 140MG-H8E-D10 | 230 | 3 | --- | 100 | - | 230 | 3 | 65 | 68 | 25 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
AB113J-C72...-D10H-..460V | C | MPCB | Allen-Bradley | 140MG-H8E-D10 | 480 | 3 | --- | 100 | - | 480 | 3 | 65 | 65 | 50 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
AB113J-C72...-D10H-..575V | C | MPCB | Allen-Bradley | 140MG-H8E-D10 | 600 | 3 | --- | 100 | - | 600 | 3 | 25 | 62 | 60 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
AB113J-C85...-D10H-..200V | C | MPCB | Allen-Bradley | 140MG-H8E-D10 | 200 | 3 | --- | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
AB113J-C85...-D10H-..230V | C | MPCB | Allen-Bradley | 140MG-H8E-D10 | 230 | 3 | --- | 100 | - | 230 | 3 | 65 | 80 | 30 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
AB113J-C85...-D10H-..460V | C | MPCB | Allen-Bradley | 140MG-H8E-D10 | 480 | 3 | --- | 100 | - | 480 | 3 | 65 | 77 | 60 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
AB113J-C85...-D10H-..575V | C | MPCB | Allen-Bradley | 140MG-H8E-D10 | 600 | 3 | --- | 100 | - | 600 | 3 | 25 | 62 | 60 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
AB113J-C97...-D10H-..200V | C | MPCB | Allen-Bradley | 140MG-H8E-D10 | 200 | 3 | --- | 100 | - | 200 | 3 | 65 | 92 | 30 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
AB113J-C97...-D10H-..230V | C | MPCB | Allen-Bradley | 140MG-H8E-D10 | 230 | 3 | --- | 100 | - | 230 | 3 | 65 | 80 | 30 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
AB113J-C97...-D10H-..460V | C | MPCB | Allen-Bradley | 140MG-H8E-D10 | 480 | 3 | --- | 100 | - | 480 | 3 | 65 | 96 | 75 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
AB113J-C97...-D10H-..575V | C | MPCB | Allen-Bradley | 140MG-H8E-D10 | 600 | 3 | --- | 100 | - | 600 | 3 | 25 | 77 | 75 | 3840 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
AB113J-D115...-D15J-..200V | C | MPCB | Allen-Bradley | 140MG-J8E-D15 | 200 | 3 | --- | 150 | - | 200 | 3 | 65 | 92 | 30 | 10800 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-D115 | 200 | 3 | 10 | 92 | 30
AB113J-D115...-D15J-..230V | C | MPCB | Allen-Bradley | 140MG-J8E-D15 | 230 | 3 | --- | 150 | - | 230 | 3 | 65 | 104 | 40 | 10800 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-D115 | 230 | 3 | 10 | 104 | 40
AB113J-D115...-D15J-..460V | C | MPCB | Allen-Bradley | 140MG-J8E-D15 | 480 | 3 | --- | 150 | - | 480 | 3 | 65 | 96 | 75 | 10800 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-D115 | 480 | 3 | 10 | 96 | 75
AB113J-D115...-D15J-..575V | C | MPCB | Allen-Bradley | 140MG-J8E-D15 | 600 | 3 | --- | 150 | - | 600 | 3 | 25 | 99 | 100 | 10800 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-D115 | 600 | 3 | 10 | 99 | 100
AB113J-D140...-D15J-..200V | C | MPCB | Allen-Bradley | 140MG-J8E-D15 | 200 | 3 | --- | 150 | - | 200 | 3 | 65 | 120 | 40 | 10800 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-D140 | 200 | 3 | 10 | 120 | 40
AB113J-D140...-D15J-..230V | C | MPCB | Allen-Bradley | 140MG-J8E-D15 | 230 | 3 | --- | 150 | - | 230 | 3 | 65 | 130 | 50 | 10800 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-D140 | 230 | 3 | 10 | 130 | 50
AB113J-D140...-D15J-..460V | C | MPCB | Allen-Bradley | 140MG-J8E-D15 | 480 | 3 | --- | 150 | - | 480 | 3 | 65 | 124 | 100 | 10800 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-D140 | 480 | 3 | 10 | 124 | 100
AB113J-D140...-D15J-..575V | C | MPCB | Allen-Bradley | 140MG-J8E-D15 | 600 | 3 | --- | 150 | - | 600 | 3 | 25 | 125 | 125 | 10800 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-D140 | 600 | 3 | 10 | 125 | 125
AB193T1-001-480V.01 | C | CB | Allen-Bradley | 140UT-D7D3-C10 | 480Y/277V | 3 | 65 | 10 | -- | 480Y/277V | 3 | 30 | 2.1 | 1 | 956 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C09-D10 | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen-Bradley | 193-T1AB25 | 600 | 3 | 5 | 2.5 | --
AB193T1-002-480V.01 | C | CB | Allen-Bradley | 140UT-D7D3-C15 | 480Y/277V | 3 | 65 | 15 | -- | 480Y/277V | 3 | 30 | 3.4 | 2 | 956 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C09-D10 | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen-Bradley | 193-T1AB40 | 600 | 3 | 5 | 4 | --
AB193T1-003-480V.01 | C | CB | Allen-Bradley | 140UT-D7D3-C15 | 480Y/277V | 3 | 65 | 15 | -- | 480Y/277V | 3 | 30 | 4.8 | 3 | 956 | 1, 5, 6, 7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C09-D10 | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen-Bradley | 193-T1AB63 | 600 | 3 | 5 | 6.3 | --
AB193T1-004-480V.01 | C | CB | Allen-Bradley | 140UT-D7D3-C20 | 480Y/277V | 3 | 65 | 20 | -- | 480Y/277V | 3 | 30 | 7.6 | 5 | 956 | 1,5,6,7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C09-D10 | 480 | 3 | 5 | 7.6 | 5
|  | OLR | Allen-Bradley | 193-T1AC10 | 600 | 3 | 5 | 10 | --
AB193T1-005-480V.01 | C | CB | Allen-Bradley | 140UT-D7D3-C20 | 480Y/277V | 3 | 65 | 20 | -- | 480Y/277V | 3 | 30 | 11 | 7.5 | 956 | 1,5,6,7 | E125316 Vol 1 Sec 8
|  | MC | Allen-Bradley | 100-C12-D10 | 480 | 3 | 5 | 11 | 7.5
|  | OLR | Allen-Bradley | 193-T1AC12 | 600 | 3 | 5 | 12 | --
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & OLR shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the OLR heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type C & D Combination Motor Controllers).
(6) = The enclosure shall have the minimum number of hinges and latches as tabulated below:
|  | Database ID Nos. | No. of Hinges | No. of Latches
|  | AB193T1… | 2 | 2
|  | AB113J-C30… | 2 | 2
|  | AB113J-C37… | 2 | 2
|  | AB113J-C43… | 2 | 2
|  | AB113J-C55… | 2 | 2
|  | AB113J-C60… | 2 | 2
|  | AB113J-C72… | 2 | 2
|  | AB113J-C85… | 2 | 2
|  | AB113J-C97… | 2 | 2
|  | AB113J-D115… | 2 | 2
|  | AB113J-D140… | 2 | 2
(7) = Specific conductor size required for internal wiring between components as tabulated below:
|  | Database ID Nos. | Contactor Model | Max AWG
|  | AB193T1… | 100-C09/C12 | 12
|  | AB113J-C30… | 100-C30 | 10
|  | AB113J-C37… | 100-C37 | 8
|  | AB113J-C43… | 100-C43 | 8
|  | AB113J-C55… | 100-C55 | 6
|  | AB113J-C60… | 100-C60 | 6
|  | AB113J-C72… | 100-C72 | 4
|  | AB113J-C85… | 100-C85 | 4
|  | AB113J-C97… | 100-C97 | 3
|  | AB113J-D115… | 100-D115 | 2
|  | AB113J-D140… | 100-D140 | 1
Indicates the current rating of the Motor Protection Circuit Breaker (MPCB)
|  | MPCB Code | MPCB Cat. No. | MPCB Overload Range, A
|  | -C25H | 140MG-H8E-C25 | 10 to 25
|  | -C60H | 140MG-H8E-C60 | 24-60
|  | -D10H | 140MG-H8E-D10 | 40-100
|  | -D15J | 140MG-J8E-D15 | 60-150

## MCP 113H Series C E100
[23 empty] | Issued: | 2021-04-30
Last Revised:
Database Identification Number | [B2] Listed Combination Motor Controller Information | [7 empty] | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability
| Listing Report Information |  |  |  |  | Enclosure or Unit Dimensions
| UL File Number | Report Issue Date YYYY-MM-DD | Volume / Section (Vol#).(Sec#) | Model Number or Product Style/ Designation | Product Description on Page/Figure/Ill. | Enclosure or Unit Height, inches | Width, inches | Depth, inches |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number [1] AND [8] | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP rating | Enclosure Volume, CU inches
AB113H-C16...-E1CC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 200 | 3 | 5 | 1-5 | --
AB113H-C16G...-E1CC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 200 | 3 | 3 | 1-5 | --
AB113H-C16...-E1CC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 230 | 3 | 3 | 1-5 | --
AB113H-C16G...-E1CC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 230 | 3 | 3 | 1-5 | --
AB113H-C16...-E1CC15-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 480 | 3 | 3 | 1-5 | --
AB113H-C16G...-E1CC15-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 480 | 3 | 3 | 1-5 | --
AB113H-C16...-E1CC15-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 3.9 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 600 | 3 | 5 | 17 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 600 | 3 | 3 | 1-5 | --
AB113H-C16...-E1CC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 200 | 3 | 3 | 1-5 | --
AB113H-C16G...-E1CC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 200 | 3 | 3 | 1-5 | --
AB113H-C16...-E1CC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 230 | 3 | 3 | 1-5 | --
AB113H-C16G...-E1CC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 230 | 3 | 3 | 1-5 | --
AB113H-C16...-E1CC15-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 480 | 3 | 3 | 1-5 | --
AB113H-C16G...-E1CC15-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 480 | 3 | 3 | 1-5 | --
AB113H-C16...-E1CC15-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 3.9 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 600 | 3 | 5 | 17 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 600 | 3 | 3 | 1-5 | --
AB113H-C16...-E1DC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 200 | 3 | 5 | 3.2-16 | -
AB113H-C16G...-E1DC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 200 | 3 | 5 | 3.2-16 | -
AB113H-C16...-E1DC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 230 | 3 | 5 | 3.2-16 | -
AB113H-C16G...-E1DC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 230 | 3 | 5 | 3.2-16 | -
AB113H-C16...-E1DC15-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 600 | 3 | 5 | 17 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 600 | 3 | 5 | 3.2-16 | -
AB113H-C16...-E1DC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 200 | 3 | 5 | 3.2-16 | -
AB113H-C16G...-E1DC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 200 | 3 | 5 | 3.2-16 | -
AB113H-C16...-E1DC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 230 | 3 | 5 | 3.2-16 | -
AB113H-C16G...-E1DC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 230 | 3 | 5 | 3.2-16 | -
AB113H-C16...-E1DC15-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 600 | 3 | 5 | 17 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 600 | 3 | 5 | 3.2-16 | -
AB113H-C16...-E1EC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 200 | 3 | 5 | 5.4-27 | -
AB113H-C16G...-E1EC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 200 | 3 | 5 | 5.4-27 | -
AB113H-C16...-E1EC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 230 | 3 | 5 | 5.4-27 | -
AB113H-C16G...-E1EC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 230 | 3 | 5 | 5.4-27 | -
AB113H-C16...-E1EC15-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 600 | 3 | 5 | 17 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 600 | 3 | 5 | 5.4-27 | -
AB113H-C16...-E1EC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 200 | 3 | 5 | 3.2-16 | -
AB113H-C16G...-E1EC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 200 | 3 | 5 | 3.2-16 | -
AB113H-C16...-E1EC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 230 | 3 | 5 | 3.2-16 | -
AB113H-C16G...-E1EC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 230 | 3 | 5 | 3.2-16 | -
AB113H-C16...-EF1EC15-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C16 | 600 | 3 | 5 | 17 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 600 | 3 | 5 | 3.2-16 | -
AB113H-C23...-E1CC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 200 | 3 | 3 | 1-5 | --
AB113H-C23G...-E1CC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 200 | 3 | 3 | 1-5 | --
AB113H-C23...-E1CC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 230 | 3 | 3 | 1-5 | --
AB113H-C23G...-E1CC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 230 | 3 | 3 | 1-5 | --
AB113H-C23...-E1CC15-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 480 | 3 | 5 | 24 | 17.5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 480 | 3 | 3 | 1-5 | --
AB113H-C23G...-E1CC15-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 480 | 3 | 5 | 24 | 17.5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 480 | 3 | 3 | 1-5 | --
AB113H-C23...-E1CC15-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 3.9 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 600 | 3 | 5 | 20 | 18
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 600 | 3 | 3 | 1-5 | --
AB113H-C23...-E1CC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 200 | 3 | 3 | 1-5 | --
AB113H-C23G...-E1CC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 200 | 3 | 3 | 1-5 | --
AB113H-C23...-E1CC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 230 | 3 | 3 | 1-5 | --
AB113H-C23G...-E1CC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 230 | 3 | 3 | 1-5 | --
AB113H-C23...-E1CC15-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 480 | 3 | 5 | 24 | 17.5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 480 | 3 | 3 | 1-5 | --
AB113H-C23G...-E1CC15-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 480 | 3 | 5 | 24 | 17.5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 480 | 3 | 3 | 1-5 | --
AB113H-C23...-E1CC15-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 3.9 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 600 | 3 | 5 | 20 | 18
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 600 | 3 | 3 | 1-5 | --
AB113H-C23...-E1DC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 200 | 3 | 5 | 3.2-16 | -
AB113H-C23G...-E1DC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 200 | 3 | 5 | 3.2-16 | -
AB113H-C23...-E1DC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 230 | 3 | 5 | 3.2-16 | -
AB113H-C23G...-E1DC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 230 | 3 | 5 | 3.2-16 | -
AB113H-C23...-E1DC15-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 600 | 3 | 5 | 20 | 18
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 600 | 3 | 5 | 3.2-16 | -
AB113H-C23...-E1DC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 200 | 3 | 5 | 3.2-16 | -
AB113H-C23G...-E1DC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 200 | 3 | 5 | 3.2-16 | -
AB113H-C23...-E1DC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 230 | 3 | 5 | 3.2-16 | -
AB113H-C23G...-E1DC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 230 | 3 | 5 | 3.2-16 | -
AB113H-C23...-E1DC15-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 600 | 3 | 5 | 20 | 18
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 600 | 3 | 5 | 3.2-16 | -
AB113H-C23...-E1EC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 200 | 3 | 5 | 5.4-27 | -
AB113H-C23G...-E1EC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 200 | 3 | 5 | 5.4-27 | -
AB113H-C23...-E1EC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 230 | 3 | 5 | 5.4-27 | -
AB113H-C23G...-E1EC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 230 | 3 | 5 | 5.4-27 | -
AB113H-C23...-E1EC15-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 600 | 3 | 5 | 20 | 18
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 600 | 3 | 5 | 5.4-27 | -
AB113H-C23...-E1EC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EFEB | 200 | 3 | 5 | 5.4-27 | -
AB113H-C23G...-E1EC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EFEB | 200 | 3 | 5 | 5.4-27 | -
AB113H-C23...-E1EC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFEB | 230 | 3 | 5 | 5.4-27 | -
AB113H-C23G...-E1EC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFEB | 230 | 3 | 5 | 5.4-27 | -
AB113H-C23...-EF1EC15-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C23 | 600 | 3 | 5 | 20 | 18
[10 empty] | OLR | Allen-Bradley | 193-1EFEB | 600 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC15-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC15-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 600 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC30-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC30-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC30-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC30-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 22 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 600 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC50-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC30-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC50-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC50-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 600 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1FC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC15-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC15-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC30-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC30-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC30-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC30-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 22 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC50-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC30-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC50-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC50-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB113H-C30G...-E1EC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC15-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC30-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC30-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC30-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC50-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC30-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC50-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1FC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C30G...-E1FC15-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C30G...-E1FC30-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C30G...-E1FC30-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C30G...-E1FC30-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C30G...-E1FC50-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C30G...-E1FC30-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C30G...-E1FC50-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1EC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC15-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC15-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 600 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC30-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC30-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC30-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC30-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 22 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 600 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC50-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC30-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC50-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1EC50-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 600 | 3 | 5 | 5.4-27 | -
AB113H-C30...-E1FC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC15-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC15-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC30-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC30-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC30-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC30-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 22 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC50-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC30-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC50-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C30...-E1FC50-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB113H-C30G...-E1EC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC15-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC30-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC30-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC30-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC50-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC30-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1EC50-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | -
AB113H-C30G...-E1FC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C30G...-E1FC15-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C30G...-E1FC30-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C30G...-E1FC30-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C30G...-E1FC30-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C30G...-E1FC50-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C30G...-E1FC30-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C30G...-E1FC50-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C37...-E1FC50-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C37...-E1FC50-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C37...-E1FC50-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C37...-E1FC50-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB113H-C37G...-E1FC50-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C37G...-E1FC50-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C37G...-E1FC50-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C37...-E1FC50-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C37...-E1FC50-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C37...-E1FC50-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C37...-E1FC50-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C37 | 600 | 3 | 5 | 32 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB113H-C37G...-E1FC50-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C37 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C37G...-E1FC50-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C37 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C37G...-E1FC50-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C37 | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC50-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC50-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC50-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC50-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB113H-C43G...-E1FC50-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C43G...-E1FC50-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C43G...-E1FC50-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC50-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC50-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC50-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC50-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB113H-C43G...-E1FC50-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C43G...-E1FC50-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C43G...-E1FC50-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC70-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC70-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC70-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC70-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 600 | 3 | -- | 70 | -- | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB113H-C43G...-E1FC70-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C43G...-E1FC70-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 42 FLA | 15 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C43G...-E1FC70-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 40 FLA | 30 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC70-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC70-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC70-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC70-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 600 | 3 | -- | 70 | -- | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB113H-C43G...-E1FC70-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C43G...-E1FC70-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 42 FLA | 15 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C43G...-E1FC70-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 40 FLA | 30 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC80-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 200 | 3 | -- | 80 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC80-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 230 | 3 | -- | 80 | -- | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC80-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 480 | 3 | -- | 80 | -- | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC80-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 600 | 3 | -- | 80 | -- | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB113H-C43G...-E1FC80-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 200 | 3 | -- | 80 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C43G...-E1FC80-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 230 | 3 | -- | 80 | -- | 230 | 3 | 65 | 42 FLA | 15 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C43G...-E1FC80-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 480 | 3 | -- | 80 | -- | 480 | 3 | 65 | 40 FLA | 30 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC80-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 200 | 3 | -- | 80 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC80-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 230 | 3 | -- | 80 | -- | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC80-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 480 | 3 | -- | 80 | -- | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC80-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 600 | 3 | -- | 80 | -- | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 600 | 3 | 5 | 32 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB113H-C43G...-E1FC80-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 200 | 3 | -- | 80 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C43G...-E1FC80-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 230 | 3 | -- | 80 | -- | 230 | 3 | 65 | 42 FLA | 15 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C43G...-E1FC80-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 480 | 3 | -- | 80 | -- | 480 | 3 | 65 | 40 FLA | 30 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC70-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C43...-E1FC70-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C55...-E1FC70-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C55...-E1FC70-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 600 | 3 | -- | 70 | -- | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB113H-C55G...-E1FC70-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C55G...-E1FC70-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 54 FLA | 20 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C55G...-E1FC70-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 52 FLA | 40 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C55...-E1FC70-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C55...-E1FC70-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C55...-E1FC70-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C55...-E1FC70-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 600 | 3 | -- | 70 | -- | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB113H-C55G...-E1FC70-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C55G...-E1FC70-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 54 FLA | 20 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C55G...-E1FC70-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 52 FLA | 40 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C55...-E1FC80-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 200 | 3 | -- | 80 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C55...-E1FC80-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 230 | 3 | -- | 80 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C55...-E1FC80-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 480 | 3 | -- | 80 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C55...-E1FC80-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 600 | 3 | -- | 80 | -- | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB113H-C55G...-E1FC80-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 200 | 3 | -- | 80 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C55G...-E1FC80-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 230 | 3 | -- | 80 | -- | 230 | 3 | 65 | 54 FLA | 20 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C55G...-E1FC80-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 480 | 3 | -- | 80 | -- | 480 | 3 | 65 | 52 FLA | 40 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C55...-E1FC80-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 200 | 3 | -- | 80 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C55...-E1FC80-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 230 | 3 | -- | 80 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C55...-E1FC80-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 480 | 3 | -- | 80 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C55...-E1FC80-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 600 | 3 | -- | 80 | -- | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 600 | 3 | 5 | 41 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB113H-C55G...-E1FC80-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 200 | 3 | -- | 80 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB113H-C55G...-E1FC80-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 230 | 3 | -- | 80 | -- | 230 | 3 | 65 | 54 FLA | 20 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB113H-C55G...-E1FC80-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 480 | 3 | -- | 80 | -- | 480 | 3 | 65 | 52 FLA | 40 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C55 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB113H-C60...-E1FD10-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB113H-C60...-E1FD10-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB113H-C60...-E1FD10-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 480 | 3 | -- | 100 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB113H-C60...-E1FD10-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 600 | 3 | -- | 100 | -- | 600 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 600 | 3 | 10 | 20-100 | --
AB113H-C60...-E1FD12-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB113H-C60...-E1FD12-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB113H-C60...-E1FD12-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB113H-C60...-E1FD12-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | -- | 125 | -- | 600 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 600 | 3 | 10 | 20-100 | --
AB113H-C72...-E1FD10-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB113H-C72...-E1FD10-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 59.4 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB113H-C72...-E1FD10-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 480 | 3 | -- | 100 | -- | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB113H-C72...-E1FD10-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 600 | 3 | -- | 100 | -- | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 600 | 3 | 10 | 20-100 | --
AB113H-C72...-E1FD12-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB113H-C72...-E1FD12-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 59.4 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB113H-C72...-E1FD12-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB113H-C72...-E1FD12-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | -- | 125 | -- | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 600 | 3 | 10 | 20-100 | --
AB113H-C60G...-E1FD10-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB113H-C60G...-E1FD10-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB113H-C60G...-E1FD10-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 480 | 3 | -- | 100 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB113H-C60G...-E1FD12-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB113H-C60G...-E1FD12-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB113H-C60G...-E1FD12-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB113H-C72G...-E1FD10-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB113H-C72G...-E1FD10-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 59.4 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB113H-C72G...-E1FD10-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 480 | 3 | -- | 100 | -- | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB113H-C72G...-E1FD12-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB113H-C72G...-E1FD12-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 59.4 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB113H-C72G...-E1FD12-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB113H-C60...-E1FD10-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB113H-C60...-E1FD10-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB113H-C60...-E1FD10-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 480 | 3 | -- | 100 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB113H-C60...-E1FD10-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 600 | 3 | -- | 100 | -- | 600 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 600 | 3 | 10 | 20-100 | --
AB113H-C60...-E1FD12-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB113H-C60...-E1FD12-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB113H-C60...-E1FD12-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB113H-C60...-E1FD12-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | -- | 125 | -- | 600 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 600 | 3 | 10 | 20-100 | --
AB113H-C72...-E1FD10-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB113H-C72...-E1FD10-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 59.4 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB113H-C72...-E1FD10-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 480 | 3 | -- | 100 | -- | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB113H-C72...-E1FD10-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 600 | 3 | -- | 100 | -- | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 600 | 3 | 10 | 20-100 | --
AB113H-C72...-E1FD12-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB113H-C72...-E1FD12-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 59.4 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB113H-C72...-E1FD12-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB113H-C72...-E1FD12-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | -- | 125 | -- | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 600 | 3 | 10 | 62 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 600 | 3 | 10 | 20-100 | --
AB113H-C60G...-E1FD10-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB113H-C60G...-E1FD10-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB113H-C60G...-E1FD10-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 480 | 3 | -- | 100 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB113H-C60G...-E1FD12-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB113H-C60G...-E1FD12-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB113H-C60G...-E1FD12-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C60 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB113H-C72G...-E1FD10-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB113H-C72G...-E1FD10-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 59.4 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB113H-C72G...-E1FD10-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 480 | 3 | -- | 100 | -- | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB113H-C72G...-E1FD12-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 200 | 3 | 10 | 62.1 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB113H-C72G...-E1FD12-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 59.4 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 230 | 3 | 10 | 68 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB113H-C72G...-E1FD12-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C72 | 480 | 3 | 10 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB113H-C85...-E1FD12-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB113H-C85...-E1FD12-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB113H-C85...-E1FD12-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB113H-C85...-E1FD12-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | -- | 125 | -- | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 600 | 3 | 10 | 20-100 | --
AB113H-C97...-E1FD12-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB113H-C97...-E1FD12-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB113H-C97...-E1FD12-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB113H-C97...-E1FD12-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | -- | 125 | -- | 600 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 600 | 3 | 10 | 20-100 | --
AB113H-C85G...-E1FD12-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB113H-C85G...-E1FD12-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB113H-C85G...-E1FD12-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB113H-C97G...-E1FD12-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB113H-C97G...-E1FD12-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB113H-C97G...-E1FD12-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB113H-C85...-E1FD12-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB113H-C85...-E1FD12-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB113H-C85...-E1FD12-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB113H-C85...-E1FD12-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | -- | 125 | -- | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C85 | 600 | 3 | 10 | 62 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 600 | 3 | 10 | 20-100 | --
AB113H-C97...-E1FD12-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB113H-C97...-E1FD12-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB113H-C97...-E1FD12-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB113H-C97...-E1FD12-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | -- | 125 | -- | 600 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C97 | 600 | 3 | 10 | 77 | 75
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 600 | 3 | 10 | 20-100 | --
AB113H-C85G...-E1FD12-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C85 | 200 | 3 | 10 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB113H-C85G...-E1FD12-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C85 | 230 | 3 | 10 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB113H-C85G...-E1FD12-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C85 | 480 | 3 | 10 | 77 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB113H-C97G...-E1FD12-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C97 | 200 | 3 | 10 | 92 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB113H-C97G...-E1FD12-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C97 | 230 | 3 | 10 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB113H-C97G...-E1FD12-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 100-C97 | 480 | 3 | 10 | 96 | 75
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & OLR shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the OLR heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type C & D Combination Motor Controllers).
(6) = The enclosure shall have the minimum of 2 hinges and 2 latches.
(7) = Specific conductor size required for internal wiring between components as tabulated below:
[10 empty] | Cat. No. | AWG No.
[10 empty] | 113H-C16, C23, C30 | 10
[10 empty] | 113H-C37 | 8
[10 empty] | 113H-C43 | 8
[10 empty] | 113H–C55 | 6
[10 empty] | 113H-C60 | 6
[10 empty] | 113H-C72 | 4
[10 empty] | 113H-C85 | 4
[10 empty] | 113H-C97 | 3

## MCP 107H Series C E100
[23 empty] | Issued: | 2021-04-30
[23 empty] | Revised: | 2021-06-18
Database Identification Number | [B2] Listed Combination Motor Controller Information | [7 empty] | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability
| Listing Report Information |  |  |  |  | Enclosure or Unit Dimensions
| UL File Number | Report Issue Date YYYY-MM-DD | Volume / Section (Vol#).(Sec#) | Model Number or Product Style/ Designation | Product Description on Page/Figure/Ill. | Enclosure or Unit Height, inches | Width, inches | Depth, inches |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number [1] AND [8] | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP rating | Enclosure Volume, CU inches
AB107H-C16...-E1CC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 200 | 3 | 5 | 1-5 | --
AB107H-C16G...-E1CC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 200 | 3 | 3 | 1-5 | --
AB107H-C16...-E1CC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 230 | 3 | 3 | 1-5 | --
AB107H-C16G...-E1CC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 230 | 3 | 3 | 1-5 | --
AB107H-C16...-E1CC15-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 480 | 3 | 3 | 1-5 | --
AB107H-C16G...-E1CC15-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 480 | 3 | 3 | 1-5 | --
AB107H-C16...-E1CC15-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 3.9 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 600 | 3 | 5 | 17 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 600 | 3 | 3 | 1-5 | --
AB107H-C16...-E1CC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 200 | 3 | 3 | 1-5 | --
AB107H-C16G...-E1CC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 200 | 3 | 3 | 1-5 | --
AB107H-C16...-E1CC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 230 | 3 | 3 | 1-5 | --
AB107H-C16G...-E1CC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 230 | 3 | 3 | 1-5 | --
AB107H-C16...-E1CC15-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 480 | 3 | 3 | 1-5 | --
AB107H-C16G...-E1CC15-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 480 | 3 | 5 | 14 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 480 | 3 | 3 | 1-5 | --
AB107H-C16...-E1CC15-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 3.9 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 600 | 3 | 5 | 17 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 600 | 3 | 3 | 1-5 | --
AB107H-C16...-E1DC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 200 | 3 | 5 | 3.2-16 | -
AB107H-C16G...-E1DC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 200 | 3 | 5 | 3.2-16 | -
AB107H-C16...-E1DC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 230 | 3 | 5 | 3.2-16 | -
AB107H-C16G...-E1DC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 230 | 3 | 5 | 3.2-16 | -
AB107H-C16...-E1DC15-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 600 | 3 | 5 | 17 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 600 | 3 | 5 | 3.2-16 | -
AB107H-C16...-E1DC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 200 | 3 | 5 | 3.2-16 | -
AB107H-C16G...-E1DC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 200 | 3 | 5 | 3.2-16 | -
AB107H-C16...-E1DC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 230 | 3 | 5 | 3.2-16 | -
AB107H-C16G...-E1DC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 230 | 3 | 5 | 3.2-16 | -
AB107H-C16...-E1DC15-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 600 | 3 | 5 | 17 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 600 | 3 | 5 | 3.2-16 | -
AB107H-C16...-E1EC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 200 | 3 | 5 | 5.4-27 | -
AB107H-C16G...-E1EC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 200 | 3 | 5 | 5.4-27 | -
AB107H-C16...-E1EC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 230 | 3 | 5 | 5.4-27 | -
AB107H-C16G...-E1EC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 230 | 3 | 5 | 5.4-27 | -
AB107H-C16...-E1EC15-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 600 | 3 | 5 | 17 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 600 | 3 | 5 | 5.4-27 | -
AB107H-C16...-E1EC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 200 | 3 | 5 | 3.2-16 | -
AB107H-C16G...-E1EC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 200 | 3 | 5 | 17.5 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 200 | 3 | 5 | 3.2-16 | -
AB107H-C16...-E1EC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 230 | 3 | 5 | 3.2-16 | -
AB107H-C16G...-E1EC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 230 | 3 | 5 | 15.2 | 5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 230 | 3 | 5 | 3.2-16 | -
AB107H-C16...-EF1EC15-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C16 | 600 | 3 | 5 | 17 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 600 | 3 | 5 | 3.2-16 | -
AB107H-C23...-E1CC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 200 | 3 | 3 | 1-5 | --
AB107H-C23G...-E1CC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 200 | 3 | 3 | 1-5 | --
AB107H-C23...-E1CC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 230 | 3 | 3 | 1-5 | --
AB107H-C23G...-E1CC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 230 | 3 | 3 | 1-5 | --
AB107H-C23...-E1CC15-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 480 | 3 | 5 | 24 | 17.5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 480 | 3 | 3 | 1-5 | --
AB107H-C23G...-E1CC15-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 480 | 3 | 5 | 24 | 17.5
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 480 | 3 | 3 | 1-5 | --
AB107H-C23...-E1CC15-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 3.9 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 600 | 3 | 5 | 20 | 18
[10 empty] | OLR | Allen-Bradley | 193-1EECB | 600 | 3 | 3 | 1-5 | --
AB107H-C23...-E1CC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 200 | 3 | 3 | 1-5 | --
AB107H-C23G...-E1CC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 4.8 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 200 | 3 | 3 | 1-5 | --
AB107H-C23...-E1CC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 230 | 3 | 3 | 1-5 | --
AB107H-C23G...-E1CC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 4.2 FLA | 1 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 230 | 3 | 3 | 1-5 | --
AB107H-C23...-E1CC15-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 480 | 3 | 5 | 24 | 17.5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 480 | 3 | 3 | 1-5 | --
AB107H-C23G...-E1CC15-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 4.8 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 480 | 3 | 5 | 24 | 17.5
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 480 | 3 | 3 | 1-5 | --
AB107H-C23...-E1CC15-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 3.9 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 600 | 3 | 5 | 20 | 18
[10 empty] | OLR | Allen-Bradley | 193-1EFCB | 600 | 3 | 3 | 1-5 | --
AB107H-C23...-E1DC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 200 | 3 | 5 | 3.2-16 | -
AB107H-C23G...-E1DC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 200 | 3 | 5 | 3.2-16 | -
AB107H-C23...-E1DC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 230 | 3 | 5 | 3.2-16 | -
AB107H-C23G...-E1DC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 230 | 3 | 5 | 3.2-16 | -
AB107H-C23...-E1DC15-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 600 | 3 | 5 | 20 | 18
[10 empty] | OLR | Allen-Bradley | 193-1EEDB | 600 | 3 | 5 | 3.2-16 | -
AB107H-C23...-E1DC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 200 | 3 | 5 | 3.2-16 | -
AB107H-C23G...-E1DC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 200 | 3 | 5 | 3.2-16 | -
AB107H-C23...-E1DC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 230 | 3 | 5 | 3.2-16 | -
AB107H-C23G...-E1DC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 230 | 3 | 5 | 3.2-16 | -
AB107H-C23...-E1DC15-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 600 | 3 | 5 | 20 | 18
[10 empty] | OLR | Allen-Bradley | 193-1EFDB | 600 | 3 | 5 | 3.2-16 | -
AB107H-C23...-E1EC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 200 | 3 | 5 | 5.4-27 | -
AB107H-C23G...-E1EC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 200 | 3 | 5 | 5.4-27 | -
AB107H-C23...-E1EC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 230 | 3 | 5 | 5.4-27 | -
AB107H-C23G...-E1EC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 230 | 3 | 5 | 5.4-27 | -
AB107H-C23...-E1EC15-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 600 | 3 | 5 | 20 | 18
[10 empty] | OLR | Allen-Bradley | 193-1EEEB | 600 | 3 | 5 | 5.4-27 | -
AB107H-C23...-E1EC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EFEB | 200 | 3 | 5 | 5.4-27 | -
AB107H-C23G...-E1EC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11.0 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 200 | 3 | 5 | 24 | 7
[10 empty] | OLR | Allen-Bradley | 193-1EFEB | 200 | 3 | 5 | 5.4-27 | -
AB107H-C23...-E1EC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFEB | 230 | 3 | 5 | 5.4-27 | -
AB107H-C23G...-E1EC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 230 | 3 | 5 | 22 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFEB | 230 | 3 | 5 | 5.4-27 | -
AB107H-C23...-EF1EC15-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C23 | 600 | 3 | 5 | 20 | 18
[10 empty] | OLR | Allen-Bradley | 193-1EFEB | 600 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC15-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC15-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 600 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC30-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC30-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC30-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC30-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 22 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 600 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC50-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC30-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC50-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC50-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 600 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1FC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC15-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC15-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC30-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC30-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC30-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC30-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 22 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC50-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC30-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC50-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC50-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB107H-C30G...-E1EC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | -
AB107H-C30G...-E1EC15-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | -
AB107H-C30G...-E1EC15-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | -
AB107H-C30G...-E1EC30-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | -
AB107H-C30G...-E1EC30-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | -
AB107H-C30G...-E1EC30-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | -
AB107H-C30G...-E1EC50-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 200 | 3 | 5 | 5.4-27 | -
AB107H-C30G...-E1EC30-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 230 | 3 | 5 | 5.4-27 | -
AB107H-C30G...-E1EC50-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEED | 480 | 3 | 5 | 5.4-27 | -
AB107H-C30G...-E1FC15-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C30G...-E1FC15-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C30G...-E1FC30-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C30G...-E1FC30-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C30G...-E1FC30-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C30G...-E1FC50-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C30G...-E1FC30-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C30G...-E1FC50-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1EC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC15-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC15-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 600 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC30-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC30-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC30-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC30-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 22 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 600 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC50-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC30-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC50-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1EC50-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 600 | 3 | 5 | 5.4-27 | -
AB107H-C30...-E1FC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC15-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC15-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C15 | 600 | 3 | -- | 15 | -- | 600 | 3 | 25 | 11 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC30-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC30-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC30-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC30-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C30 | 600 | 3 | -- | 30 | -- | 600 | 3 | 25 | 22 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC50-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC30-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC50-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C30...-E1FC50-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 27 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 600 | 3 | 5 | 27 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB107H-C30G...-E1EC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | -
AB107H-C30G...-E1EC15-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 230 | 3 | -- | 15 | -- | 230 | 3 | 65 | 9.6 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | -
AB107H-C30G...-E1EC15-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | -
AB107H-C30G...-E1EC30-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | -
AB107H-C30G...-E1EC30-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | -
AB107H-C30G...-E1EC30-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | -
AB107H-C30G...-E1EC50-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 200 | 3 | 5 | 5.4-27 | -
AB107H-C30G...-E1EC30-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 230 | 3 | 5 | 5.4-27 | -
AB107H-C30G...-E1EC50-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFED | 480 | 3 | 5 | 5.4-27 | -
AB107H-C30G...-E1FC15-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 200 | 3 | -- | 15 | -- | 200 | 3 | 65 | 11 FLA | 3 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C30G...-E1FC15-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C15 | 480 | 3 | -- | 15 | -- | 480 | 3 | 65 | 11 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C30G...-E1FC30-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 200 | 3 | -- | 30 | -- | 200 | 3 | 65 | 17.5 FLA | 5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C30G...-E1FC30-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 230 | 3 | -- | 30 | -- | 230 | 3 | 65 | 22 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C30G...-E1FC30-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C30 | 480 | 3 | -- | 30 | -- | 480 | 3 | 65 | 21 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C30G...-E1FC50-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 25.3 FLA | 7.5 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 200 | 3 | 5 | 25.3 | 7.5
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C30G...-E1FC30-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C30G...-E1FC50-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 27 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C30 | 480 | 3 | 5 | 27 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C37...-E1FC50-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C37 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C37...-E1FC50-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C37 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C37...-E1FC50-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C37 | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C37...-E1FC50-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C37 | 600 | 3 | 5 | 32 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB107H-C37G...-E1FC50-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C37 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C37G...-E1FC50-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C37 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C37G...-E1FC50-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C37 | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C37...-E1FC50-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C37 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C37...-E1FC50-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C37 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C37...-E1FC50-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C37 | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C37...-E1FC50-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C37 | 600 | 3 | 5 | 32 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB107H-C37G...-E1FC50-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C37 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C37G...-E1FC50-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C37 | 230 | 3 | 5 | 28 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C37G...-E1FC50-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 34 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C37 | 480 | 3 | 5 | 34 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC50-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC50-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC50-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC50-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 600 | 3 | 5 | 32 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB107H-C43G...-E1FC50-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C43G...-E1FC50-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C43G...-E1FC50-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC50-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC50-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC50-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC50-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C50 | 600 | 3 | -- | 50 | -- | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 600 | 3 | 5 | 32 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB107H-C43G...-E1FC50-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 200 | 3 | -- | 50 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C43G...-E1FC50-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 230 | 3 | -- | 50 | -- | 230 | 3 | 65 | 28 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C43G...-E1FC50-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-C50 | 480 | 3 | -- | 50 | -- | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC70-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC70-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC70-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC70-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 600 | 3 | -- | 70 | -- | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 600 | 3 | 5 | 32 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB107H-C43G...-E1FC70-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C43G...-E1FC70-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 42 FLA | 15 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C43G...-E1FC70-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 40 FLA | 30 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC70-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC70-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC70-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC70-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 600 | 3 | -- | 70 | -- | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 600 | 3 | 5 | 32 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB107H-C43G...-E1FC70-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C43G...-E1FC70-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 42 FLA | 15 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C43G...-E1FC70-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 40 FLA | 30 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC80-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 200 | 3 | -- | 80 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC80-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 230 | 3 | -- | 80 | -- | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC80-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 480 | 3 | -- | 80 | -- | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC80-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 600 | 3 | -- | 80 | -- | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 600 | 3 | 5 | 32 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB107H-C43G...-E1FC80-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 200 | 3 | -- | 80 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C43G...-E1FC80-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 230 | 3 | -- | 80 | -- | 230 | 3 | 65 | 42 FLA | 15 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C43G...-E1FC80-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 480 | 3 | -- | 80 | -- | 480 | 3 | 65 | 40 FLA | 30 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC80-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 200 | 3 | -- | 80 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC80-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 230 | 3 | -- | 80 | -- | 230 | 3 | 65 | 42 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC80-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 480 | 3 | -- | 80 | -- | 480 | 3 | 65 | 40 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC80-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 600 | 3 | -- | 80 | -- | 600 | 3 | 25 | 32 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 600 | 3 | 5 | 32 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB107H-C43G...-E1FC80-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 200 | 3 | -- | 80 | -- | 200 | 3 | 65 | 32.2 FLA | 10 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 200 | 3 | 5 | 32.2 | 10
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C43G...-E1FC80-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 230 | 3 | -- | 80 | -- | 230 | 3 | 65 | 42 FLA | 15 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 230 | 3 | 5 | 42 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C43G...-E1FC80-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 480 | 3 | -- | 80 | -- | 480 | 3 | 65 | 40 FLA | 30 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C43 | 480 | 3 | 5 | 40 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC70-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C43...-E1FC70-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C55...-E1FC70-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C55...-E1FC70-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 600 | 3 | -- | 70 | -- | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 600 | 3 | 5 | 41 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB107H-C55G...-E1FC70-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C55G...-E1FC70-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 54 FLA | 20 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C55G...-E1FC70-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 52 FLA | 40 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C55...-E1FC70-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C55...-E1FC70-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C55...-E1FC70-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C55...-E1FC70-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C70 | 600 | 3 | -- | 70 | -- | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 600 | 3 | 5 | 41 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB107H-C55G...-E1FC70-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 200 | 3 | -- | 70 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C55G...-E1FC70-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 230 | 3 | -- | 70 | -- | 230 | 3 | 65 | 54 FLA | 20 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C55G...-E1FC70-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C70 | 480 | 3 | -- | 70 | -- | 480 | 3 | 65 | 52 FLA | 40 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C55...-E1FC80-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 200 | 3 | -- | 80 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C55...-E1FC80-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 230 | 3 | -- | 80 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C55...-E1FC80-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 480 | 3 | -- | 80 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C55...-E1FC80-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 600 | 3 | -- | 80 | -- | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 600 | 3 | 5 | 41 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 600 | 3 | 5 | 11 - 55 | --
AB107H-C55G...-E1FC80-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 200 | 3 | -- | 80 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C55G...-E1FC80-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 230 | 3 | -- | 80 | -- | 230 | 3 | 65 | 54 FLA | 20 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C55G...-E1FC80-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 480 | 3 | -- | 80 | -- | 480 | 3 | 65 | 52 FLA | 40 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C55...-E1FC80-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 200 | 3 | -- | 80 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C55...-E1FC80-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 230 | 3 | -- | 80 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C55...-E1FC80-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 480 | 3 | -- | 80 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C55...-E1FC80-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-C80 | 600 | 3 | -- | 80 | -- | 600 | 3 | 25 | 41 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 600 | 3 | 5 | 41 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 600 | 3 | 5 | 11 - 55 | --
AB107H-C55G...-E1FC80-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 200 | 3 | -- | 80 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 200 | 3 | 5 | 11 - 55 | --
AB107H-C55G...-E1FC80-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 230 | 3 | -- | 80 | -- | 230 | 3 | 65 | 54 FLA | 20 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 230 | 3 | 5 | 11 - 55 | --
AB107H-C55G...-E1FC80-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 36 | 30 | 10 | D | ICB | Allen-Bradley | 140MG-G8P-C80 | 480 | 3 | -- | 80 | -- | 480 | 3 | 65 | 52 FLA | 40 | 10800 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C55 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFFD | 480 | 3 | 5 | 11 - 55 | --
AB107H-C60...-E1FD10-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB107H-C60...-E1FD10-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB107H-C60...-E1FD10-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 480 | 3 | -- | 100 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB107H-C60...-E1FD10-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 600 | 3 | -- | 100 | -- | 600 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 600 | 3 | 10 | 20-100 | --
AB107H-C60...-E1FD12-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB107H-C60...-E1FD12-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB107H-C60...-E1FD12-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB107H-C60...-E1FD12-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | -- | 125 | -- | 600 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 600 | 3 | 10 | 20-100 | --
AB107H-C72...-E1FD10-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 200 | 3 | 10 | 62.1 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB107H-C72...-E1FD10-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 59.4 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 230 | 3 | 10 | 68 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB107H-C72...-E1FD10-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 480 | 3 | -- | 100 | -- | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 480 | 3 | 10 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB107H-C72...-E1FD10-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 600 | 3 | -- | 100 | -- | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 600 | 3 | 10 | 62 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 600 | 3 | 10 | 20-100 | --
AB107H-C72...-E1FD12-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 200 | 3 | 10 | 62.1 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB107H-C72...-E1FD12-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 59.4 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 230 | 3 | 10 | 68 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB107H-C72...-E1FD12-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 480 | 3 | 10 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB107H-C72...-E1FD12-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | -- | 125 | -- | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 600 | 3 | 10 | 62 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 600 | 3 | 10 | 20-100 | --
AB107H-C60G...-E1FD10-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB107H-C60G...-E1FD10-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB107H-C60G...-E1FD10-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 480 | 3 | -- | 100 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB107H-C60G...-E1FD12-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB107H-C60G...-E1FD12-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB107H-C60G...-E1FD12-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB107H-C72G...-E1FD10-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 200 | 3 | 10 | 62.1 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB107H-C72G...-E1FD10-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 59.4 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 230 | 3 | 10 | 68 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB107H-C72G...-E1FD10-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 480 | 3 | -- | 100 | -- | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 480 | 3 | 10 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB107H-C72G...-E1FD12-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 200 | 3 | 10 | 62.1 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB107H-C72G...-E1FD12-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 59.4 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 230 | 3 | 10 | 68 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB107H-C72G...-E1FD12-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 480 | 3 | 10 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB107H-C60...-E1FD10-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB107H-C60...-E1FD10-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB107H-C60...-E1FD10-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 480 | 3 | -- | 100 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB107H-C60...-E1FD10-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 600 | 3 | -- | 100 | -- | 600 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 600 | 3 | 10 | 20-100 | --
AB107H-C60...-E1FD12-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB107H-C60...-E1FD12-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB107H-C60...-E1FD12-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB107H-C60...-E1FD12-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | -- | 125 | -- | 600 | 3 | 25 | 52 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 600 | 3 | 5 | 52 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 600 | 3 | 10 | 20-100 | --
AB107H-C72...-E1FD10-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 200 | 3 | 10 | 62.1 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB107H-C72...-E1FD10-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 59.4 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 230 | 3 | 10 | 68 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB107H-C72...-E1FD10-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 480 | 3 | -- | 100 | -- | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 480 | 3 | 10 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB107H-C72...-E1FD10-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D10 | 600 | 3 | -- | 100 | -- | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 600 | 3 | 10 | 62 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 600 | 3 | 10 | 20-100 | --
AB107H-C72...-E1FD12-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 200 | 3 | 10 | 62.1 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB107H-C72...-E1FD12-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 59.4 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 230 | 3 | 10 | 68 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB107H-C72...-E1FD12-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 480 | 3 | 10 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB107H-C72...-E1FD12-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | -- | 125 | -- | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 600 | 3 | 10 | 62 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 600 | 3 | 10 | 20-100 | --
AB107H-C60G...-E1FD10-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB107H-C60G...-E1FD10-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB107H-C60G...-E1FD10-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 480 | 3 | -- | 100 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB107H-C60G...-E1FD12-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 48.3 FLA | 15 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 200 | 3 | 5 | 48.3 | 15
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB107H-C60G...-E1FD12-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 54 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 230 | 3 | 5 | 54 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB107H-C60G...-E1FD12-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 52 FLA | 40 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C60 | 480 | 3 | 5 | 52 | 40
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB107H-C72G...-E1FD10-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 200 | 3 | -- | 100 | -- | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 200 | 3 | 10 | 62.1 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB107H-C72G...-E1FD10-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 230 | 3 | -- | 100 | -- | 230 | 3 | 65 | 59.4 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 230 | 3 | 10 | 68 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB107H-C72G...-E1FD10-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D10 | 480 | 3 | -- | 100 | -- | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 480 | 3 | 10 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB107H-C72G...-E1FD12-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 62.1 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 200 | 3 | 10 | 62.1 | 20
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB107H-C72G...-E1FD12-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 59.4 FLA | 20 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 230 | 3 | 10 | 68 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB107H-C72G...-E1FD12-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 65 FLA | 50 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C72 | 480 | 3 | 10 | 65 | 50
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB107H-C85...-E1FD12-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C85 | 200 | 3 | 10 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB107H-C85...-E1FD12-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C85 | 230 | 3 | 10 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB107H-C85...-E1FD12-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C85 | 480 | 3 | 10 | 77 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB107H-C85...-E1FD12-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | -- | 125 | -- | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C85 | 600 | 3 | 10 | 62 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 600 | 3 | 10 | 20-100 | --
AB107H-C97...-E1FD12-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C97 | 200 | 3 | 10 | 92 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB107H-C97...-E1FD12-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C97 | 230 | 3 | 10 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB107H-C97...-E1FD12-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C97 | 480 | 3 | 10 | 96 | 75
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB107H-C97...-E1FD12-..575V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | -- | 125 | -- | 600 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C97 | 600 | 3 | 10 | 77 | 75
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 600 | 3 | 10 | 20-100 | --
AB107H-C85G...-E1FD12-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C85 | 200 | 3 | 10 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB107H-C85G...-E1FD12-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C85 | 230 | 3 | 10 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB107H-C85G...-E1FD12-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C85 | 480 | 3 | 10 | 77 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB107H-C97G...-E1FD12-..200V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C97 | 200 | 3 | 10 | 92 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 200 | 3 | 10 | 20-100 | --
AB107H-C97G...-E1FD12-..230V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C97 | 230 | 3 | 10 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 230 | 3 | 10 | 20-100 | --
AB107H-C97G...-E1FD12-..460V.01 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C97 | 480 | 3 | 10 | 96 | 75
[10 empty] | OLR | Allen-Bradley | 193-1EEGE | 480 | 3 | 10 | 20-100 | --
AB107H-C85...-E1FD12-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C85 | 200 | 3 | 10 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB107H-C85...-E1FD12-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C85 | 230 | 3 | 10 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB107H-C85...-E1FD12-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C85 | 480 | 3 | 10 | 77 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB107H-C85...-E1FD12-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | -- | 125 | -- | 600 | 3 | 25 | 62 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C85 | 600 | 3 | 10 | 62 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 600 | 3 | 10 | 20-100 | --
AB107H-C97...-E1FD12-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C97 | 200 | 3 | 10 | 92 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB107H-C97...-E1FD12-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C97 | 230 | 3 | 10 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB107H-C97...-E1FD12-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C97 | 480 | 3 | 10 | 96 | 75
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB107H-C97...-E1FD12-..575V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-H8P-D12 | 600 | 3 | -- | 125 | -- | 600 | 3 | 25 | 77 FLA | 75 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C97 | 600 | 3 | 10 | 77 | 75
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 600 | 3 | 10 | 20-100 | --
AB107H-C85G...-E1FD12-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 78.2 FLA | 25 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C85 | 200 | 3 | 10 | 78.2 | 25
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB107H-C85G...-E1FD12-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C85 | 230 | 3 | 10 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB107H-C85G...-E1FD12-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 77 FLA | 60 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C85 | 480 | 3 | 10 | 77 | 60
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
AB107H-C97G...-E1FD12-..200V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 200 | 3 | -- | 125 | -- | 200 | 3 | 65 | 92 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C97 | 200 | 3 | 10 | 92 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 200 | 3 | 10 | 20-100 | --
AB107H-C97G...-E1FD12-..230V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 230 | 3 | -- | 125 | -- | 230 | 3 | 65 | 80 FLA | 30 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C97 | 230 | 3 | 10 | 80 | 30
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 230 | 3 | 10 | 20-100 | --
AB107H-C97G...-E1FD12-..460V.02 | E125316 | 2009-08-13 | Vol. 1/Sec. 7 |  |  | 24 | 20 | 8 | D | ICB | Allen-Bradley | 140MG-G8P-D12 | 480 | 3 | -- | 125 | -- | 480 | 3 | 65 | 96 FLA | 75 | 3840 | 1,5,6,7
[10 empty] | MC | Allen-Bradley | 104-C97 | 480 | 3 | 10 | 96 | 75
[10 empty] | OLR | Allen-Bradley | 193-1EFGE | 480 | 3 | 10 | 20-100 | --
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & OLR shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the OLR heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type C & D Combination Motor Controllers).
(6) = The enclosure shall have a minimum of 2 hinges and 2 latches.
(7) = Specific conductor size required for internal wiring between components as tabulated below:
[10 empty] | Contactor Cat. No. | AWG No.
[10 empty] | 104-C16, C23, C30 | 10
[10 empty] | 104-C37 | 8
[10 empty] | 104-C43 | 8
[10 empty] | 104–C55 | 6
[10 empty] | 104-C60 | 6
[10 empty] | 104-C72 | 4
[10 empty] | 104-C85 | 4
[10 empty] | 104-C97 | 3