## Fusible-Contactor&O.L.Relay
Certification of combinations of components in combination motor controllers for use in industrial control panels | [17 empty] | Last Revised: 2006-04-25
NOTE A: For Combinations using current transformers, the current transformer must be provided as specified on the installation instructions for the overload relay.
NOTE B: Where a fuseholder is specified, or where none is specified, as an alternative, any Listed Fuseholder may be used. The short-circuit current rating of the Combination will be restricted by the short-circuit current rating of the Fuseholder.
ID Number | Combination Type | Individual Component | [7 empty] | Combination SCCR | [6 empty] | Combination UL File | Enclosure Vol. (cu in)
|  | Type | Manufacturer | Catalog Designation | Ratings |  |  |  |  | kA | Volts | Ph | Maximum HP | Maximum NEC FLC | Minimum Enclosure Volume (cu ft) | Conditions of Acceptability
[5 empty] | kA | Overload Relay Current Rating | Maximum Fuse Current Rating | Volts | Poles
SE&A FCT2006001 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1.38 | 1(1.38), 3(For 48DC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK203 - Class J: FCJK603 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 200 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 3 | 200 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 200 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 30 | 200 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 30 | 200 | 3
SE&A FCT2006002 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 1.5 | 6.9 | 1.38 | 1(1.38), 3(For 48DC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK203 - Class J: FCJK603 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 3 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 30 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 30 | 240 | 3
SE&A FCT2006003 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 1.5 | 6.9 | 1.38 | 1(1.38), 3(For 48DC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK603 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 480 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 3 | 480 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 480 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 30 | 480 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 30 | 480 | 3
SE&A FCT2006004 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 1.5 | 6.9 | 1.38 | 1(1.38), 3(For 48DC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK603 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 600 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 3 | 600 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 600 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 30 | 600 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 30 | 600 | 3
SE&A FCT2006005 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1.38 | 1(1.38), 3(For 48DC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK203 - Class J: FCJK603 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 200 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 3 | 200 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 200 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 30 | 200 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 30 | 200 | 3
SE&A FCT2006006 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1.38 | 1(1.38), 3(For 48DC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK203 - Class J: FCJK603 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 3 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 30 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 30 | 240 | 3
SE&A FCT2006007 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1.38 | 1(1.38), 3(For 48DC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK603 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 480 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 3 | 480 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 480 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 30 | 480 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 30 | 480 | 3
SE&A FCT2006008 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 5 | 6.1 | 1.38 | 1(1.38), 3(For 48DC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK603 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 600 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 3 | 600 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 600 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 30 | 600 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 30 | 600 | 3
SE&A FCT2006009 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1.38 | 1(1.38), 3(For 48DC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK606 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 200 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 3 | 200 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 200 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 60 | 200 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 60 | 200 | 3
SE&A FCT2006010 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1.38 | 1(1.38), 3(For 48DC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK606 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 3 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 60 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 60 | 240 | 3
SE&A FCT2006011 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1.38 | 1(1.38), 3(For 48DC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK606 - Class J: FCJK606 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 480 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 3 | 480 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 480 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 60 | 480 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 60 | 480 | 3
SE&A FCT2006012 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1.38 | 1(1.38), 3(For 48DC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK606 - Class J: FCJK606 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 600 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 3 | 600 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 600 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 60 | 600 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 60 | 600 | 3
SE&A FCT2006013 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38), 3(For 48EC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK606 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 30 | 200 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 200 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 60 | 200 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 60 | 200 | 3
SE&A FCT2006014 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1.38 | 1(1.38), 3(For 48EC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK606 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 30 | 240 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 240 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 60 | 240 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 60 | 240 | 3
SE&A FCT2006015 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1.38 | 1(1.38), 3(For 48EC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK606 - Class J: FCJK606 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 30 | 480 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 480 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 60 | 480 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 60 | 480 | 3
SE&A FCT2006016 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1.38 | 1(1.38), 3(For 48EC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK606 - Class J: FCJK606 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 30 | 600 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 600 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 60 | 600 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 60 | 600 | 3
SE&A FCT2006017 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38), 3(For 48GC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 30 | 200 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 200 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 60 | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 100 | 200 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 200 | 3
SE&A FCT2006018 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1.38 | 1(1.38), 3(For 48GC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 30 | 240 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 240 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 60 | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 100 | 240 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 240 | 3
SE&A FCT2006019 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1.38 | 1(1.38), 3(For 48GC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 30 | 480 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 480 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 60 | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 100 | 480 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 480 | 3
SE&A FCT2006020 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 1.38 | 1(1.38), 3(For 48GC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 30 | 600 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 600 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 60 | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 100 | 600 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 600 | 3
SE&A FCT2006021 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2.78 | 1(2.78), 3(For 48GC3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 200 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 40 | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 60 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 200 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 200 | 3
SE&A FCT2006022 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2.78 | 1(2.78), 3(For 48GC3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 240 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 40 | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 60 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 240 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 240 | 3
SE&A FCT2006023 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2.78 | 1(2.78), 3(For 48GC3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 480 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 40 | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 60 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 480 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 480 | 3
SE&A FCT2006024 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 2.78 | 1(2.78), 3(For 48GC3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 600 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 40 | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 60 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 600 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 600 | 3
SE&A FCT2006025 | A | DS | Siemens | MCS 610 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 3.47 | 1(3.47), 3(For 48HA3) | E43399 Vol. 1 Sec. 6 | 5996.16
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40HP32A | 5 | 100 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 60 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 100 | 200 | 3
SE&A FCT2006026 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3.47 | 1(3.47), 3(For 48HA3) | E43399 Vol. 1 Sec. 6 | 5996.16
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40HP32A | 5 | 100 | - | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 60 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 240 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 100 | 200 | 3
SE&A FCT2006027 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3.47 | 1(3.47), 3(For 48HA3) | E43399 Vol. 1 Sec. 6 | 5996.16
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40HP32A | 5 | 100 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 60 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 100 | 480 | 3
SE&A FCT2006028 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 3.47 | 1(3.47), 3(For 48HA3) | E43399 Vol. 1 Sec. 6 | 5996.16
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40HP32A | 5 | 100 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 60 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 100 | 600 | 3
SE&A FCT2006029 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 4.86 | 1(4.86), 3(For 48HA3) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40IP32A | 5 | 125 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 60 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 200 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 150 | 200 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 200 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 200 | 200 | 3
SE&A FCT2006030 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4.86 | 1(4.86), 3(For 48HA3) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40IP32A | 5 | 125 | - | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 60 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 240 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 150 | 240 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 200 | 240 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 200 | 240 | 3
SE&A FCT2006031 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4.86 | 1(4.86), 3(For 48HA3) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40IP32A | 5 | 125 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 60 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 480 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 150 | 480 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 200 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 200 | 480 | 3
SE&A FCT2006032 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4.86 | 1(4.86), 3(For 48HA3) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40IP32A | 5 | 125 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 60 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 600 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 150 | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 200 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 200 | 600 | 3
SE&A FCT2006033 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 4.86 | 1(4.86), 3(For 48JA3) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40JG32A | 5 | 135 | - | 200 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 200 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 30 - 60 | 200 | 200 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 200 | 200 | 3
SE&A FCT2006034 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 4.86 | 1(4.86), 3(For 48JA3) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40JG32A | 5 | 135 | - | 200 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 200 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 30 - 60 | 200 | 200 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 200 | 200 | 3
SE&A FCT2006035 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 4.86 | 1(4.86), 3(For 48JA3) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40JG32A | 5 | 135 | - | 240 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 240 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 30 - 60 | 200 | 240 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 200 | 200 | 3
SE&A FCT2006036 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 4.86 | 1(4.86), 3(For 48JA3) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40JG32A | 5 | 135 | - | 240 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 240 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 30 - 60 | 400 | 240 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 400 | 240 | 3
SE&A FCT2006037 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 4.86 | 1(4.86), 3(For 48JA3) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40JG32A | 5 | 135 | - | 480 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 480 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 30 - 60 | 200 | 480 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 200 | 480 | 3
SE&A FCT2006038 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 4.86 | 1(4.86), 3(For 48JA3) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40JG32A | 5 | 135 | - | 480 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 480 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 30 - 60 | 400 | 480 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 400 | 480 | 3
SE&A FCT2006039 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4.86 | 1(4.86), 3(For 48JA3) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40JG32A | 5 | 135 | - | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 600 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 30 - 60 | 200 | 600 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 200 | 600 | 3
SE&A FCT2006040 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4.86 | 1(4.86), 3(For 48JA3) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40JG32A | 5 | 135 | - | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 600 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 30 - 60 | 400 | 600 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 400 | 600 | 3
SE&A FCT2006041 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 75 | 221 | 6.94 | 1(6.94), See Also Note A | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40LP32A | 10 | 270 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 400 | 200 | 3
SE&A FCT2006042 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 75 | 221 | 6.94 | 1(6.94), See Also Note A | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40LP32A | 10 | 270 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 600 | 200 | 3
SE&A FCT2006043 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 6.94 | 1(6.94), See Also Note A | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40LP32A | 10 | 270 | - | 240 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 400 | 240 | 3
SE&A FCT2006044 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 6.94 | 1(6.94), See Also Note A | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240 | -
|  | F | Siemens | RK1, RK5 | 200 | - | See Below | 600
|  | MC | Siemens | 40LP32A | 10 | 270 | - | 240 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 600 | 240 | 3
SE&A FCT2006045 | A | DS | Siemens | JJ63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 6.94 | 1(6.94), See Also Note A | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40LP32A | 10 | 270 | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 400 | 480 | 3
SE&A FCT2006046 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 6.94 | 1(6.94), See Also Note A | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40LP32A | 10 | 270 | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 600 | 480 | 3
SE&A FCT2006047 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 6.94 | 1(6.94), See Also Note A | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40LP32A | 10 | 270 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 400 | 600 | 3
SE&A FCT2006048 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 6.94 | 1(6.94), See Also Note A | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40LP32A | 10 | 270 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 600 | 600 | 3
SE&A FCT2006049 | A | DS | Siemens | LXD63S600A | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 150 | 414 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40MP32A | 18 | 540 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 600 | 200 | 3
SE&A FCT2006050 | A | DS | Siemens | LXD63S600A | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 400 | 382 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | MC | Siemens | 40MP32A | 18 | 540 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 600 | 600 | 3
SE&A FCT2006051 | A | DS | Siemens | JXD63S400 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 75 | 221 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | MC | Siemens | 3RT1066 | 5 | 285 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 400 | 200 | 3
SE&A FCT2006052 | A | DS | Siemens | JXD63S400 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 75 | 221 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 3RT1066 | 5 | 285 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 200 | 3
SE&A FCT2006053 | A | DS | Siemens | JXD63S400 | 100 | - |  | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | MC | Siemens | 3RT1066 | 5 | 285 | - | 208 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 400 | 208 | 3
SE&A FCT2006054 | A | DS | Siemens | JXD63S400 | 100 | - |  | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 3RT1066 | 5 | 285 | - | 208 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 208 | 3
SE&A FCT2006055 | A | DS | Siemens | JXD63S400 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | MC | Siemens | 3RT1066 | 5 | 312 | - | 240 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 400 | 240 | 3
SE&A FCT2006056 | A | DS | Siemens | JXD63S400 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 3RT1066 | 5 | 312 | - | 240 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 240 | 3
SE&A FCT2006057 | A | DS | Siemens | JXD63S400 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | MC | Siemens | 3RT1066 | 5 | 302 | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 400 | 480 | 3
SE&A FCT2006058 | A | DS | Siemens | JXD63S400 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 3RT1066 | 5 | 302 | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 480 | 3
SE&A FCT2006059 | A | DS | Siemens | JXD63S400 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | MC | Siemens | 3RT1066 | 5 | 289 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 400 | 600 | 3
SE&A FCT2006060 | A | DS | Siemens | JXD63S400 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | MC | Siemens | 3RT1066 | 5 | 289 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 600 | 3
SE&A FCT2006061 | A | DS | Siemens | LXD63S600 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 150 | 414 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | MC | Siemens | 3RT1076 | 5 | 414 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 200 | 3
SE&A FCT2006062 | A | DS | Siemens | LXD63S600 | 100 | - |  | 600 | 3 | 100 | 208 | 3 | 150 | 396 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | MC | Siemens | 3RT1076 | 5 | 414 | - | 208 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 208 | 3
SE&A FCT2006063 | A | DS | Siemens | LXD63S600 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | FH | ANY | LISTED | SEE NOTE B | 600 |  | 240 | -
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | MC | Siemens | 3RT1076 | 5 | 480 | - | 240 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 240 | 3
SE&A FCT2006064 | A | DS | Siemens | LXD63S600 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | MC | Siemens | 3RT1076 | 5 | 477 | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 480 | 3
SE&A FCT2006065 | A | DS | Siemens | LXD63S600 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 400 | 382 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | MC | Siemens | 3RT1076 | 5 | 472 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 600 | 3

## Fusible-Starter
Certification of combinations of components in combination motor controllers for use in industrial control panels | [17 empty] | Last Revised: 2006-04-25
NOTE B: Where a fuseholder is specified, or where none is specified, as an alternative, any Listed Fuseholder may be used. The short-circuit current rating of the Combination will be restricted by the short-circuit current rating of the Fuseholder.
ID Number | Combination Type | Individual Component | [7 empty] | Combination SCCR | [6 empty] | Combination UL File | Enclosure Vol. (cu in)
|  | Type | Manufacturer | Catalog Designation | Ratings |  |  |  |  | kA | Volts | Ph | Maximum HP | Maximum NEC FLC | Minimum Enclosure Volume (cu ft) | Conditions of Acceptability
[5 empty] | kA | Overload Relay Current Rating | Maximum Fuse Current Rating | Volts | Poles
SE&A FST2006001 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK203 - Class J: FCJK603 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 3 | 200 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 5 | 200 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 30 | 200 | 3
SE&A FST2006002 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 1.5 | 6.9 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK203 - Class J: FCJK603 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 3 | 240 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 5 | 240 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 30 | 240 | 3
SE&A FST2006003 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 1.5 | 6.9 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK603 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 3 | 480 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 5 | 480 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 30 | 480 | 3
SE&A FST2006004 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 1.5 | 6.9 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK603 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 3 | 600 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 5 | 600 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 30 | 600 | 3
SE&A FST2006005 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK203 - Class J: FCJK603 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 3 | 200 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 5 | 200 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 15 | 200 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 30 | 200 | 3
SE&A FST2006006 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK203 - Class J: FCJK603 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 3 | 240 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 5 | 240 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 15 | 240 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 30 | 240 | 3
SE&A FST2006007 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK603 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 3 | 480 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 5 | 480 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 15 | 480 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 30 | 480 | 3
SE&A FST2006008 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 5 | 6.1 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK603 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 3 | 600 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 5 | 600 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 15 | 600 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 30 | 600 | 3
SE&A FST2006009 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK606 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 3 | 200 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 5 | 200 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 15 | 200 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 30 | 200 | 3
SE&A FST2006010 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK606 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 3 | 240 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 5 | 240 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 15 | 240 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 30 | 240 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 60 | 240 | 3
SE&A FST2006011 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK606 - Class J: FCJK606 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 3 | 480 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 5 | 480 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 15 | 480 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 30 | 480 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 60 | 480 | 3
SE&A FST2006012 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK606 - Class J: FCJK606 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 3 | 600 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 5 | 600 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 15 | 600 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 30 | 600 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 60 | 600 | 3
SE&A FST2006013 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK606 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 40 | 200 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 60 | 200 | 3
SE&A FST2006014 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK606 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 40 | 240 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 60 | 240 | 3
SE&A FST2006015 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK606 - Class J: FCJK606 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 40 | 480 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 60 | 480 | 3
SE&A FST2006016 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK606 - Class J: FCJK606 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 40 | 600 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 60 | 600 | 3
SE&A FST2006017 | A | DS | Siemens | MCS 610 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 50 | 200 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 100 | 200 | 3
SE&A FST2006018 | A | DS | Siemens | MCS 610 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 50 | 240 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 100 | 240 | 3
SE&A FST2006019 | A | DS | Siemens | MCS 610 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 50 | 480 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 100 | 480 | 3
SE&A FST2006020 | A | DS | Siemens | MCS 610 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 50 | 600 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 100 | 600 | 3
SE&A FST2006021 | A | DS | Siemens | MCS 610 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 200 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 200 | 3
SE&A FST2006022 | A | DS | Siemens | MCS 610 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 240 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 240 | 3
SE&A FST2006023 | A | DS | Siemens | MCS 610 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 480 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 480 | 3
SE&A FST2006024 | A | DS | Siemens | MCS 610 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 600 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 600 | 3
SE&A FST2006025 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 3.47 | 1(3.47) | E43399 Vol. 1 Sec. 6 | 5996.16
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 100 | 200 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 200 | 200 | 3
SE&A FST2006026 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3.47 | 1(3.47) | E43399 Vol. 1 Sec. 6 | 5996.16
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 100 | 240 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 200 | 240 | 3
SE&A FST2006027 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3.47 | 1(3.47) | E43399 Vol. 1 Sec. 6 | 5996.16
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 100 | 480 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 200 | 480 | 3
SE&A FST2006028 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 3.47 | 1(3.47) | E43399 Vol. 1 Sec. 6 | 5996.16
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 100 | 600 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 200 | 600 | 3
SE&A FST2006029 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 200 | 200 | 3
SE&A FST2006030 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 200 | 240 | 3
SE&A FST2006031 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 200 | 480 | 3
SE&A FST2006032 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 200 | 600 | 3
SE&A FST2006033 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 200 | 200 | 3
SE&A FST2006034 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 400 | 200 | 3
SE&A FST2006035 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 200 | 240 | 3
SE&A FST2006036 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 400 | 240 | 3
SE&A FST2006037 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 200 | 480 | 3
SE&A FST2006038 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 400 | 480 | 3
SE&A FST2006039 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 200 | 600 | 3
SE&A FST2006040 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 400 | 600 | 3
SE&A FST2006041 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 75 | 221 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14LPU32A | 10 | 55 - 250 | 400 | 200 | 3
SE&A FST2006042 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 75 | 221 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14LPU32A | 10 | 55 - 250 | 600 | 200 | 3
SE&A FST2006044 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14LPU32A | 10 | 55 - 250 | 400 | 240 | 3
SE&A FST2006045 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14LPU32A | 10 | 55 - 250 | 600 | 240 | 3
SE&A FST2006046 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14LPU32A | 10 | 55 - 250 | 400 | 480 | 3
SE&A FST2006047 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14LPU32A | 10 | 55 - 250 | 600 | 480 | 3
SE&A FST2006048 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14LP32A | 5 | na | 400 | 600 | 3
SE&A FST2006049 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | J | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14LPU32A | 10 | 55 - 250 | 600 | 600 | 3
SE&A FST2006050 | A | DS | Siemens | LXD63S600A | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 150 | 414 | 8.33 | 1(8.33) | E43399 Vol. 1 Sec. 6 | 14394.24
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5 | 200 | - | See Below | 600 | -
|  | STR | Siemens | 14MPX32A | 18 | 200 - 540 | 600 | 200 | 3
SE&A FCT2006051 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | FH | Siemens | Class R: FCRK203 - Class J: FCJK603 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3016 | 5 | 7.8 | 30 | 200 | 3
SE&A FCT2006052 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | FH | Siemens | Class R: FCRK203 - Class J: FCJK603 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3016 | 5 | 6.8 | 30 | 240 | 3
SE&A FCT2006053 | A | DS | Siemens | MCS603 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK603 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3016 | 5 | 7.6 | 30 | 480 | 3
SE&A FCT2006054 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK606 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3026 | 5 | 25.3 | 60 | 200 | 3
SE&A FCT2006055 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK606 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3026 | 5 | 22 | 60 | 240 | 3
SE&A FCT2006056 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | FH | Siemens | Class R: FCRK606 - Class J: FCJK606 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3026 | 5 | 21 | 60 | 480 | 3
SE&A FCT2006057 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | FH | Siemens | Class R: FCRK606 - Class J: FCJK606 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3026 | 5 | 22 | 60 | 600 | 3
SE&A FCT2006058 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK606 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3036 | 5 | 32.2 | 60 | 200 | 3
SE&A FCT2006059 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | FH | Siemens | Class R: FCRK206 - Class J: FCJK606 | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3036 | 5 | 42 | 60 | 240 | 3
SE&A FCT2006060 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | FH | Siemens | Class R: FCRK606 - Class J: FCJK606 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3036 | 5 | 40 | 60 | 480 | 3
SE&A FCT2006061 | A | DS | Siemens | MCS606 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | FH | Siemens | Class R: FCRK606 - Class J: FCJK606 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3036 | 5 | 41 | 60 | 600 | 3
SE&A FCT2006062 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3046 | 5 | 92 | 200 | 200 | 3
SE&A FCT2006063 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3046 | 5 | 80 | 200 | 240 | 3
SE&A FCT2006064 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3046 | 5 | 96 | 200 | 480 | 3
SE&A FCT2006065 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3046 | 5 | 99 | 200 | 600 | 3
SE&A FCT2006066 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 4.16 | 1(4.16) | E43399 Vol. 1 Sec. 6 | 7188.48
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3452 | 5 | 32.2 | 100 | 200 | 3
SE&A FCT2006067 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4.16 | 1(4.16) | E43399 Vol. 1 Sec. 6 | 7188.48
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3452 | 5 | 28 | 100 | 240 | 3
SE&A FCT2006068 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4.16 | 1(4.16) | E43399 Vol. 1 Sec. 6 | 7188.48
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3452 | 5 | 34 | 100 | 480 | 3
SE&A FCT2006069 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4.16 | 1(4.16) | E43399 Vol. 1 Sec. 6 | 7188.48
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3452 | 5 | 32 | 100 | 600 | 3
SE&A FCT2006070 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3454 | 5 | 48.3 | 100 | 200 | 3
SE&A FCT2006071 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 20 | 42 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3454 | 5 | 42 | 100 | 240 | 3
SE&A FCT2006072 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3454 | 5 | 52 | 100 | 480 | 3
SE&A FCT2006073 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3454 | 5 | 52 | 100 | 600 | 3
SE&A FCT2006074 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3455 | 5 | 62.1 | 100 | 200 | 3
SE&A FCT2006075 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3455 | 5 | 68 | 100 | 240 | 3
SE&A FCT2006076 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3455 | 5 | 65 | 100 | 480 | 3
SE&A FCT2006077 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3455 | 5 | 62 | 100 | 600 | 3
SE&A FCT2006078 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3456 | 5 | 78.2 | 100 | 200 | 3
SE&A FCT2006079 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3456 | 5 | 80 | 100 | 240 | 3
SE&A FCT2006080 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3456 | 5 | 77 | 100 | 480 | 3
SE&A FCT2006081 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3456 | 5 | 77 | 100 | 600 | 3
SE&A FCT2006082 | A | DS | Siemens | MCS610 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK610 - Class J: FCK610 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3458 | 5 | 92 | 100 | 200 | 3
SE&A FCT2006083 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3458 | 5 | 104 | 100 | 240 | 3
SE&A FCT2006084 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3458 | 5 | 96 | 100 | 600 | 3
SE&A FCT2006085 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4.86 | 1(4.86) | E43399 Vol. 1 Sec. 6 | 8398.08
|  | FH | Siemens | Class R: FCRK620 - Class J: FCK620 | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3458 | 5 | 99 | 100 | 600 | 3
SE&A FCT2006086 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3465 | 5 | 120 | 400 | 200 | 3
SE&A FCT2006087 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3465 | 5 | 130 | 400 | 240 | 3
SE&A FCT2006088 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3465 | 5 | 124 | 400 | 480 | 3
SE&A FCT2006089 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3465 | 5 | 125 | 400 | 600 | 3
SE&A FCT2006090 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 60 | 177 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3466 | 5 | 177 | 400 | 200 | 3
SE&A FCT2006091 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3466 | 5 | 192 | 400 | 240 | 3
SE&A FCT2006092 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3466 | 5 | 180 | 400 | 480 | 3
SE&A FCT2006093 | A | DS | Siemens | MCS620 | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 175 | 168 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | MC | Siemens | 3RW3466 | 5 | 168 | 400 | 600 | 3
SE&A FCT2006094 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 75 | 221 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3467 | 5 | 221 | 400 | 200 | 3
SE&A FCT2006095 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3467 | 5 | 248 | 400 | 240 | 3
SE&A FCT2006096 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3467 | 5 | 240 | 400 | 480 | 3
SE&A FCT2006097 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 6.94 | 1(6.94) | E43399 Vol. 1 Sec. 6 | 11992.32
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3467 | 5 | 242 | 400 | 600 | 3
SE&A FCT2006098 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 75 | 221 | 15 | 1(15.00) | E43399 Vol. 1 Sec. 6 | 25920
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3468 | 5 | 221 | 600 | 200 | 3
SE&A FCT2006099 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 15 | 1(15.00) | E43399 Vol. 1 Sec. 6 | 25920
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3468 | 5 | 248 | 600 | 240 | 3
SE&A FCT2006100 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 15 | 1(15.00) | E43399 Vol. 1 Sec. 6 | 25920
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3468 | 5 | 240 | 600 | 480 | 3
SE&A FCT2006101 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 15 | 1(15.00) | E43399 Vol. 1 Sec. 6 | 25920
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3468 | 5 | 242 | 600 | 600 | 3
SE&A FCT2006102 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 200 | 3 | 125 | 359 | 15 | 1(15.00) | E43399 Vol. 1 Sec. 6 | 25920
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3472 | 5 | 359 | 600 | 200 | 3
SE&A FCT2006103 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 15 | 1(15.00) | E43399 Vol. 1 Sec. 6 | 25920
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 240
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3472 | 5 | 360 | 600 | 240 | 3
SE&A FCT2006104 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 15 | 1(15.00) | E43399 Vol. 1 Sec. 6 | 25920
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3472 | 5 | 361 | 600 | 480 | 3
SE&A FCT2006105 | A | DS | Siemens | JD63S400A or JXD63S400A | 100 | - |  | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 15 | 1(15.00) | E43399 Vol. 1 Sec. 6 | 25920
|  | FH | ANY | LISTED | SEE NOTE B |  |  | 600
|  | F | ANY | RK1, RK5, J | 200 | - | See Below | 600
|  | STR | Siemens | 3RW3472 | 5 | 336 | 600 | 600 | 3

## I.T. C.B.-Contactor&O.L.Relay
Certification of combinations of components in combination motor controllers for use in industrial control panels | [17 empty] | Last Revised: 2024-03-06
NOTE A: For Combinations using current transformers, the current transformer must be provided as specified on the installation instructions for the overload relay.
ID Number | Combination Type | Individual Component | [7 empty] | Combination SCCR | [6 empty] | Combination UL File | Enclosure Vol. (cu in)
|  | Type | Manufacturer | Catalog Designation | Ratings |  |  |  |  | kA | Volts | Ph | Maximum HP | Maximum NEC FLC | Minimum Enclosure Volume (cu ft) | Conditions of Acceptability
[5 empty] | kA | Overload Relay Current Rating | Circuit Breaker Current Rating | Volts | Poles
SE&A ITCTR2006001 | D | ICB | Siemens | ED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 200 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 200 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 200 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 10 | 200 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 10 | 200 | 3
SE&A ITCTR2006002 | D | ICB | Siemens | CED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 200 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 200 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 200 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 10 | 200 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 10 | 200 | 3
SE&A ITCTR2006005 | D | ICB | Siemens | ED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 1.5 | 6 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 10 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 10 | 240 | 3
SE&A ITCTR2006006 | D | ICB | Siemens | CED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 1.5 | 6 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 10 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 10 | 240 | 3
SE&A ITCTR2006007 | D | ICB | Siemens | ED63A | - | - | See Below | 480 | 3 | 30 | 480 | 3 | 2 | 3.4 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 480 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 480 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 480 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 10 | 480 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 10 | 480 | 3
SE&A ITCTR2006008 | D | ICB | Siemens | CED63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 2 | 3.4 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 480 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 480 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 480 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 10 | 480 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 10 | 480 | 3
SE&A ITCTR2006009 | D | ICB | Siemens | ED63A | - | - | See Below | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 600 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 600 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 600 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 5 | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 5 | 600 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 5 | 600 | 3
SE&A ITCTR2006010 | D | ICB | Siemens | CED63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 2 | 2.7 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 600 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 600 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 600 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 5 | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 5 | 600 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 5 | 600 | 3
SE&A ITCTR2006011 | D | ICB | Siemens | ED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 200 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 200 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 200 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 25 | 200 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 25 | 200 | 3
SE&A ITCTR2006012 | D | ICB | Siemens | CED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 200 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 200 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 200 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 25 | 200 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 25 | 200 | 3
SE&A ITCTR2006015 | D | ICB | Siemens | ED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 3 | 9.6 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 25 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 25 | 240 | 3
SE&A ITCTR2006016 | D | ICB | Siemens | CED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 3 | 9.6 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 25 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 25 | 240 | 3
SE&A ITCTR2006017 | D | ICB | Siemens | ED63A | - | - | See Below | 240 | 3 | 30 | 480 | 3 | 5 | 7.6 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 25 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 25 | 240 | 3
SE&A ITCTR2006018 | D | ICB | Siemens | ED63A | - | - | See Below | 480 | 3 | 30 | 480 | 3 | 5 | 7.6 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 480 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 480 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 480 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 25 | 480 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 25 | 480 | 3
SE&A ITCTR2006019 | D | ICB | Siemens | ED63A | - | - | See Below | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 600 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 600 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 600 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 10 | 600 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 10 | 600 | 3
SE&A ITCTR2006020 | D | ICB | Siemens | CED63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 5 | 6.1 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 600 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 600 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 600 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 10 | 600 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 10 | 600 | 3
SE&A ITCTR2006021 | D | ICB | Siemens | ED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 7.5 | 22 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 25 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 25 | 240 | 3
SE&A ITCTR2006022 | D | ICB | Siemens | CED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 7.5 | 22 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 25 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 25 | 240 | 3
SE&A ITCTR2006023 | D | ICB | Siemens | ED63A | - | - | See Below | 480 | 3 | 30 | 480 | 3 | 10 | 14 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 480 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 480 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 480 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 25 | 480 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 25 | 480 | 3
SE&A ITCTR2006024 | D | ICB | Siemens | CED63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 10 | 14 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 480 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 480 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 480 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 25 | 480 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 25 | 480 | 3
SE&A ITCTR2006025 | D | ICB | Siemens | ED63A | - | - | See Below | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 600 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 600 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 600 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 25 | 600 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 25 | 600 | 3
SE&A ITCTR2006026 | D | ICB | Siemens | CED63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 10 | 11 | 0.694 | 1(0.69), 3(For 48DC3), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 600 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 1 | 600 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 5 | 600 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 10 | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 25 | 600 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 25 | 600 | 3
SE&A ITCTR2006027 | D | ICB | Siemens | ED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38), 3(For 48EC3), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 25 | 200 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 200 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 200 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 40 | 200 | 3
SE&A ITCTR2006028 | D | ICB | Siemens | CED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38), 3(For 48EC3), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 25 | 200 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 200 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 200 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 40 | 200 | 3
SE&A ITCTR2006029 | D | ICB | Siemens | ED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 10 | 28 | 1.38 | 1(1.38), 3(For 48EC3), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 25 | 240 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 240 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 240 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 40 | 240 | 3
SE&A ITCTR2006030 | D | ICB | Siemens | CED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 10 | 28 | 1.38 | 1(1.38), 3(For 48EC3), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 25 | 240 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 240 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 240 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 40 | 240 | 3
SE&A ITCTR2006031 | D | ICB | Siemens | ED63A | - | - | See Below | 480 | 3 | 30 | 480 | 3 | 15 | 21 | 1.38 | 1(1.38), 3(For 48EC3), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 25 | 480 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 480 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 480 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 40 | 480 | 3
SE&A ITCTR2006032 | D | ICB | Siemens | CED63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 15 | 21 | 1.38 | 1(1.38), 3(For 48EC3), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 25 | 480 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 480 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 480 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 40 | 480 | 3
SE&A ITCTR2006033 | D | ICB | Siemens | ED63A | - | - | See Below | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1.38 | 1(1.38), 3(For 48EC3), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 25 | 600 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 25 | 600 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 25 | 600 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 25 | 600 | 3
SE&A ITCTR2006034 | D | ICB | Siemens | CED63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 15 | 17 | 1.38 | 1(1.38), 3(For 48EC3), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 25 | 600 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 25 | 600 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 25 | 600 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 25 | 600 | 3
SE&A ITCTR2006035 | D | ICB | Siemens | ED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38), 3(For 48GC3), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 25 | 200 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 200 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 50 | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 50 | 200 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 50 | 200 | 3
SE&A ITCTR2006036 | D | ICB | Siemens | CED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38), 3(For 48GC3), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 25 | 200 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 200 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 50 | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 50 | 200 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 50 | 200 | 3
SE&A ITCTR2006037 | D | ICB | Siemens | ED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 15 | 42 | 1.38 | 1(1.38), 3(For 48GC3), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 25 | 240 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 240 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 50 | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 50 | 240 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 50 | 240 | 3
SE&A ITCTR2006038 | D | ICB | Siemens | CED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 15 | 42 | 1.38 | 1(1.38), 3(For 48GC3), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 25 | 240 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 240 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 50 | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 50 | 240 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 50 | 240 | 3
SE&A ITCTR2006039 | D | ICB | Siemens | ED63A | - | - | See Below | 480 | 3 | 30 | 480 | 3 | 25 | 34 | 1.38 | 1(1.38), 3(For 48GC3), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 25 | 480 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 480 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 50 | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 50 | 480 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 50 | 480 | 3
SE&A ITCTR2006040 | D | ICB | Siemens | CED63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 25 | 34 | 1.38 | 1(1.38), 3(For 48GC3), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 25 | 480 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 480 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 50 | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 50 | 480 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 50 | 480 | 3
SE&A ITCTR2006041 | D | ICB | Siemens | ED63A | - | - | See Below | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1.38 | 1(1.38), 3(For 48GC3), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 25 | 600 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 600 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 40 | 600 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 40 | 600 | 3
SE&A ITCTR2006042 | D | ICB | Siemens | CED63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 25 | 27 | 1.38 | 1(1.38), 3(For 48GC3), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 25 | 600 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 40 | 600 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 50 | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 50 | 600 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 50 | 600 | 3
SE&A ITCTR2006043 | D | ICB | Siemens | ED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2.08 | 1(2.08), 3(For 48GC3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 200 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 50 | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 200 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 200 | 3
SE&A ITCTR2006044 | D | ICB | Siemens | CED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2.08 | 1(2.08), 3(For 48GC3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 200 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 50 | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 200 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 200 | 3
SE&A ITCTR2006045 | D | ICB | Siemens | ED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 20 | 54 | 2.08 | 1(2.08), 3(For 48GC3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 240 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 50 | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 240 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 240 | 3
SE&A ITCTR2006046 | D | ICB | Siemens | CED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 20 | 54 | 2.08 | 1(2.08), 3(For 48GC3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 240 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 50 | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 240 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 240 | 3
SE&A ITCTR2006047 | D | ICB | Siemens | ED63A | - | - | See Below | 480 | 3 | 30 | 480 | 3 | 30 | 40 | 2.08 | 1(2.08), 3(For 48GC3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 480 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 50 | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 480 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 480 | 3
SE&A ITCTR2006048 | D | ICB | Siemens | CED63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 30 | 40 | 2.08 | 1(2.08), 3(For 48GC3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 480 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 50 | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 480 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 480 | 3
SE&A ITCTR2006049 | D | ICB | Siemens | ED63A | - | - | See Below | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2.08 | 1(2.08), 3(For 48GC3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 600 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 40 | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 40 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 40 | 600 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 40 | 600 | 3
SE&A ITCTR2006050 | D | ICB | Siemens | CED63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 30 | 32 | 2.08 | 1(2.08), 3(For 48GC3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 600 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 40 | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 40 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 40 | 600 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 40 | 600 | 3
SE&A ITCTR2006051 | D | ICB | Siemens | ED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2.08 | 1(2.08), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 200 | 3
SE&A ITCTR2006052 | D | ICB | Siemens | CED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2.08 | 1(2.08), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 200 | 3
SE&A ITCTR2006053 | D | ICB | Siemens | ED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2.08 | 1(2.08), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 240 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 240 | 3
SE&A ITCTR2006054 | D | ICB | Siemens | CED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2.08 | 1(2.08), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 240 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 240 | 3
SE&A ITCTR2006055 | D | ICB | Siemens | ED63A | - | - | See Below | 480 | 3 | 30 | 480 | 3 | 50 | 65 | 2.08 | 1(2.08), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 480 | 3
SE&A ITCTR2006056 | D | ICB | Siemens | CED63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 50 | 65 | 2.08 | 1(2.08), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 480 | 3
SE&A ITCTR2006057 | D | ICB | Siemens | ED63A | - | - | See Below | 600 | 3 | 18 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 600 | 3
SE&A ITCTR2006058 | D | ICB | Siemens | CED63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 600 | 3
SE&A ITCTR2006059 | D | ICB | Siemens | FXD63A | - | - | See Below | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 150 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 600 | 3
SE&A ITCTR2006060 | D | ICB | Siemens | CFXD63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 150 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 600 | 3
SE&A ITCTR2006061 | D | ICB | Siemens | ED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 2.08 | 1(2.08), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 200 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 200 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 200 | 3
SE&A ITCTR2006062 | D | ICB | Siemens | CED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 2.08 | 1(2.08), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 200 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 200 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 200 | 3
SE&A ITCTR2006063 | D | ICB | Siemens | ED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 40 | 104 | 2.08 | 1(2.08), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 240 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 240 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 240 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 240 | 3
SE&A ITCTR2006064 | D | ICB | Siemens | CED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 40 | 104 | 2.08 | 1(2.08), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 240 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 240 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 240 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 240 | 3
SE&A ITCTR2006065 | D | ICB | Siemens | ED63A | - | - | See Below | 480 | 3 | 30 | 480 | 3 | 75 | 96 | 2.08 | 1(2.08), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 480 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 480 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 460 | 3
SE&A ITCTR2006066 | D | ICB | Siemens | CED63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 75 | 96 | 2.08 | 1(2.08), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 480 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 480 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 460 | 3
SE&A ITCTR2006067 | D | ICB | Siemens | ED63A | - | - | See Below | 600 | 3 | 18 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 600 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 600 | 3
SE&A ITCTR2006068 | D | ICB | Siemens | CED63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 600 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 600 | 3
SE&A ITCTR2006069 | D | ICB | Siemens | FXD63A | - | - | See Below | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 600 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 600 | 3
SE&A ITCTR2006070 | D | ICB | Siemens | CFXD63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78), 3(For 48HA3), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 100 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 600 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 600 | 3
SE&A ITCTR2006071 | D | ICB | Siemens | FXD63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 40 | 120 | 2.78 | 1(2.78), 3(For 48JA3), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 200 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 200 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 150 | 200 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 150 | 200 | 3
SE&A ITCTR2006072 | D | ICB | Siemens | CFXD63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 40 | 120 | 2.78 | 1(2.78), 3(For 48JA3), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 200 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 200 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 150 | 200 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 150 | 200 | 3
SE&A ITCTR2006073 | D | ICB | Siemens | FXD63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 50 | 130 | 2.78 | 1(2.78), 3(For 48JA3), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 240 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 240 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 150 | 240 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 150 | 240 | 3
SE&A ITCTR2006074 | D | ICB | Siemens | CFXD63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 50 | 130 | 2.78 | 1(2.78), 3(For 48JA3), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 240 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 240 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 150 | 240 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 150 | 240 | 3
SE&A ITCTR2006075 | D | ICB | Siemens | FXD63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 100 | 124 | 2.78 | 1(2.78), 3(For 48JA3), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 480 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 480 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 150 | 480 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 150 | 480 | 3
SE&A ITCTR2006076 | D | ICB | Siemens | CFXD63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 100 | 124 | 2.78 | 1(2.78), 3(For 48JA3), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 480 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 480 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 150 | 480 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 150 | 480 | 3
SE&A ITCTR2006077 | D | ICB | Siemens | ED63A | - | - | See Below | 600 | 3 | 18 | 600 | 3 | 100 | 99 | 2.78 | 1(2.78), 3(For 48JA3), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 600 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 150 | 600 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 125 | 600 | 3
SE&A ITCTR2006078 | D | ICB | Siemens | CED63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 100 | 99 | 2.78 | 1(2.78), 3(For 48JA3), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 600 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 150 | 600 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 125 | 600 | 3
SE&A ITCTR2006079 | D | ICB | Siemens | JXD63A | - | - | See Below | 480 | 3 | 35 | 480 | 3 | 200 | 240 | 4.16 | 1(4.16), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 7188.48
|  | MC | Siemens | 40LP32A | 10 | 270 | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 400 | 480 | 3
SE&A ITCTR2006080 | D | ICB | Siemens | JXD63A | - | - | See Below | 600 | 3 | 25 | 600 | 3 | 200 | 192 | 4.16 | 1(4.16), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 7188.48
|  | MC | Siemens | 40LP32A | 10 | 270 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 400 | 600 | 3
SE&A ITCTR2006081 | D | ICB | Siemens | LXD63H | - | - | See Below | 600 | 3 | 25 | 600 | 3 | 400 | 382 | 5.55 | 1(5.55), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 40MP32A | 18 | 540 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 400 | 600 | 3
SE&A ITCTR2006109 | D | ICB | Siemens | JXD63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 75 | 221 | 4.16 | 1(4.16), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 7188.48
|  | MC | Siemens | 3RT1066 | 10 | 285 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 400 | 200 | 3
SE&A ITCTR2006110 | D | ICB | Siemens | JXD63A | - | - | See Below | 208 | 3 | 100 | 208 | 3 | 75 | 211 | 4.16 | 1(4.16), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 7188.48
|  | MC | Siemens | 3RT1066 | 10 | 285 | - | 208 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 400 | 208 | 3
SE&A ITCTR2006111 | D | ICB | Siemens | JXD63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 100 | 248 | 4.16 | 1(4.16), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 7188.48
|  | MC | Siemens | 3RT1066 | 10 | 312 | - | 240 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 400 | 240 | 3
SE&A ITCTR2006112 | D | ICB | Siemens | JXD63A | - | - | See Below | 480 | 3 | 35 | 480 | 3 | 200 | 240 | 4.16 | 1(4.16), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 7188.48
|  | MC | Siemens | 3RT1066 | 10 | 302 | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 400 | 480 | 3
SE&A ITCTR2006113 | D | ICB | Siemens | JXD63A | - | - | See Below | 600 | 3 | 25 | 600 | 3 | 200 | 192 | 4.16 | 1(4.16), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 7188.48
|  | MC | Siemens | 3RT1066 | 10 | 289 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 400 | 600 | 3
SE&A ITCTR2006114 | D | ICB | Siemens | FXD63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 60 | 177 | 2.08 | 1(2.08), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 3RT1264 | 18 | 177 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 250 | 200 | 3
SE&A ITCTR2006115 | D | ICB | Siemens | FXD63A | - | - | See Below | 208 | 3 | 100 | 208 | 3 | 60 | 169 | 2.08 | 1(2.08), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 3RT1264 | 18 | 177 | - | 208 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 250 | 208 | 3
SE&A ITCTR2006116 | D | ICB | Siemens | FXD63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 75 | 192 | 2.08 | 1(2.08), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 3RT1264 | 18 | 192 | - | 240 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 250 | 240 | 3
SE&A ITCTR2006117 | D | ICB | Siemens | FXD63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 150 | 180 | 2.08 | 1(2.08), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 3RT1264 | 18 | 180 | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 250 | 480 | 3
SE&A ITCTR2006118 | D | ICB | Siemens | FXD63A | - | - | See Below | 600 | 3 | 25 | 600 | 3 | 200 | 192 | 2.08 | 1(2.08), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 3RT1264 | 18 | 192 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 250 | 600 | 3
SE&A ITCTR2006119 | D | ICB | Siemens | JXD63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 100 | 285 | 5.55 | 1(5.55), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 3RT1266 | 18 | 285 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 400 | 200 | 3
SE&A ITCTR2006120 | D | ICB | Siemens | JXD63A | - | - | See Below | 208 | 3 | 100 | 208 | 3 | 100 | 273 | 5.55 | 1(5.55), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 3RT1266 | 18 | 285 | - | 208 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 400 | 208 | 3
SE&A ITCTR2006121 | D | ICB | Siemens | JXD63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 125 | 312 | 5.55 | 1(5.55), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 3RT1266 | 18 | 312 | - | 240 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 400 | 240 | 3
SE&A ITCTR2006122 | D | ICB | Siemens | JXD63A | - | - | See Below | 480 | 3 | 35 | 480 | 3 | 250 | 302 | 5.55 | 1(5.55), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 3RT1264 | 18 | 302 | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 400 | 480 | 3
SE&A ITCTR2006123 | D | ICB | Siemens | JXD63A | - | - | See Below | 600 | 3 | 25 | 600 | 3 | 300 | 289 | 5.55 | 1(5.55), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 3RT1266 | 18 | 289 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 400 | 600 | 3
SE&A ITCTR2006124 | D | ICB | Siemens | LXD63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 150 | 414 | 8.33 | 1(8.33), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | MC | Siemens | 3RT1276 | 18 | 414 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 200 | 3
SE&A ITCTR2006125 | D | ICB | Siemens | LXD63A | - | - | See Below | 208 | 3 | 100 | 208 | 3 | 150 | 396 | 8.33 | 1(8.33), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | MC | Siemens | 3RT1276 | 18 | 414 | - | 208 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 208 | 3
SE&A ITCTR2006126 | D | ICB | Siemens | LXD63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 200 | 480 | 8.33 | 1(8.33), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | MC | Siemens | 3RT1276 | 18 | 480 | - | 240 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 240 | 3
SE&A ITCTR2006127 | D | ICB | Siemens | LXD63A | - | - | See Below | 480 | 3 | 35 | 480 | 3 | 400 | 477 | 8.33 | 1(8.33), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | MC | Siemens | 3RT1276 | 18 | 477 | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 480 | 3
SE&A ITCTR2006128 | D | ICB | Siemens | LXD63A | - | - | See Below | 600 | 3 | 25 | 600 | 3 | 500 | 472 | 8.33 | 1(8.33), 5, See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | MC | Siemens | 3RT1276 | 18 | 472 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 600 | 3

## I.T. C.B.-Starter
Certification of combinations of components in combination motor controllers for use in industrial control panels | [17 empty] | Last Revised: 2024-03-06
ID Number | Combination Type | Individual Component | [7 empty] | Combination SCCR | [6 empty] | Combination UL File | Enclosure Vol. (cu in)
|  | Type | Manufacturer | Catalog Designation | Ratings |  |  |  |  | kA | Volts | Ph | Maximum HP | Maximum NEC FLC | Minimum Enclosure Volume (cu ft) | Conditions of Acceptability
[5 empty] | kA | Overload Relay Current Rating | Circuit Breaker Current Rating | Volts | Poles
SE&A ITST2006001 | D | ICB | Siemens | ED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 1 | 200 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 5 | 200 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 10 | 200 | 3
SE&A ITST2006002 | D | ICB | Siemens | CED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 1 | 200 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 5 | 200 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 10 | 200 | 3
SE&A ITST2006003 | D | ICB | Siemens | ED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 1.5 | 6 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 1 | 240 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 5 | 240 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 10 | 240 | 3
SE&A ITST2006004 | D | ICB | Siemens | CED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 1.5 | 6 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 1 | 240 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 5 | 240 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 10 | 240 | 3
SE&A ITST2006005 | D | ICB | Siemens | ED63A | - | - | See Below | 480 | 3 | 30 | 480 | 3 | 2 | 3.4 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 1 | 480 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 5 | 480 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 10 | 480 | 3
SE&A ITST2006006 | D | ICB | Siemens | CED63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 2 | 3.4 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 1 | 480 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 5 | 480 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 10 | 480 | 3
SE&A ITST2006007 | D | ICB | Siemens | ED63A | - | - | See Below | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 1 | 600 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 5 | 600 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 5 | 600 | 3
SE&A ITST2006008 | D | ICB | Siemens | CED63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 2 | 2.7 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 1 | 600 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 5 | 600 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 5 | 600 | 3
SE&A ITST2006009 | D | ICB | Siemens | ED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 1 | 200 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 5 | 200 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 10 | 200 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 25 | 200 | 3
SE&A ITST2006010 | D | ICB | Siemens | CED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 1 | 200 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 5 | 200 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 10 | 200 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 25 | 200 | 3
SE&A ITST2006011 | D | ICB | Siemens | ED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 3 | 9.6 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 1 | 240 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 5 | 240 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 10 | 240 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 25 | 240 | 3
SE&A ITST2006012 | D | ICB | Siemens | CED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 3 | 9.6 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 1 | 240 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 5 | 240 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 10 | 240 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 25 | 240 | 3
SE&A ITST2006013 | D | ICB | Siemens | ED63A | - | - | See Below | 480 | 3 | 30 | 480 | 3 | 5 | 7.6 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 1 | 480 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 5 | 480 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 10 | 480 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 25 | 480 | 3
SE&A ITST2006014 | D | ICB | Siemens | CED63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 5 | 7.6 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 1 | 480 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 5 | 480 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 10 | 480 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 25 | 480 | 3
SE&A ITST2006015 | D | ICB | Siemens | ED63A | - | - | See Below | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 1 | 600 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 5 | 600 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 10 | 600 | 3
SE&A ITST2006016 | D | ICB | Siemens | CED63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 5 | 6.1 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 1 | 600 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 5 | 600 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 10 | 600 | 3
SE&A ITST2006017 | D | ICB | Siemens | ED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 7.5 | 22 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 1 | 240 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 5 | 240 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 10 | 240 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 25 | 240 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 25 | 240 | 3
SE&A ITST2006018 | D | ICB | Siemens | CED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 7.5 | 22 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 1 | 240 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 5 | 240 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 10 | 240 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 25 | 240 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 25 | 240 | 3
SE&A ITST2006019 | D | ICB | Siemens | ED63A | - | - | See Below | 480 | 3 | 30 | 480 | 3 | 10 | 14 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 1 | 480 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 5 | 480 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 10 | 480 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 25 | 480 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 25 | 480 | 3
SE&A ITST2006020 | D | ICB | Siemens | CED63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 10 | 14 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 1 | 480 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 5 | 480 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 10 | 480 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 25 | 480 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 25 | 480 | 3
SE&A ITST2006021 | D | ICB | Siemens | ED63A | - | - | See Below | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 1 | 600 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 5 | 600 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 10 | 600 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 25 | 600 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 25 | 600 | 3
SE&A ITST2006022 | D | ICB | Siemens | CED63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 10 | 11 | 0.694 | 1(0.69), 5 | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 1 | 600 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 5 | 600 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 10 | 600 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 25 | 600 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 25 | 600 | 3
SE&A ITST2006023 | D | ICB | Siemens | ED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 25 | 200 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 40 | 200 | 3
SE&A ITST2006024 | D | ICB | Siemens | CED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 25 | 200 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 40 | 200 | 3
SE&A ITST2006025 | D | ICB | Siemens | ED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 10 | 28 | 1.38 | 1(1.38), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 25 | 240 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 40 | 240 | 3
SE&A ITST2006026 | D | ICB | Siemens | CED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 10 | 28 | 1.38 | 1(1.38), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 25 | 240 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 40 | 240 | 3
SE&A ITST2006027 | D | ICB | Siemens | ED63A | - | - | See Below | 480 | 3 | 30 | 480 | 3 | 15 | 21 | 1.38 | 1(1.38), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 25 | 480 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 40 | 480 | 3
SE&A ITST2006028 | D | ICB | Siemens | CED63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 15 | 21 | 1.38 | 1(1.38), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 25 | 480 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 40 | 480 | 3
SE&A ITST2006029 | D | ICB | Siemens | ED63A | - | - | See Below | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1.38 | 1(1.38), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 25 | 600 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 40 | 600 | 3
SE&A ITST2006030 | D | ICB | Siemens | CED63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 15 | 17 | 1.38 | 1(1.38), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 25 | 600 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 40 | 600 | 3
SE&A ITST2006031 | D | ICB | Siemens | ED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 25 | 200 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 50 | 200 | 3
SE&A ITST2006032 | D | ICB | Siemens | CED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 25 | 200 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 50 | 200 | 3
SE&A ITST2006033 | D | ICB | Siemens | ED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 15 | 42 | 1.38 | 1(1.38), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 25 | 240 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 50 | 240 | 3
SE&A ITST2006034 | D | ICB | Siemens | CED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 15 | 42 | 1.38 | 1(1.38), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 25 | 240 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 50 | 240 | 3
SE&A ITST2006035 | D | ICB | Siemens | ED63A | - | - | See Below | 480 | 3 | 30 | 480 | 3 | 25 | 34 | 1.38 | 1(1.38), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 25 | 480 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 50 | 480 | 3
SE&A ITST2006036 | D | ICB | Siemens | CED63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 25 | 34 | 1.38 | 1(1.38), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 25 | 480 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 50 | 480 | 3
SE&A ITST2006037 | D | ICB | Siemens | ED63A | - | - | See Below | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1.38 | 1(1.38), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 25 | 600 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 40 | 600 | 3
SE&A ITST2006038 | D | ICB | Siemens | CED63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 25 | 27 | 1.38 | 1(1.38), 5 | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 25 | 600 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 40 | 600 | 3
SE&A ITST2006039 | D | ICB | Siemens | ED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 200 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 200 | 3
SE&A ITST2006040 | D | ICB | Siemens | CED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 200 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 200 | 3
SE&A ITST2006041 | D | ICB | Siemens | ED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 20 | 54 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 240 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 240 | 3
SE&A ITST2006042 | D | ICB | Siemens | CED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 20 | 54 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 240 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 240 | 3
SE&A ITST2006043 | D | ICB | Siemens | ED63A | - | - | See Below | 480 | 3 | 30 | 480 | 3 | 30 | 40 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 480 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 480 | 3
SE&A ITST2006044 | D | ICB | Siemens | CED63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 30 | 40 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 480 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 480 | 3
SE&A ITST2006045 | D | ICB | Siemens | ED63A | - | - | See Below | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 40 | 600 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 40 | 600 | 3
SE&A ITST2006046 | D | ICB | Siemens | CED63A | - | - | See Below | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 40 | 600 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 40 | 600 | 3
SE&A ITST2006047 | D | ICB | Siemens | ED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 100 | 200 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 125 | 200 | 3
SE&A ITST2006048 | D | ICB | Siemens | CED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 100 | 200 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 125 | 200 | 3
SE&A ITST2006049 | D | ICB | Siemens | ED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 100 | 240 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 125 | 240 | 3
SE&A ITST2006050 | D | ICB | Siemens | CED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 100 | 240 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 125 | 240 | 3
SE&A ITST2006051 | D | ICB | Siemens | ED63A | - | - | See Below | 480 | 3 | 30 | 480 | 3 | 50 | 65 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 100 | 480 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 125 | 480 | 3
SE&A ITST2006052 | D | ICB | Siemens | CED63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 50 | 65 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 100 | 480 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 125 | 480 | 3
SE&A ITST2006053 | D | ICB | Siemens | ED63A | - | - | See Below | 600 | 3 | 18 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 100 | 600 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 100 | 600 | 3
SE&A ITST2006054 | D | ICB | Siemens | CED63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 100 | 600 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 100 | 600 | 3
SE&A ITST2006055 | D | ICB | Siemens | FD63A | - | - | See Below | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 100 | 600 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 100 | 600 | 3
SE&A ITST2006056 | D | ICB | Siemens | CFD63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 100 | 600 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 100 | 600 | 3
SE&A ITST2006057 | D | ICB | Siemens | ED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 125 | 200 | 3
SE&A ITST2006058 | D | ICB | Siemens | CED63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 125 | 200 | 3
SE&A ITST2006059 | D | ICB | Siemens | ED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 40 | 104 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 125 | 240 | 3
SE&A ITST2006060 | D | ICB | Siemens | CED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 40 | 104 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 125 | 240 | 3
SE&A ITST2006061 | D | ICB | Siemens | ED63A | - | - | See Below | 480 | 3 | 30 | 480 | 3 | 75 | 96 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 125 | 480 | 3
SE&A ITST2006062 | D | ICB | Siemens | CED63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 75 | 96 | 2.08 | 1(2.08), 5 | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 125 | 480 | 3
SE&A ITST2006063 | D | ICB | Siemens | ED63A | - | - | See Below | 600 | 3 | 18 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 100 | 600 | 3
SE&A ITST2006064 | D | ICB | Siemens | CED63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 100 | 600 | 3
SE&A ITST2006065 | D | ICB | Siemens | FXD63A | - | - | See Below | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 150 | 600 | 3
SE&A ITST2006066 | D | ICB | Siemens | CFD63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 150 | 600 | 3
SE&A ITST2006067 | D | ICB | Siemens | FXD63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 40 | 120 | 2.78 | 1(2.78), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 150 | 200 | 3
SE&A ITST2006068 | D | ICB | Siemens | CFD63A | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 40 | 120 | 2.78 | 1(2.78), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 150 | 200 | 3
SE&A ITST2006069 | D | ICB | Siemens | ED63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 50 | 130 | 2.78 | 1(2.78), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 150 | 340 | 3
SE&A ITST2006070 | D | ICB | Siemens | FXD63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 50 | 130 | 2.78 | 1(2.78), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 150 | 240 | 3
SE&A ITST2006071 | D | ICB | Siemens | CFD63A | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 50 | 130 | 2.78 | 1(2.78), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 150 | 240 | 3
SE&A ITST2006072 | D | ICB | Siemens | FXD63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 100 | 124 | 2.78 | 1(2.78), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 150 | 480 | 3
|  |  | Siemens | [5 empty] | 3
SE&A ITST2006073 | D | ICB | Siemens | CFD63A | - | - | See Below | 480 | 3 | 100 | 480 | 3 | 100 | 124 | 2.78 | 1(2.78), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 150 | 480 | 3
SE&A ITST2006074 | D | ICB | Siemens | ED63A | - | - | See Below | 600 | 3 | 18 | 600 | 3 | 100 | 99 | 2.78 | 1(2.78), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 125 | 600 | 3
SE&A ITST2006075 | D | ICB | Siemens | CED63A | - | - | See Below | 600 | 3 | 42 | 600 | 3 | 100 | 99 | 2.78 | 1(2.78), 5 | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 125 | 600 | 3
SE&A ITST2006076 | D | ICB | Siemens | JXD63H | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 75 | 221 | 4.16 | 1(4.16), 5 | E43399 Vol. 1 Sec. 6 | 7188.48
|  | STR | Siemens | 14LPU32A | 10 | 55 - 250 | 400 | 200 | 3
SE&A ITST2006077 | D | ICB | Siemens | JXD63H | - | - | See Below | 240 | 3 | 100 | 240 | 3 | 100 | 248 | 4.16 | 1(4.16), 5 | E43399 Vol. 1 Sec. 6 | 7188.48
|  | STR | Siemens | 14LPU32A | 10 | 55 - 250 | 400 | 240 | 3
SE&A ITST2006078 | D | ICB | Siemens | JXD63H | - | - | See Below | 480 | 3 | 35 | 480 | 3 | 200 | 240 | 4.16 | 1(4.16), 5 | E43399 Vol. 1 Sec. 6 | 7188.48
|  | STR | Siemens | 14LPU32A | 10 | 55 - 250 | 400 | 480 | 3
|  |  | Siemens | [5 empty] | 3
SE&A ITST2006079 | D | ICB | Siemens | JXD63H | - | - | See Below | 600 | 3 | 25 | 600 | 3 | 200 | 192 | 4.16 | 1(4.16), 5 | E43399 Vol. 1 Sec. 6 | 7188.48
|  | STR | Siemens | 14LPU32A | 10 | 55 - 250 | 400 | 600 | 3
SE&A ITST2006080 | D | ICB | Siemens | LXD63H | - | - | See Below | 600 | 3 | 25 | 600 | 3 | 400 | 382 | 5.55 | 1(5.55), 5 | E43399 Vol. 1 Sec. 6 | 9590.4
|  | STR | Siemens | 14MPX32A | 18 | 200 - 540 | 600 | 600 | 3

## T.M. C.B.-Contactor&O.L.Relay
Certification of combinations of components in combination motor controllers for use in industrial control panels | [17 empty] | Last Revised: 2024-03-06
NOTE A: For Combinations using current transformers, the current transformer must be provided as specified on the installation instructions for the overload relay.
ID Number | Combination Type | Individual Component | [7 empty] | Combination SCCR | [6 empty] | Combination UL File | Enclosure Vol. (cu in)
|  | Type | Manufacturer | Catalog Designation | Ratings |  |  |  |  | kA | Volts | Ph | Maximum HP | Maximum NEC FLC | Minimum Enclosure Volume (cu ft) | Conditions of Acceptability
[5 empty] | kA | Contactor Rating or Overload Relay Current Rating | Circuit Breaker Current Rating | Volts | Poles
SE&A CTR2006001 | C | CB | Siemens | ED63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 200 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 200 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 200 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 200 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 15 | 200 | 3
SE&A CTR2006002 | C | CB | Siemens | HHED63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 200 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 200 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 200 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 200 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 15 | 200 | 3
SE&A CTR2006003 | C | CB | Siemens | CED63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 200 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 200 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 200 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 200 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 15 | 200 | 3
SE&A CTR2006004 | C | CB | Siemens | ED63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 1.5 | 6 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 15 | 240 | 3
SE&A CTR2006005 | C | CB | Siemens | HHED63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 1.5 | 6 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 15 | 240 | 3
SE&A CTR2006006 | C | CB | Siemens | CED63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 1.5 | 6 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 15 | 240 | 3
SE&A CTR2006007 | C | CB | Siemens | ED63B | 25 | - | See Below | 480 | 3 | 25 | 480 | 3 | 2 | 3.4 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 480 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 480 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 480 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 480 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 15 | 480 | 3
SE&A CTR2006008 | C | CB | Siemens | HHED63B | 65 | - | See Below | 480 | 3 | 65 | 480 | 3 | 2 | 3.4 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 480 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 480 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 480 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 480 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 15 | 480 | 3
SE&A CTR2006009 | C | CB | Siemens | CED63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 2 | 3.4 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 480 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 480 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 480 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 480 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 15 | 480 | 3
SE&A CTR2006010 | C | CB | Siemens | ED63B | 18 | - | See Below | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 600 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 600 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 600 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 600 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 15 | 600 | 3
SE&A CTR2006011 | C | CB | Siemens | HHED63B | 25 | - | See Below | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 600 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 600 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 600 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 600 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 15 | 600 | 3
SE&A CTR2006012 | C | CB | Siemens | CED63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40BP32A | 5 | 10 | - | 600 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 600 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 600 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 600 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 15 | 600 | 3
SE&A CTR2006013 | C | CB | Siemens | ED63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 3 | 11 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 200 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 200 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 200 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 20 | 200 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 20 | 200 | 3
SE&A CTR2006014 | C | CB | Siemens | HHED63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 200 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 200 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 200 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 20 | 200 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 20 | 200 | 3
SE&A CTR2006015 | C | CB | Siemens | CED63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 200 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 200 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 200 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 20 | 200 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 20 | 200 | 3
SE&A CTR2006016 | C | CB | Siemens | ED63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 3 | 9.6 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 20 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 20 | 240 | 3
SE&A CTR2006017 | C | CB | Siemens | HHED63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 3 | 9.6 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 20 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 20 | 240 | 3
SE&A CTR2006018 | C | CB | Siemens | CED63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 3 | 9.6 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 20 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 20 | 240 | 3
SE&A CTR2006019 | C | CB | Siemens | ED63B | 25 | - | See Below | 480 | 3 | 25 | 480 | 3 | 5 | 7.6 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 480 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 480 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 480 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 20 | 480 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 20 | 480 | 3
SE&A CTR2006020 | C | CB | Siemens | HHED63B | 65 | - | See Below | 480 | 3 | 65 | 480 | 3 | 5 | 7.6 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 480 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 480 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 480 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 20 | 480 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 20 | 480 | 3
SE&A CTR2006021 | C | CB | Siemens | CED63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 5 | 7.6 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 480 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 480 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 480 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 20 | 480 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 20 | 480 | 3
SE&A CTR2006022 | C | CB | Siemens | ED63B | 18 | - | See Below | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 600 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 600 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 600 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 600 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 15 | 600 | 3
SE&A CTR2006023 | C | CB | Siemens | HHED63B | 25 | - | See Below | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 600 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 600 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 600 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 600 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 15 | 600 | 3
SE&A CTR2006024 | C | CB | Siemens | CED63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40CP32A | 5 | 20 | - | 600 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 600 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 600 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 600 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 15 | 600 | 3
SE&A CTR2006025 | C | CB | Siemens | ED63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 200 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 200 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 200 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 200 | 3
|  |  |  | 48ARF, 48ASF | 5 | 13 - 27 | 50 | 200 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 50 | 200 | 3
SE&A CTR2006026 | C | CB | Siemens | HHED63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 200 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 200 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 200 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 200 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 50 | 200 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 50 | 200 | 3
SE&A CTR2006027 | C | CB | Siemens | CED63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 200 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 200 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 200 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 200 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 50 | 200 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 50 | 200 | 3
SE&A CTR2006028 | C | CB | Siemens | ED63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 7.5 | 22 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 240 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 50 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 50 | 240 | 3
SE&A CTR2006029 | C | CB | Siemens | HHED63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 7.5 | 22 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 240 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 50 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 50 | 240 | 3
SE&A CTR2006030 | C | CB | Siemens | CED63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 7.5 | 22 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 240 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 240 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 240 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 240 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 50 | 240 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 50 | 240 | 3
SE&A CTR2006031 | C | CB | Siemens | ED63B | 25 | - | See Below | 480 | 3 | 25 | 480 | 3 | 10 | 14 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 480 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 480 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 480 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 480 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 50 | 480 | 3
SE&A CTR2006032 | C | CB | Siemens | HHED63B | 65 | - | See Below | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 480 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 480 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 480 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 480 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 50 | 480 | 3
SE&A CTR2006033 | C | CB | Siemens | CED63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 10 | 14 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 480 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 480 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 480 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 480 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 50 | 480 | 3
SE&A CTR2006034 | C | CB | Siemens | ED63B | 18 | - | See Below | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 600 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 600 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 600 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 600 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 20 | 600 | 3
SE&A CTR2006035 | C | CB | Siemens | HHED63B | 25 | - | See Below | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 600 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 600 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 600 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 600 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 20 | 600 | 3
SE&A CTR2006036 | C | CB | Siemens | CED63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 0.694 | 1(0.69), 3 (For 48DC3) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | MC | Siemens | 40DP32A | 5 | 30 | - | 600 | 3
|  | OLR | Siemens | 48ARA, 48ASA | 5 | .25 - 1 | 15 | 600 | 3
|  | OLR | Siemens | 48ARB, 48ASB | 5 | .75 -3 | 15 | 600 | 3
|  | OLR | Siemens | 48ARD, 48ASD | 5 | 2.5 -10 | 15 | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 5 - 16 | 15 | 600 | 3
|  | OLR | Siemens | 48DC3 | 5 | 30 | 20 | 600 | 3
SE&A CTR2006037 | C | CB | Siemens | ED63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38), 3 (For 48EC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 200 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 200 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 200 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 50 | 200 | 3
SE&A CTR2006038 | C | CB | Siemens | HHED63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38), 3 (For 48EC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 200 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 200 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 200 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 50 | 200 | 3
SE&A CTR2006039 | C | CB | Siemens | CED63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38), 3 (For 48EC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 200 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 200 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 200 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 50 | 200 | 3
SE&A CTR2006040 | C | CB | Siemens | ED63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 10 | 28 | 1.38 | 1(1.38), 3 (For 48EC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 240 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 240 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 240 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 50 | 240 | 3
SE&A CTR2006041 | C | CB | Siemens | HHED63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 10 | 28 | 1.38 | 1(1.38), 3 (For 48EC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 240 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 240 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 240 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 50 | 240 | 3
SE&A CTR2006042 | C | CB | Siemens | CED63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 10 | 28 | 1.38 | 1(1.38), 3 (For 48EC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 240 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 240 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 240 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 50 | 240 | 3
SE&A CTR2006043 | C | CB | Siemens | ED63B | 25 | - | See Below | 480 | 3 | 25 | 480 | 3 | 15 | 21 | 1.38 | 1(1.38), 3 (For 48EC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 480 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 480 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 480 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 50 | 480 | 3
SE&A CTR2006044 | C | CB | Siemens | HHED63B | 65 | - | See Below | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 1.38 | 1(1.38), 3 (For 48EC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 480 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 480 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 480 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 50 | 480 | 3
SE&A CTR2006045 | C | CB | Siemens | CED63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 15 | 21 | 1.38 | 1(1.38), 3 (For 48EC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 480 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 480 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 480 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 50 | 480 | 3
SE&A CTR2006046 | C | CB | Siemens | ED63B | 18 | - | See Below | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1.38 | 1(1.38), 3 (For 48EC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 600 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 600 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 30 | 600 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 30 | 600 | 3
SE&A CTR2006047 | C | CB | Siemens | HHED63B | 25 | - | See Below | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1.38 | 1(1.38), 3 (For 48EC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 600 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 600 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 600 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 30 | 600 | 3
SE&A CTR2006048 | C | CB | Siemens | CED63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1.38 | 1(1.38), 3 (For 48EC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40EP32A | 5 | 40 | - | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 600 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 600 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 30 | 600 | 3
|  | OLR | Siemens | 48EC3 | 5 | 45 | 30 | 600 | 3
SE&A CTR2006049 | C | CB | Siemens | ED63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 200 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 200 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 90 | 200 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 90 | 200 | 3
SE&A CTR2006050 | C | CB | Siemens | HHED63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 200 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 200 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 90 | 200 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 90 | 200 | 3
SE&A CTR2006051 | C | CB | Siemens | CED63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 200 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 200 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 200 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 90 | 200 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 90 | 200 | 3
SE&A CTR2006052 | C | CB | Siemens | ED63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 15 | 42 | 1.38 | 1(1.38), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 240 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 240 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 90 | 240 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 90 | 240 | 3
SE&A CTR2006053 | C | CB | Siemens | HHED63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 15 | 42 | 1.38 | 1(1.38), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 240 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 240 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 90 | 240 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 90 | 240 | 3
SE&A CTR2006054 | C | CB | Siemens | CED63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 15 | 42 | 1.38 | 1(1.38), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 240 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 240 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 240 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 90 | 240 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 90 | 240 | 3
SE&A CTR2006055 | C | CB | Siemens | ED63B | 25 | - | See Below | 480 | 3 | 25 | 480 | 3 | 25 | 34 | 1.38 | 1(1.38), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 480 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 480 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 90 | 480 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 90 | 480 | 3
SE&A CTR2006056 | C | CB | Siemens | HHED63B | 200 | - | See Below | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1.38 | 1(1.38), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 480 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 480 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 90 | 480 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 90 | 480 | 3
SE&A CTR2006057 | C | CB | Siemens | CED63B | 65 | - | See Below | 480 | 3 | 100 | 480 | 3 | 25 | 34 | 1.38 | 1(1.38), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 480 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 480 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 480 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 90 | 480 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 90 | 480 | 3
SE&A CTR2006058 | C | CB | Siemens | ED63B | 18 | - | See Below | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1.38 | 1(1.38), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 600 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 600 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 50 | 600 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 50 | 600 | 3
SE&A CTR2006059 | C | CB | Siemens | HHED63B | 25 | - | See Below | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1.38 | 1(1.38), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 600 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 600 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 50 | 600 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 50 | 600 | 3
SE&A CTR2006060 | C | CB | Siemens | CED63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1.38 | 1, 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | MC | Siemens | 40FP32A | 5 | 50 | - | 600 | 3
|  | OLR | Siemens | 48ARE, 48ASE | 5 | 9 - 18 | 20 | 600 | 3
|  | OLR | Siemens | 48ARF, 48ASF | 5 | 13 - 27 | 30 | 600 | 3
|  | OLR | Siemens | 48ARG, 48ASG | 5 | 20 - 40 | 40 | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22 - 45 | 50 | 600 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 50 | 600 | 3
SE&A CTR2006061 | C | CB | Siemens | ED63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 15 | 48.3 | 2.08 | 1(2.08), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 200 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 30 | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 200 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 200 | 3
SE&A CTR2006062 | C | CB | Siemens | HHED63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2.08 | 1(2.08), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 200 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 30 | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 200 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 200 | 3
SE&A CTR2006063 | C | CB | Siemens | CED63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2.08 | 1(2.08), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 200 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 30 | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 200 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 200 | 3
SE&A CTR2006064 | C | CB | Siemens | ED63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 20 | 54 | 2.08 | 1(2.08), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 240 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 30 | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 240 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 240 | 3
SE&A CTR2006065 | C | CB | Siemens | HHED63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 20 | 54 | 2.08 | 1(2.08), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 240 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 30 | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 240 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 240 | 3
SE&A CTR2006066 | C | CB | Siemens | CED63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 20 | 54 | 2.08 | 1(2.08), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 240 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 30 | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 240 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 240 | 3
SE&A CTR2006067 | C | CB | Siemens | ED63B | 25 | - | See Below | 480 | 3 | 25 | 480 | 3 | 30 | 40 | 2.08 | 1(2.08), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 480 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 30 | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 480 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 480 | 3
SE&A CTR2006068 | C | CB | Siemens | HHED63B | 65 | - | See Below | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 2.08 | 1(2.08), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 480 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 30 | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 480 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 480 | 3
SE&A CTR2006069 | C | CB | Siemens | CED63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 30 | 40 | 2.08 | 1(2.08), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 480 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 30 | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 480 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 100 | 480 | 3
SE&A CTR2006070 | C | CB | Siemens | ED63B | 18 | - | See Below | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2.08 | 1(2.08), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 600 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 30 | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 70 | 600 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 70 | 600 | 3
SE&A CTR2006071 | C | CB | Siemens | HHED63B | 25 | - | See Below | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2.08 | 1(2.08), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 600 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 30 | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 70 | 600 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 70 | 600 | 3
SE&A CTR2006072 | C | CB | Siemens | CED63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2.08 | 1(2.08), 3 (For 48GC3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40GP32A | 5 | 65 | - | 600 | 3
|  | OLR | Siemens | 48BRF, 48BSF | 5 | 13 - 27 | 30 | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 70 | 600 | 3
|  | OLR | Siemens | 48GC3 | 5 | 60 | 70 | 600 | 3
SE&A CTR2006073 | C | CB | Siemens | ED63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 20 | 62.1 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 200 | 3
SE&A CTR2006074 | C | CB | Siemens | HHED63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 200 | 3
SE&A CTR2006075 | C | CB | Siemens | CED63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 200 | 3
SE&A CTR2006076 | C | CB | Siemens | FD63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 20 | 62.1 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 150 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 200 | 3
SE&A CTR2006077 | C | CB | Siemens | HFD63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 150 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 200 | 3
SE&A CTR2006078 | C | CB | Siemens | HHFD63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 150 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 200 | 3
SE&A CTR2006079 | C | CB | Siemens | CFD63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 150 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 200 | 3
SE&A CTR2006080 | C | CB | Siemens | ED63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 25 | 68 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 240 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 240 | 3
SE&A CTR2006081 | C | CB | Siemens | HHED63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 240 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 240 | 3
SE&A CTR2006082 | C | CB | Siemens | CED63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 240 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 240 | 3
SE&A CTR2006083 | C | CB | Siemens | FD63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 25 | 68 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 240 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 240 | 3
SE&A CTR2006084 | C | CB | Siemens | HFD63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 240 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 240 | 3
SE&A CTR2006085 | C | CB | Siemens | HHFD63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 240 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 240 | 3
SE&A CTR2006086 | C | CB | Siemens | CFD63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 240 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 240 | 3
SE&A CTR2006087 | C | CB | Siemens | ED63B | 25 | - | See Below | 480 | 3 | 25 | 480 | 3 | 50 | 65 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 480 | 3
SE&A CTR2006088 | C | CB | Siemens | HHED63B | 65 | - | See Below | 480 | 3 | 65 | 480 | 3 | 50 | 65 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 480 | 3
SE&A CTR2006089 | C | CB | Siemens | CED63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 50 | 65 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 125 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 480 | 3
SE&A CTR2006090 | C | CB | Siemens | FD63B | 35 | - | See Below | 480 | 3 | 35 | 480 | 3 | 50 | 65 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 150 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 480 | 3
SE&A CTR2006091 | C | CB | Siemens | HFD63B | 65 | - | See Below | 480 | 3 | 65 | 480 | 3 | 50 | 65 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 150 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 480 | 3
SE&A CTR2006092 | C | CB | Siemens | HHFD63B | 100 | - | See Below | 480 | 3 | 100 | 480 | 3 | 50 | 65 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 150 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 480 | 3
SE&A CTR2006093 | C | CB | Siemens | CFD63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 50 | 65 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 150 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 480 | 3
SE&A CTR2006094 | C | CB | Siemens | ED63B | 18 | - | See Below | 600 | 3 | 18 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 100 | 600 | 3
SE&A CTR2006095 | C | CB | Siemens | HHED63B | 25 | - | See Below | 600 | 3 | 18 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 100 | 600 | 3
SE&A CTR2006096 | C | CB | Siemens | CED63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 100 | 600 | 3
SE&A CTR2006097 | C | CB | Siemens | FD63B | 18 | - | See Below | 600 | 3 | 22 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 100 | 600 | 3
SE&A CTR2006098 | C | CB | Siemens | HFD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 100 | 600 | 3
SE&A CTR2006099 | C | CB | Siemens | HHFD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 100 | 600 | 3
SE&A CTR2006100 | C | CB | Siemens | CFD63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40HP32A | 10 | 100 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 100 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 100 | 600 | 3
SE&A CTR2006101 | C | CB | Siemens | ED63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 30 | 92 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 200 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 200 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 200 | 3
SE&A CTR2006102 | C | CB | Siemens | HHED63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 200 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 200 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 200 | 3
SE&A CTR2006103 | C | CB | Siemens | CED63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 200 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 200 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 200 | 3
SE&A CTR2006104 | C | CB | Siemens | FD63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 30 | 92 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 200 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 200 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 200 | 3
SE&A CTR2006105 | C | CB | Siemens | HFD63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 200 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 200 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 200 | 3
SE&A CTR2006106 | C | CB | Siemens | HHFD63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 200 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 200 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 200 | 3
SE&A CTR2006107 | C | CB | Siemens | CFD63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 200 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 200 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 200 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 200 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 200 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 200 | 3
SE&A CTR2006108 | C | CB | Siemens | FD63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 40 | 104 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 240 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 240 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 240 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 240 | 3
SE&A CTR2006109 | C | CB | Siemens | HFD63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 40 | 104 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 240 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 240 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 240 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 240 | 3
SE&A CTR2006110 | C | CB | Siemens | HHFD63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 40 | 104 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 240 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 240 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 240 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 240 | 3
SE&A CTR2006111 | C | CB | Siemens | CFD63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 40 | 104 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 240 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 240 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 240 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 240 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 240 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 240 | 3
SE&A CTR2006112 | C | CB | Siemens | ED63B | 25 | - | See Below | 480 | 3 | 25 | 480 | 3 | 75 | 96 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 480 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 480 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 480 | 3
SE&A CTR2006113 | C | CB | Siemens | HHED63B | 65 | - | See Below | 480 | 3 | 100 | 480 | 3 | 75 | 96 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 480 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 480 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 480 | 3
SE&A CTR2006114 | C | CB | Siemens | CED63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 75 | 96 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 480 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 480 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 480 | 3
SE&A CTR2006115 | C | CB | Siemens | FD63B | 35 | - | See Below | 480 | 3 | 35 | 480 | 3 | 75 | 96 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 480 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 480 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 480 | 3
SE&A CTR2006116 | C | CB | Siemens | HFD63B | 65 | - | See Below | 480 | 3 | 65 | 480 | 3 | 75 | 96 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 480 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 480 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 480 | 3
SE&A CTR2006117 | C | CB | Siemens | HHFD63B | 100 | - | See Below | 480 | 3 | 100 | 480 | 3 | 75 | 96 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 480 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 480 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 480 | 3
SE&A CTR2006118 | C | CB | Siemens | CFD63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 75 | 96 | 2.08 | 1(2.08), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 480 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 480 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 480 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 480 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 480 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 480 | 3
SE&A CTR2006119 | C | CB | Siemens | ED63B | 18 | - | See Below | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 600 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 600 | 3
SE&A CTR2006120 | C | CB | Siemens | HHED63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 600 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 600 | 3
SE&A CTR2006121 | C | CB | Siemens | CED63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 600 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 125 | 600 | 3
SE&A CTR2006122 | C | CB | Siemens | FD63B | 18 | - | See Below | 600 | 3 | 22 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 600 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 600 | 3
SE&A CTR2006123 | C | CB | Siemens | HFD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 600 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 600 | 3
SE&A CTR2006124 | C | CB | Siemens | HHFD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 600 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 600 | 3
SE&A CTR2006125 | C | CB | Siemens | CFD63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78), 3 (For 48HA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40IP32A | 10 | 125 | - | 600 | 3
|  | OLR | Siemens | 48BRH, 48BSH | 5 | 22- 45 | 50 | 600 | 3
|  | OLR | Siemens | 48BRJ, 48BSJ | 5 | 30 - 60 | 60 | 600 | 3
|  | OLR | Siemens | 48BRK, 48BSK | 5 | 45 - 90 | 100 | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 150 | 600 | 3
|  | OLR | Siemens | 48HA3 | 5 | 100 | 150 | 600 | 3
SE&A CTR2006126 | C | CB | Siemens | FD63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 40 | 120 | 2.78 | 1(2.78), 3 (For 48JA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 200 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 200 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 250 | 200 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 250 | 200 | 3
SE&A CTR2006127 | C | CB | Siemens | HFD63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 40 | 120 | 2.78 | 1(2.78), 3 (For 48JA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 200 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 200 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 250 | 200 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 250 | 200 | 3
SE&A CTR2006128 | C | CB | Siemens | HHFD63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 40 | 120 | 2.78 | 1(2.78), 3 (For 48JA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 200 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 200 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 250 | 200 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 250 | 200 | 3
SE&A CTR2006129 | C | CB | Siemens | CFD63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 40 | 120 | 2.78 | 1(2.78), 3 (For 48JA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 200 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 200 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 250 | 200 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 250 | 200 | 3
SE&A CTR2006130 | C | CB | Siemens | FD63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 50 | 130 | 2.78 | 1(2.78), 3 (For 48JA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 240 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 240 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 250 | 240 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 250 | 240 | 3
SE&A CTR2006131 | C | CB | Siemens | HFD63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 50 | 130 | 2.78 | 1(2.78), 3 (For 48JA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 240 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 240 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 250 | 240 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 250 | 240 | 3
SE&A CTR2006132 | C | CB | Siemens | HHFD63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 50 | 130 | 2.78 | 1(2.78), 3 (For 48JA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 240 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 240 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 250 | 240 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 250 | 240 | 3
SE&A CTR2006133 | C | CB | Siemens | CFD63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 50 | 130 | 2.78 | 1(2.78), 3 (For 48JA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 240 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 240 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 250 | 240 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 250 | 240 | 3
SE&A CTR2006134 | C | CB | Siemens | FD63B | 35 | - | See Below | 480 | 3 | 35 | 480 | 3 | 100 | 124 | 2.78 | 1(2.78), 3 (For 48JA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 480 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 480 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 250 | 480 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 250 | 480 | 3
SE&A CTR2006135 | C | CB | Siemens | HFD63B | 65 | - | See Below | 480 | 3 | 65 | 480 | 3 | 100 | 124 | 2.78 | 1(2.78), 3 (For 48JA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 480 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 480 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 250 | 480 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 250 | 480 | 3
SE&A CTR2006136 | C | CB | Siemens | HHFD63B | 100 | - | See Below | 480 | 3 | 100 | 480 | 3 | 100 | 124 | 2.78 | 1(2.78), 3 (For 48JA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 480 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 480 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 250 | 480 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 250 | 480 | 3
SE&A CTR2006137 | C | CB | Siemens | CFD63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 100 | 124 | 2.78 | 1(2.78), 3 (For 48JA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 480 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 480 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 250 | 480 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 250 | 480 | 3
SE&A CTR2006138 | C | CB | Siemens | FD63B | 18 | - | See Below | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 2.78 | 1(2.78), 3 (For 48JA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 600 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 150 | 600 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 150 | 600 | 3
SE&A CTR2006139 | C | CB | Siemens | HFD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 2.78 | 1(2.78), 3 (For 48JA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 600 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 150 | 600 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 150 | 600 | 3
SE&A CTR2006140 | C | CB | Siemens | HHFD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 2.78 | 1(2.78), 3 (For 48JA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 600 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 150 | 600 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 150 | 600 | 3
SE&A CTR2006141 | C | CB | Siemens | CFD63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 2.78 | 1(2.78), 3 (For 48JA3) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | MC | Siemens | 40JG32A | 10 | 135 | - | 600 | 3
|  | OLR | Siemens | 48BRL, 48BSL | 5 | 57 - 115 | 125 | 600 | 3
|  | OLR | Siemens | 48BRM, 48BSM | 5 | 67 - 135 | 150 | 600 | 3
|  | OLR | Siemens | 48JA3 | 5 | 180 | 150 | 600 | 3
SE&A CTR2006142 | C | CB | Siemens | JD63B | 65 | - | See Below | 200 | 3 | 100 | 200 | 3 | 75 | 221 | 4.16 | 1(4.16), See Also Note A | E43399 Vol. 1 Sec. 6 | 7188.48
|  | MC | Siemens | 40LP32A | 10 | 270 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 400 | 200 | 3
SE&A CTR2006143 | C | CB | Siemens | JD63B | 65 | - | See Below | 240 | 3 | 100 | 240 | 3 | 100 | 248 | 4.16 | 1(4.16), See Also Note A | E43399 Vol. 1 Sec. 6 | 7188.48
|  | MC | Siemens | 40LP32A | 10 | 270 | - | 240 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 400 | 240 | 3
SE&A CTR2006144 | C | CB | Siemens | JD63B | 35 | - | See Below | 480 | 3 | 50 | 480 | 3 | 200 | 240 | 4.16 | 1(4.16), See Also Note A | E43399 Vol. 1 Sec. 6 | 7188.48
|  | MC | Siemens | 40LP32A | 10 | 270 | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 400 | 480 | 3
SE&A CTR2006145 | C | CB | Siemens | CFD63B | 18 | - | See Below | 600 | 3 | 42 | 600 | 3 | 200 | 192 | 4.16 | 1(4.16), See Also Note A | E43399 Vol. 1 Sec. 6 | 7188.48
|  | MC | Siemens | 40LP32A | 10 | 270 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 250 | 600 | 3
SE&A CTR2006146 | C | CB | Siemens | JD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 200 | 192 | 4.16 | 1(4.16), See Also Note A | E43399 Vol. 1 Sec. 6 | 7188.48
|  | MC | Siemens | 40LP32A | 10 | 270 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 400 | 600 | 3
SE&A CTR2006147 | C | CB | Siemens | LD63B | 65 | - | See Below | 200 | 3 | 100 | 200 | 3 | 150 | 414 | 5.55 | 1(5.55), See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 40MP32A | 18 | 540 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 200 | 3
SE&A CTR2006148 | C | CB | Siemens | MD63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 150 | 414 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | MC | Siemens | 40MP32A | 18 | 540 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 800 | 200 | 3
SE&A CTR2006150 | C | CB | Siemens | LD63B | 65 | - | See Below | 240 | 3 | 100 | 240 | 3 | 200 | 480 | 5.55 | 1(5.55), See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 40MP32A | 18 | 540 | - | 240 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 240 | 3
SE&A CTR2006151 | C | CB | Siemens | MD63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 200 | 480 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | MC | Siemens | 40MP32A | 18 | 540 | - | 240 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 800 | 240 | 3
SE&A CTR2006152 | C | CB | Siemens | LD63B | 35 | - | See Below | 480 | 3 | 50 | 480 | 3 | 400 | 477 | 5.55 | 1(5.55), See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 40MP32A | 18 | na | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 480 | 3
SE&A CTR2006153 | C | CB | Siemens | MD63B | 50 | - | See Below | 480 | 3 | 50 | 480 | 3 | 400 | 477 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | MC | Siemens | 40MP32A | 18 | 540 | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 800 | 480 | 3
SE&A CTR2006154 | C | CB | Siemens | LD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 400 | 382 | 5.55 | 1(5.55), See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 40MP32A | 18 | 540 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | na | 600 | 600 | 3
SE&A CTR2006182 | C | CB | Siemens | JD63B | 65 | - | See Below | 200 | 3 | 100 | 200 | 3 | 60 | 177 | 2.08 | 1(2.08), See Also Note A | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 3RT1056 | 10 | 177 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 250 | 200 | 3
SE&A CTR2006183 | C | CB | Siemens | JD63B | 65 | - | See Below | 208 | 3 | 100 | 208 | 3 | 60 | 169 | 2.08 | 1(2.08), See Also Note A | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 3RT1056 | 10 | 177 | - | 208 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 250 | 208 | 3
SE&A CTR2006184 | C | CB | Siemens | JD63B | 65 | - | See Below | 240 | 3 | 100 | 240 | 3 | 75 | 192 | 2.08 | 1(2.08), See Also Note A | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 3RT1056 | 10 | 192 | - | 240 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 250 | 240 | 3
SE&A CTR2006185 | C | CB | Siemens | JD63B | 35 | - | See Below | 480 | 3 | 50 | 480 | 3 | 150 | 180 | 2.08 | 1(2.08), See Also Note A | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 3RT1056 | 10 | 180 | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 250 | 480 | 3
SE&A CTR2006186 | C | CB | Siemens | JD63B | 35 | - | See Below | 600 | 3 | 25 | 600 | 3 | 200 | 192 | 4.16 | 1(4.16), See Also Note A | E43399 Vol. 1 Sec. 6 | 7188.48
|  | MC | Siemens | 3RT1066 | 14 | 192 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 400 | 600 | 3
SE&A CTR2006187 | C | CB | Siemens | LD63B | 65 | - | See Below | 200 | 3 | 100 | 200 | 3 | 150 | 414 | 5.55 | 1(5.55), See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 3RT1076 | 18 | 414 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 400 | 200 | 3
SE&A CTR2006188 | C | CB | Siemens | MD63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 150 | 414 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | MC | Siemens | 3RT1076 | 18 | 414 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 800 | 200 | 3
SE&A CTR2006189 | C | CB | Siemens | LD63B | 65 | - | See Below | 208 | 3 | 100 | 208 | 3 | 150 | 396 | 5.55 | 1(5.55), See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 3RT1076 | 18 | 414 | - | 208 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 600 | 208 | 3
SE&A CTR2006190 | C | CB | Siemens | MD63B | 65 | - | See Below | 208 | 3 | 65 | 208 | 3 | 150 | 396 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | MC | Siemens | 3RT1076 | 18 | 414 | - | 208 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 800 | 208 | 3
SE&A CTR2006191 | C | CB | Siemens | LD63B | 65 | - | See Below | 240 | 3 | 100 | 240 | 3 | 200 | 480 | 5.55 | 1(5.55), See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 3RT1076 | 18 | 480 | - | 240 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 600 | 240 | 3
SE&A CTR2006192 | C | CB | Siemens | MD63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 200 | 480 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | MC | Siemens | 3RT1076 | 18 | 480 | - | 240 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 800 | 240 | 3
SE&A CTR2006193 | C | CB | Siemens | LD63B | 35 | - | See Below | 480 | 3 | 50 | 480 | 3 | 400 | 477 | 5.55 | 1(5.55), See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 3RT1076 | 18 | 477 | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 600 | 480 | 3
SE&A CTR2006194 | C | CB | Siemens | MD63B | 50 | - | See Below | 480 | 3 | 50 | 480 | 3 | 400 | 477 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | MC | Siemens | 3RT1076 | 18 | 477 | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 800 | 480 | 3
SE&A CTR2006195 | C | CB | Siemens | LD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 400 | 382 | 5.55 | 1(5.55), See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 3RT1076 | 18 | 472 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 600 | 600 | 3
SE&A CTR2006196 | C | CB | Siemens | FXD63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 60 | 177 | 2.08 | 1(2.08), See Also Note A | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 3RT1264 | 18 | 177 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 250 | 200 | 3
SE&A CTR2006197 | C | CB | Siemens | FXD63B | 65 | - | See Below | 208 | 3 | 65 | 208 | 3 | 60 | 169 | 2.08 | 1(2.08), See Also Note A | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 3RT1264 | 18 | 177 | - | 208 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 250 | 208 | 3
SE&A CTR2006198 | C | CB | Siemens | FXD63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 75 | 192 | 2.08 | 1(2.08), See Also Note A | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 3RT1264 | 18 | 192 | - | 240 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 250 | 240 | 3
SE&A CTR2006199 | C | CB | Siemens | FXD63B | 35 | - | See Below | 480 | 3 | 35 | 480 | 3 | 150 | 180 | 2.08 | 1(2.08), See Also Note A | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 3RT1264 | 18 | 180 | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 250 | 480 | 3
SE&A CTR2006200 | C | CB | Siemens | FXD63B | 18 | - | See Below | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 2.08 | 1(2.08), See Also Note A | E43399 Vol. 1 Sec. 6 | 3594.24
|  | MC | Siemens | 3RT1264 | 18 | 192 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 250 | 600 | 3
SE&A CTR2006201 | C | CB | Siemens | JXD63B | 65 | - | See Below | 200 | 3 | 100 | 200 | 3 | 100 | 285 | 5.55 | 1(5.55), See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 3RT1266 | 18 | 285 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 400 | 200 | 3
SE&A CTR2006202 | C | CB | Siemens | JXD63B | 65 | - | See Below | 208 | 3 | 100 | 208 | 3 | 100 | 273 | 5.55 | 1(5.55), See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 3RT1266 | 18 | 285 | - | 208 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 400 | 208 | 3
SE&A CTR2006203 | C | CB | Siemens | JXD63B | 65 | - | See Below | 240 | 3 | 100 | 240 | 3 | 125 | 312 | 5.55 | 1(5.55), See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 3RT1266 | 18 | 312 | - | 240 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 400 | 240 | 3
SE&A CTR2006204 | C | CB | Siemens | JXD63B | 35 | - | See Below | 480 | 3 | 50 | 480 | 3 | 250 | 302 | 5.55 | 1(5.55), See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 3RT1266 | 18 | 302 | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 400 | 480 | 3
SE&A CTR2006205 | C | CB | Siemens | JXD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 300 | 289 | 5.55 | 1(5.55), See Also Note A | E43399 Vol. 1 Sec. 6 | 9590.4
|  | MC | Siemens | 3RT1266 | 18 | 289 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 400 | 600 | 3
SE&A CTR2006206 | C | CB | Siemens | LXD63B | 65 | - | See Below | 200 | 3 | 100 | 200 | 3 | 150 | 414 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | MC | Siemens | 3RT1276 | 18 | 414 | - | 200 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 600 | 200 | 3
SE&A CTR2006207 | C | CB | Siemens | LXD63B | 65 | - | See Below | 208 | 3 | 100 | 208 | 3 | 150 | 396 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | MC | Siemens | 3RT1276 | 18 | 414 | - | 208 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 600 | 208 | 3
SE&A CTR2006208 | C | CB | Siemens | LXD63B | 65 | - | See Below | 240 | 3 | 100 | 240 | 3 | 200 | 480 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | MC | Siemens | 3RT1276 | 18 | 480 | - | 240 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 600 | 240 | 3
SE&A CTR2006209 | C | CB | Siemens | LXD63B | 35 | - | See Below | 480 | 3 | 50 | 480 | 3 | 400 | 477 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | MC | Siemens | 3RT1276 | 18 | 477 | - | 480 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 600 | 480 | 3
SE&A CTR2006210 | C | CB | Siemens | LXD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 500 | 472 | 8.33 | 1(8.33), See Also Note A | E43399 Vol. 1 Sec. 6 | 14394.24
|  | MC | Siemens | 3RT1276 | 18 | 472 | - | 600 | 3
|  | OLR | Siemens | 48CRD, 48CSD, on the output of a Current Transformer. See Note A | 5 | 5 | 600 | 600 | 3

## T.M. C.B.-Starter
Certification of combinations of components in combination motor controllers for use in industrial control panels | [17 empty] | Last Revised: 2024-03-06
ID Number | Combination Type | Individual Component | [7 empty] | Combination SCCR | [6 empty] | Combination UL File | Enclosure Vol. (cu in)
|  | Type | Manufacturer | Catalog Designation | Ratings |  |  |  |  | kA | Volts | Ph | Maximum HP | Maximum NEC FLC | Minimum Enclosure Volume (cu ft) | Conditions of Acceptability
[5 empty] | kA | Overload Relay Current Rating | Circuit Breaker Current Rating | Volts | Poles
SE&A TSTRTR2006001 | C | CB | Siemens | ED63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 15 | 200 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 15 | 200 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 15 | 200 | 3
SE&A TSTRTR2006002 | C | CB | Siemens | HHED63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 15 | 200 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 15 | 200 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 15 | 200 | 3
SE&A TSTRTR2006003 | C | CB | Siemens | CED63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 15 | 200 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 15 | 200 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 15 | 200 | 3
SE&A TSTRTR2006004 | C | CB | Siemens | ED63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 1.5 | 6 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 15 | 240 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 15 | 240 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 15 | 240 | 3
SE&A TSTRTR2006005 | C | CB | Siemens | HHED63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 1.5 | 6 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 15 | 240 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 15 | 240 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 15 | 240 | 3
SE&A TSTRTR2006006 | C | CB | Siemens | CED63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 1.5 | 6 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 15 | 240 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 15 | 240 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 15 | 240 | 3
SE&A TSTRTR2006007 | C | CB | Siemens | ED63B | 25 | - | See Below | 480 | 3 | 25 | 480 | 3 | 2 | 3.4 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 15 | 480 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 15 | 480 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 15 | 480 | 3
SE&A TSTRTR2006008 | C | CB | Siemens | HHED63B | 65 | - | See Below | 480 | 3 | 65 | 480 | 3 | 2 | 3.4 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 15 | 480 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 15 | 480 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 15 | 480 | 3
SE&A TSTRTR2006009 | C | CB | Siemens | CED63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 2 | 3.4 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 15 | 480 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 15 | 480 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 15 | 480 | 3
SE&A TSTRTR2006010 | C | CB | Siemens | ED63B | 18 | - | See Below | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 15 | 600 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 15 | 600 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 15 | 600 | 3
SE&A TSTRTR2006011 | C | CB | Siemens | HHED63B | 25 | - | See Below | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 15 | 600 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 15 | 600 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 15 | 600 | 3
SE&A TSTRTR2006012 | C | CB | Siemens | CED63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14BSA32A | 5 | .25 - 1 | 15 | 600 | 3
|  | STR | Siemens | 14BSB32A | 5 | .75 - 3 | 15 | 600 | 3
|  | STR | Siemens | 14BSD32A | 5 | 2.5 - 10 | 15 | 600 | 3
SE&A TSTRTR2006013 | C | CB | Siemens | ED63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 3 | 11 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 15 | 200 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 15 | 200 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 15 | 200 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 20 | 200 | 3
SE&A TSTRTR2006014 | C | CB | Siemens | HHED63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 15 | 200 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 15 | 200 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 15 | 200 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 20 | 200 | 3
SE&A TSTRTR2006015 | C | CB | Siemens | CED63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 15 | 200 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 15 | 200 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 15 | 200 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 20 | 200 | 3
SE&A TSTRTR2006016 | C | CB | Siemens | ED63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 3 | 9.6 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 15 | 240 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 15 | 240 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 15 | 240 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 20 | 240 | 3
SE&A TSTRTR2006017 | C | CB | Siemens | HHED63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 3 | 9.6 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 15 | 240 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 15 | 240 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 15 | 240 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 20 | 240 | 3
SE&A TSTRTR2006018 | C | CB | Siemens | CED63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 3 | 9.6 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 15 | 240 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 15 | 240 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 15 | 240 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 20 | 240 | 3
SE&A TSTRTR2006019 | C | CB | Siemens | ED63B | 25 | - | See Below | 480 | 3 | 25 | 480 | 3 | 5 | 7.6 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 15 | 480 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 15 | 480 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 15 | 480 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 20 | 480 | 3
SE&A TSTRTR2006020 | C | CB | Siemens | HHED63B | 65 | - | See Below | 480 | 3 | 65 | 480 | 3 | 5 | 7.6 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 15 | 480 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 15 | 480 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 15 | 480 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 20 | 480 | 3
SE&A TSTRTR2006021 | C | CB | Siemens | CED63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 5 | 7.6 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 15 | 480 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 15 | 480 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 15 | 480 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 20 | 480 | 3
SE&A TSTRTR2006022 | C | CB | Siemens | ED63B | 18 | - | See Below | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 15 | 600 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 15 | 600 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 15 | 600 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 20 | 600 | 3
SE&A TSTRTR2006023 | C | CB | Siemens | HHED63B | 25 | - | See Below | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 15 | 600 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 15 | 600 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 15 | 600 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 20 | 600 | 3
SE&A TSTRTR2006024 | C | CB | Siemens | CED63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14CSA32A | 5 | .25 - 1 | 15 | 600 | 3
|  | STR | Siemens | 14CSB32A | 5 | .75 - 3 | 15 | 600 | 3
|  | STR | Siemens | 14CSD32A | 5 | 2.5 - 10 | 15 | 600 | 3
|  | STR | Siemens | 14CSE32A | 5 | 9 - 18 | 20 | 600 | 3
SE&A TSTRTR2006025 | C | CB | Siemens | ED63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 15 | 200 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 15 | 200 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 15 | 200 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 20 | 200 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 50 | 200 | 3
SE&A TSTRTR2006026 | C | CB | Siemens | HED63B | - | - | See Below | 200 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 15 | 200 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 15 | 200 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 15 | 200 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 20 | 200 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 50 | 200 | 3
SE&A TSTRTR2006027 | C | CB | Siemens | HHED63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 15 | 200 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 15 | 200 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 15 | 200 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 20 | 200 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 50 | 200 | 3
SE&A TSTRTR2006028 | C | CB | Siemens | CED63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 15 | 200 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 15 | 200 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 15 | 200 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 20 | 200 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 50 | 200 | 3
SE&A TSTRTR2006029 | C | CB | Siemens | ED63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 7.5 | 22 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 15 | 240 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 15 | 240 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 15 | 240 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 20 | 240 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 50 | 240 | 3
SE&A TSTRTR2006030 | C | CB | Siemens | HHED63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 7.5 | 22 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 15 | 240 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 15 | 240 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 15 | 240 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 20 | 240 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 50 | 240 | 3
SE&A TSTRTR2006031 | C | CB | Siemens | CED63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 7.5 | 22 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 15 | 240 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 15 | 240 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 15 | 240 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 20 | 240 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 50 | 240 | 3
SE&A TSTRTR2006032 | C | CB | Siemens | ED63B | 25 | - | See Below | 480 | 3 | 25 | 480 | 3 | 10 | 14 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 15 | 480 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 15 | 480 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 15 | 480 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 20 | 480 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 30 | 480 | 3
SE&A TSTRTR2006033 | C | CB | Siemens | HHED63B | 65 | - | See Below | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 15 | 480 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 15 | 480 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 15 | 480 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 20 | 480 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 30 | 480 | 3
SE&A TSTRTR2006034 | C | CB | Siemens | CED63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 10 | 14 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 15 | 480 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 15 | 480 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 15 | 480 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 20 | 480 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 30 | 480 | 3
SE&A TSTRTR2006035 | C | CB | Siemens | ED63B | 18 | - | See Below | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 15 | 600 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 15 | 600 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 15 | 600 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 20 | 600 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 20 | 600 | 3
SE&A TSTRTR2006036 | C | CB | Siemens | HHED63B | 25 | - | See Below | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 15 | 600 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 15 | 600 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 15 | 600 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 20 | 600 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 20 | 600 | 3
SE&A TSTRTR2006037 | C | CB | Siemens | CED63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 0.694 | 1(0.69) | E43399 Vol. 1 Sec. 6 | 1199.232
|  | STR | Siemens | 14DSA32A | 5 | .25 - 1 | 15 | 600 | 3
|  | STR | Siemens | 14DSB32A | 5 | .75 - 3 | 15 | 600 | 3
|  | STR | Siemens | 14DSD32A | 5 | 2.5 - 10 | 15 | 600 | 3
|  | STR | Siemens | 14DSE32A | 5 | 9 - 18 | 20 | 600 | 3
|  | STR | Siemens | 14DSF32A | 5 | 13 - 27 | 20 | 600 | 3
SE&A TSTRTR2006038 | C | CB | Siemens | ED63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 30 | 200 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 50 | 200 | 3
SE&A TSTRTR2006039 | C | CB | Siemens | HHED63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 30 | 200 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 50 | 200 | 3
SE&A TSTRTR2006040 | C | CB | Siemens | CED63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 30 | 200 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 50 | 200 | 3
SE&A TSTRTR2006041 | C | CB | Siemens | ED63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 10 | 28 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 30 | 240 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 50 | 240 | 3
SE&A TSTRTR2006042 | C | CB | Siemens | HHED63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 10 | 28 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 30 | 240 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 50 | 240 | 3
SE&A TSTRTR2006043 | C | CB | Siemens | CED63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 10 | 28 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 30 | 240 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 50 | 240 | 3
SE&A TSTRTR2006044 | C | CB | Siemens | ED63B | 25 | - | See Below | 480 | 3 | 25 | 480 | 3 | 15 | 21 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 30 | 480 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 50 | 480 | 3
SE&A TSTRTR2006045 | C | CB | Siemens | HHED63B | 65 | - | See Below | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 30 | 480 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 50 | 480 | 3
SE&A TSTRTR2006046 | C | CB | Siemens | CED63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 15 | 21 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 30 | 480 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 50 | 480 | 3
SE&A TSTRTR2006047 | C | CB | Siemens | ED63B | 18 | - | See Below | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 30 | 600 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 50 | 600 | 3
SE&A TSTRTR2006048 | C | CB | Siemens | HHED63B | 25 | - | See Below | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 30 | 600 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 50 | 600 | 3
SE&A TSTRTR2006049 | C | CB | Siemens | CED63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14ESF32A | 5 | 13 - 27 | 30 | 600 | 3
|  | STR | Siemens | 14ESG32A | 5 | 20 - 40 | 50 | 600 | 3
SE&A TSTRTR2006050 | C | CB | Siemens | ED63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 30 | 200 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 90 | 200 | 3
SE&A TSTRTR2006051 | C | CB | Siemens | HHED63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 30 | 200 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 90 | 200 | 3
SE&A TSTRTR2006052 | C | CB | Siemens | CED63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 30 | 200 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 90 | 200 | 3
SE&A TSTRTR2006053 | C | CB | Siemens | ED63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 15 | 42 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 30 | 240 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 90 | 240 | 3
SE&A TSTRTR2006054 | C | CB | Siemens | HHED63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 15 | 42 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 30 | 240 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 90 | 240 | 3
SE&A TSTRTR2006055 | C | CB | Siemens | CED63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 15 | 42 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 30 | 240 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 90 | 240 | 3
SE&A TSTRTR2006056 | C | CB | Siemens | ED63B | 25 | - | See Below | 480 | 3 | 25 | 480 | 3 | 25 | 34 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 30 | 480 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 90 | 480 | 3
SE&A TSTRTR2006057 | C | CB | Siemens | HHED63B | 200 | - | See Below | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 30 | 480 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 90 | 480 | 3
SE&A TSTRTR2006058 | C | CB | Siemens | CED63B | 65 | - | See Below | 480 | 3 | 100 | 480 | 3 | 25 | 34 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 30 | 480 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 90 | 480 | 3
SE&A TSTRTR2006059 | C | CB | Siemens | ED63B | 18 | - | See Below | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 30 | 600 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 50 | 600 | 3
SE&A TSTRTR2006060 | C | CB | Siemens | HHED63B | 25 | - | See Below | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 30 | 600 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 50 | 600 | 3
SE&A TSTRTR2006061 | C | CB | Siemens | CED63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1.38 | 1(1.38) | E43399 Vol. 1 Sec. 6 | 2384.64
|  | STR | Siemens | 14FSF32A | 5 | 13 - 27 | 30 | 600 | 3
|  | STR | Siemens | 14FSH32A | 5 | 22 - 45 | 50 | 600 | 3
SE&A TSTRTR2006062 | C | CB | Siemens | ED63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 15 | 48.3 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 200 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 200 | 3
SE&A TSTRTR2006063 | C | CB | Siemens | HHED63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 200 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 200 | 3
SE&A TSTRTR2006064 | C | CB | Siemens | CED63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 200 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 200 | 3
SE&A TSTRTR2006065 | C | CB | Siemens | ED63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 20 | 54 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 240 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 240 | 3
SE&A TSTRTR2006066 | C | CB | Siemens | HHED63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 20 | 54 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 240 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 240 | 3
SE&A TSTRTR2006067 | C | CB | Siemens | CED63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 20 | 54 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 240 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 240 | 3
SE&A TSTRTR2006068 | C | CB | Siemens | ED63B | 25 | - | See Below | 480 | 3 | 25 | 480 | 3 | 30 | 40 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 480 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 480 | 3
SE&A TSTRTR2006069 | C | CB | Siemens | HHED63B | 65 | - | See Below | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 480 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 480 | 3
SE&A TSTRTR2006070 | C | CB | Siemens | CED63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 30 | 40 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 480 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 100 | 480 | 3
SE&A TSTRTR2006071 | C | CB | Siemens | ED63B | 18 | - | See Below | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 600 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 70 | 600 | 3
SE&A TSTRTR2006072 | C | CB | Siemens | HHED63B | 25 | - | See Below | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 600 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 70 | 600 | 3
SE&A TSTRTR2006073 | C | CB | Siemens | CED63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14GSH32A | 5 | 22 - 45 | 50 | 600 | 3
|  | STR | Siemens | 14GSJ32A | 5 | 30 - 60 | 70 | 600 | 3
SE&A TSTRTR2006074 | C | CB | Siemens | ED63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 25 | 78.2 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 200 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 125 | 200 | 3
SE&A TSTRTR2006075 | C | CB | Siemens | HHED63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 200 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 125 | 200 | 3
SE&A TSTRTR2006076 | C | CB | Siemens | CED63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 200 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 125 | 200 | 3
SE&A TSTRTR2006077 | C | CB | Siemens | FD63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 20 | 62.1 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 200 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 150 | 200 | 3
SE&A TSTRTR2006078 | C | CB | Siemens | HFD63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 200 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 150 | 200 | 3
SE&A TSTRTR2006079 | C | CB | Siemens | HHFD63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 200 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 150 | 200 | 3
SE&A TSTRTR2006080 | C | CB | Siemens | CFD63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 200 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 150 | 200 | 3
SE&A TSTRTR2006081 | C | CB | Siemens | ED63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 25 | 68 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 240 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 125 | 240 | 3
SE&A TSTRTR2006082 | C | CB | Siemens | HHED63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 240 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 125 | 240 | 3
SE&A TSTRTR2006083 | C | CB | Siemens | CED63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 240 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 125 | 240 | 3
SE&A TSTRTR2006084 | C | CB | Siemens | FD63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 25 | 68 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 240 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 150 | 240 | 3
SE&A TSTRTR2006085 | C | CB | Siemens | HFD63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 240 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 150 | 240 | 3
SE&A TSTRTR2006086 | C | CB | Siemens | HHFD63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 240 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 150 | 240 | 3
SE&A TSTRTR2006087 | C | CB | Siemens | CFD63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 240 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 150 | 240 | 3
SE&A TSTRTR2006088 | C | CB | Siemens | ED63B | 25 | - | See Below | 480 | 3 | 25 | 480 | 3 | 50 | 65 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 480 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 125 | 480 | 3
SE&A TSTRTR2006089 | C | CB | Siemens | HHED63B | 65 | - | See Below | 480 | 3 | 65 | 480 | 3 | 50 | 65 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 480 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 125 | 480 | 3
SE&A TSTRTR2006090 | C | CB | Siemens | CED63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 50 | 65 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 480 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 125 | 480 | 3
SE&A TSTRTR2006091 | C | CB | Siemens | FD63B | 35 | - | See Below | 480 | 3 | 35 | 480 | 3 | 50 | 65 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 480 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 150 | 480 | 3
SE&A TSTRTR2006092 | C | CB | Siemens | HFD63B | 65 | - | See Below | 480 | 3 | 65 | 480 | 3 | 50 | 65 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 480 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 150 | 480 | 3
SE&A TSTRTR2006093 | C | CB | Siemens | HHFD63B | 100 | - | See Below | 480 | 3 | 100 | 480 | 3 | 50 | 65 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 480 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 150 | 480 | 3
SE&A TSTRTR2006094 | C | CB | Siemens | CFD63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 50 | 65 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 480 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 150 | 480 | 3
SE&A TSTRTR2006095 | C | CB | Siemens | ED63B | 18 | - | See Below | 600 | 3 | 18 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 600 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 100 | 600 | 3
SE&A TSTRTR2006096 | C | CB | Siemens | HHED63B | 25 | - | See Below | 600 | 3 | 18 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 600 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 100 | 600 | 3
SE&A TSTRTR2006097 | C | CB | Siemens | CED63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 600 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 100 | 600 | 3
SE&A TSTRTR2006098 | C | CB | Siemens | FD63B | 18 | - | See Below | 600 | 3 | 22 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 600 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 150 | 600 | 3
SE&A TSTRTR2006099 | C | CB | Siemens | HFD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 600 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 150 | 600 | 3
SE&A TSTRTR2006100 | C | CB | Siemens | HHFD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 600 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 150 | 600 | 3
SE&A TSTRTR2006101 | C | CB | Siemens | CFD63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14HSJ32A | 10 | 30 - 60 | 60 | 600 | 3
|  | STR | Siemens | 14HSK32A | 10 | 45 - 90 | 150 | 600 | 3
SE&A TSTRTR2006102 | C | CB | Siemens | ED63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 30 | 92 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 125 | 200 | 3
SE&A TSTRTR2006103 | C | CB | Siemens | HHED63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 125 | 200 | 3
SE&A TSTRTR2006104 | C | CB | Siemens | CED63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 125 | 200 | 3
SE&A TSTRTR2006105 | C | CB | Siemens | FD63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 30 | 92 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 150 | 200 | 3
SE&A TSTRTR2006106 | C | CB | Siemens | HFD63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 150 | 200 | 3
SE&A TSTRTR2006107 | C | CB | Siemens | HHFD63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 150 | 200 | 3
SE&A TSTRTR2006108 | C | CB | Siemens | CFD63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 150 | 200 | 3
SE&A TSTRTR2006109 | C | CB | Siemens | ED63B | 65 | - | See Below | 208 | 3 | 65 | 208 | 3 | 30 | 88 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 150 | 208 | 3
SE&A TSTRTR2006110 | C | CB | Siemens | HHED63B | 100 | - | See Below | 208 | 3 | 100 | 208 | 3 | 30 | 88 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 125 | 208 | 3
SE&A TSTRTR2006111 | C | CB | Siemens | FD63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 40 | 104 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 150 | 240 | 3
SE&A TSTRTR2006112 | C | CB | Siemens | HFD63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 40 | 104 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 150 | 240 | 3
SE&A TSTRTR2006113 | C | CB | Siemens | HHFD63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 40 | 104 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 150 | 240 | 3
SE&A TSTRTR2006114 | C | CB | Siemens | CFD63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 40 | 104 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 150 | 240 | 3
SE&A TSTRTR2006115 | C | CB | Siemens | ED63B | 25 | - | See Below | 480 | 3 | 25 | 480 | 3 | 75 | 96 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 125 | 480 | 3
SE&A TSTRTR2006116 | C | CB | Siemens | HHED63B | 65 | - | See Below | 480 | 3 | 65 | 480 | 3 | 75 | 96 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 125 | 480 | 3
SE&A TSTRTR2006117 | C | CB | Siemens | CED63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 75 | 96 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 125 | 480 | 3
SE&A TSTRTR2006118 | C | CB | Siemens | FD63B | 35 | - | See Below | 480 | 3 | 35 | 480 | 3 | 75 | 96 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 125 | 480 | 3
SE&A TSTRTR2006119 | C | CB | Siemens | HFD63B | 65 | - | See Below | 480 | 3 | 65 | 480 | 3 | 75 | 96 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 150 | 480 | 3
SE&A TSTRTR2006120 | C | CB | Siemens | HHFD63B | 100 | - | See Below | 480 | 3 | 100 | 480 | 3 | 75 | 96 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 150 | 480 | 3
SE&A TSTRTR2006121 | C | CB | Siemens | CFD63B | 200 | - | See Below | 480 | 3 | 100 | 480 | 3 | 75 | 96 | 2.08 | 1(2.08) | E43399 Vol. 1 Sec. 6 | 3594.24
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 150 | 480 | 3
SE&A TSTRTR2006122 | C | CB | Siemens | ED63B | 18 | - | See Below | 600 | 3 | 18 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 125 | 600 | 3
SE&A TSTRTR2006123 | C | CB | Siemens | HHED63B | 25 | - | See Below | 600 | 3 | 18 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 125 | 600 | 3
SE&A TSTRTR2006124 | C | CB | Siemens | CED63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 125 | 600 | 3
SE&A TSTRTR2006125 | C | CB | Siemens | FD63B | 18 | - | See Below | 600 | 3 | 22 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 150 | 600 | 3
SE&A TSTRTR2006126 | C | CB | Siemens | HFD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 150 | 600 | 3
SE&A TSTRTR2006127 | C | CB | Siemens | HHFD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 150 | 600 | 3
SE&A TSTRTR2006128 | C | CB | Siemens | CFD63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14ISL32A | 10 | 57 - 115 | 150 | 600 | 3
SE&A TSTRTR2006129 | C | CB | Siemens | FD63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 40 | 120 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 250 | 200 | 3
SE&A TSTRTR2006130 | C | CB | Siemens | HFD63B | 100 | - | See Below | 200 | 3 | 100 | 200 | 3 | 40 | 120 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 250 | 200 | 3
SE&A TSTRTR2006131 | C | CB | Siemens | HHFD63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 40 | 120 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 250 | 200 | 3
SE&A TSTRTR2006132 | C | CB | Siemens | CFD63B | 200 | - | See Below | 200 | 3 | 100 | 200 | 3 | 40 | 120 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 250 | 200 | 3
SE&A TSTRTR2006133 | C | CB | Siemens | FD63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 50 | 130 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 250 | 240 | 3
SE&A TSTRTR2006134 | C | CB | Siemens | HFD63B | 100 | - | See Below | 240 | 3 | 100 | 240 | 3 | 50 | 130 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 250 | 240 | 3
SE&A TSTRTR2006135 | C | CB | Siemens | HHFD63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 50 | 130 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 250 | 240 | 3
SE&A TSTRTR2006136 | C | CB | Siemens | CFD63B | 200 | - | See Below | 240 | 3 | 100 | 240 | 3 | 50 | 130 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 250 | 240 | 3
SE&A TSTRTR2006137 | C | CB | Siemens | FD63B | 35 | - | See Below | 200 | 3 | 35 | 480 | 3 | 100 | 124 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 250 | 200 | 3
SE&A TSTRTR2006138 | C | CB | Siemens | HFD63B | 65 | - | See Below | 200 | 3 | 65 | 480 | 3 | 100 | 124 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 250 | 200 | 3
SE&A TSTRTR2006139 | C | CB | Siemens | HHFD63B | 100 | - | See Below | 200 | 3 | 100 | 480 | 3 | 100 | 124 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 250 | 200 | 3
SE&A TSTRTR2006140 | C | CB | Siemens | CFD63B | 200 | - | See Below | 200 | 3 | 100 | 480 | 3 | 100 | 124 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 250 | 200 | 3
SE&A TSTRTR2006141 | C | CB | Siemens | FD63B | 18 | - | See Below | 600 | 3 | 18 | 600 | 3 | 100 | 99 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 150 | 600 | 3
SE&A TSTRTR2006142 | C | CB | Siemens | HFD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 150 | 600 | 3
SE&A TSTRTR2006143 | C | CB | Siemens | HHFD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 150 | 600 | 3
SE&A TSTRTR2006144 | C | CB | Siemens | CFD63B | 100 | - | See Below | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 2.78 | 1(2.78) | E43399 Vol. 1 Sec. 6 | 4803.84
|  | STR | Siemens | 14JTM32A | 10 | 67 - 135 | 150 | 600 | 3
SE&A TSTRTR2006145 | C | CB | Siemens | JD63B | 65 | - | See Below | 200 | 3 | 100 | 200 | 3 | 75 | 221 | 4.16 | 1(4.16) | E43399 Vol. 1 Sec. 6 | 7188.48
|  | STR | Siemens | 14LPU32A | 10 | 55 - 250 | 400 | 200 | 3
SE&A TSTRTR2006146 | C | CB | Siemens | JD63B | 65 | - | See Below | 240 | 3 | 100 | 240 | 3 | 100 | 248 | 4.16 | 1(4.16) | E43399 Vol. 1 Sec. 6 | 7188.48
|  | STR | Siemens | 14LPU32A | 10 | 55 - 250 | 400 | 240 | 3
SE&A TSTRTR2006147 | C | CB | Siemens | JD63B | 35 | - | See Below | 480 | 3 | 50 | 480 | 3 | 200 | 240 | 4.16 | 1(4.16) | E43399 Vol. 1 Sec. 6 | 7188.48
|  | STR | Siemens | 14LPU32A | 10 | 55 - 250 | 400 | 480 | 3
SE&A TSTRTR2006148 | C | CB | Siemens | FD63B | 18 | - | See Below | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 4.16 | 1(4.16) | E43399 Vol. 1 Sec. 6 | 7188.48
|  | STR | Siemens | 14LPU32A | 10 | 55 - 250 | 400 | 600 | 3
SE&A TSTRTR2006149 | C | CB | Siemens | JD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 200 | 192 | 4.16 | 1(4.16) | E43399 Vol. 1 Sec. 6 | 7188.48
|  | STR | Siemens | 14LPU32A | 10 | 55 - 250 | 400 | 600 | 3
SE&A TSTRTR2006150 | C | CB | Siemens | LD63B | 65 | - | See Below | 200 | 3 | 100 | 200 | 3 | 150 | 414 | 5.55 | 1(5.55) | E43399 Vol. 1 Sec. 6 | 9590.4
|  | STR | Siemens | 14MPX32A | 18 | 200 - 540 | 600 | 200 | 3
SE&A TSTRTR2006151 | C | CB | Siemens | MD63B | 65 | - | See Below | 200 | 3 | 65 | 200 | 3 | 150 | 414 | 8.33 | 1(8.33) | E43399 Vol. 1 Sec. 6 | 14394.24
|  | STR | Siemens | 14MPX32A | 18 | 200 - 540 | 800 | 200 | 3
SE&A TSTRTR2006152 | C | CB | Siemens | MD63B | 65 | - | See Below | 208 | 3 | 65 | 208 | 3 | 150 | 396 | 8.33 | 1(8.33) | E43399 Vol. 1 Sec. 6 | 14394.24
|  | STR | Siemens | 14MPX32A | 18 | 200 - 540 | 800 | 208 | 3
SE&A TSTRTR2006153 | C | CB | Siemens | LD63B | 65 | - | See Below | 240 | 3 | 100 | 240 | 3 | 200 | 480 | 5.55 | 1(5.55) | E43399 Vol. 1 Sec. 6 | 9590.4
|  | STR | Siemens | 14MPX32A | 18 | 200 - 540 | 600 | 240 | 3
SE&A TSTRTR2006154 | C | CB | Siemens | MD63B | 65 | - | See Below | 240 | 3 | 65 | 240 | 3 | 200 | 480 | 8.33 | 1(8.33) | E43399 Vol. 1 Sec. 6 | 14394.24
|  | STR | Siemens | 14MPX32A | 18 | 200 - 540 | 800 | 240 | 3
SE&A TSTRTR2006155 | C | CB | Siemens | LD63B | 35 | - | See Below | 480 | 3 | 50 | 480 | 3 | 400 | 477 | 5.55 | 1(5.55) | E43399 Vol. 1 Sec. 6 | 9590.4
|  | STR | Siemens | 14MPX32A | 18 | 200 - 540 | 600 | 480 | 3
SE&A TSTRTR2006156 | C | CB | Siemens | MD63B | 50 | - | See Below | 480 | 3 | 50 | 480 | 3 | 400 | 477 | 8.33 | 1(8.33) | E43399 Vol. 1 Sec. 6 | 14394.24
|  | STR | Siemens | 14MPX32A | 18 | 200 - 540 | 800 | 480 | 3
SE&A TSTRTR2006157 | C | CB | Siemens | LD63B | 25 | - | See Below | 600 | 3 | 25 | 600 | 3 | 400 | 382 | 5.55 | 1(5.55) | E43399 Vol. 1 Sec. 6 | 9590.4
|  | STR | Siemens | 14MPX32A | 18 | 200 - 540 | 600 | 600 | 3