## 200V
Issued: 2025-04-30
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Dimension (cu in) | Conditions of Use | File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | HP Rating | Current Rating, FLA or FLA/LRA |  |  | UL File Number | Volume / Section (Vol#).(Sec#)
200 V AC, 3-PHASE
LOVSF00016DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00016DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00016DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00016DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00016DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00025DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00025DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00025DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00025DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00025DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00040DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00040DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00040DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00040DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00040DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00063DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
#REF! | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00063DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00063DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00063DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00063DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00100DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00100DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00100DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00100DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00100DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00160DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00160DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00160DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00160DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00160DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 200 | 3 | 65 | - | - | 200 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00250DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00250DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00250DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00250DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00250DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 200 | 3 | 65 | 2.5 | 1/2 | 200 | 3 | 65 | 1/2 | 2.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00400DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00400DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00400DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00400DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00400DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 200 | 3 | 65 | 3.7 | 3/4 | 200 | 3 | 65 | 3/4 | 3.7 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00650DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF00650DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00650DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00650DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF00650DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 200 | 3 | 65 | 6.9 | 1.5 | 200 | 3 | 65 | 1 1/2 | 6.9 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF09xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF12xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF18xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF09xxL | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF12xxL | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF18xxL | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF09xxD | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF12xxD | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF18xxD | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1000DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 200 | 3 | 65 | 7.8 | 2 | 200 | 3 | 65 | 2 | 7.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF09xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/A | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF09xxL | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/L | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF09xxD | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/D | 200 | 3 | 5 | 11.0 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF12xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF12xxL | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF12xxD | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF18xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF18xxL | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF18xxD | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1400DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 65 | 3 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800DPBF12xxA | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800DPBF12xxL | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800DPBF12xxD | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800DPBF18xxA | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800DPBF18xxL | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800DPBF18xxD | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E1800DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE1800 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 65 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300DPBF12xxA | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300DPBF18xxA | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300DPBF12xxL | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300DPBF18xxL | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300DPBF12xxD | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300DPBF18xxD | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 200 | 3 | 5 | 17.5 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2300DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE2300 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2500DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE2500 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2500DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE2500 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 200 | 3 | 5 | 25.3 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2500DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE2500 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E2500DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE2500 | 200 | 3 | 30 | 17.5 | 5 | 200 | 3 | 30 | 5 | 17.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF0E3200DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE3200 | 200 | 3 | 10 | 32.2 | 10 | 200 | 3 | 10 | 10 | 32.2 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 200 | 3 | 5 | 32.2 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having an ampacity of
125 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor
controllers shall be considered in the end-product application.
|  | 6 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu) No. 14 AWG wire.
|  | 7 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu), for size of conductor see table below.
|  | 8 | Contactor DPBG12xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF09xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF12xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF18xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF26xx - The xx may be replaced with suffix 00 or T4 only.
Contactor DPBF32xx - The xx may be replaced with suffix 00 or T4 only.

## 208V
Issued: 2025-04-30
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Dimension (cu in) | Conditions of Use | File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Hp Rating | Current Rating, FLA or FLA/LRA |  |  | UL File Number | Volume / Section (Vol#).(Sec#)
208 V AC, 3-PHASE
LOVSF10016DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10016DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10016DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10016DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10016DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10025DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10025DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10025DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10025DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10025DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10040DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10040DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10040DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10040DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10040DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10063DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10063DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10063DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10063DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10063DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10100DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10100DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10100DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10100DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10100DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10160DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10160DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10160DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10160DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10160DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 208 | 3 | 65 | - | - | 208 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10250DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - |  | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - |  | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - |  | 439
LOVSF10250DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - |  | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - |  | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - |  | 439
LOVSF10250DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - |  | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - |  | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - |  | 439
LOVSF10250DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - |  | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - |  | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - |  | 439
LOVSF10250DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - |  | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - |  | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - |  | 439
LOVSF10250DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10250DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10250DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10250DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10250DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 208 | 3 | 65 | 2.4 | 1/2 | 208 | 3 | 65 | 1/2 | 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10400DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10400DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10400DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10400DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10400DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 208 | 3 | 65 | 3.5 | 3/4 | 208 | 3 | 65 | 3/4 | 3.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10650DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF10650DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10650DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10650DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF10650DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 208 | 3 | 65 | 6.6 | 1.5 | 208 | 3 | 65 | 1 1/2 | 6.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF09xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF12xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF18xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF09xxL | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF12xxL | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF18xxL | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF09xxD | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF12xxD | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF18xxD | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1000DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 208 | 3 | 65 | 7.5 | 2 | 208 | 3 | 65 | 2 | 7.5 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF09xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/A | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF09xxL | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/L | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF09xxD | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/D | 208 | 3 | 5 | 10.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF12xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF12xxL | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF12xxD | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF18xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF18xxL | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF18xxD | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1400DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 208 | 3 | 65 | 10.6 | 3 | 208 | 3 | 65 | 3 | 10.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800DPBF12xxA | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800DPBF12xxL | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800DPBF12xxD | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800DPBF18xxA | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800DPBF18xxL | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800DPBF18xxD | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E1800DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE1800 | 208 | 3 | 65 | 16.7 | 5 | 208 | 3 | 65 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300DPBF12xxA | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300DPBF18xxA | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300DPBF12xxL | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300DPBF18xxL | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300DPBF12xxD | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300DPBF18xxD | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 208 | 3 | 5 | 16.7 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2300DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE2300 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2500DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE2500 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2500DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE2500 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 208 | 3 | 5 | 24.2 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2500DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE2500 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E2500DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE2500 | 208 | 3 | 30 | 16.7 | 5 | 208 | 3 | 30 | 5 | 16.7 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E3200DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE3200 | 208 | 3 | 10 | 30.8 | 10 | 208 | 3 | 10 | 10 | 30.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF1E3200DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE3200 | 208 | 3 | 10 | 30.8 | 10 | 208 | 3 | 10 | 10 | 30.8 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 208 | 3 | 5 | 30.8 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having an ampacity of
125 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor
controllers shall be considered in the end-product application.
|  | 6 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu) No. 14 AWG wire.
|  | 7 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu), for size of conductor see table below.
|  | 8 | Contactor DPBG12xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF09xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF12xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF18xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF26xx - The xx may be replaced with suffix 00 or T4 only.
Contactor DPBF32xx - The xx may be replaced with suffix 00 or T4 only.

## 240V
Issued: 2025-04-30
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Dimension (cu in) | Conditions of Use | File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Hp Rating | Current Rating, FLA or FLA/LRA |  |  | UL File Number | Volume / Section (Vol#).(Sec#)
240 V AC, 3-PHASE
LOVSF20016DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20016DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20016DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20016DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20016DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20025DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20025DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20025DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20025DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20025DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20040DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20040DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20040DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20040DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20040DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20063DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20063DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20063DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20063DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20063DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20100DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20100DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20100DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20100DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20100DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20160DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1 / 6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - |  | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - |  | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - |  | 439
LOVSF20160DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20160DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20160DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20160DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20160DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 240 | 3 | 65 | - | - | 240 | 3 | 65 | - | 1.6 / 9.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20250DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20250DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20250DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20250DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20250DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 240 | 3 | 65 | 2.2 | 1/2 | 240 | 3 | 65 | 1/2 | 2.2 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20400DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20400DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20400DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20400DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20400DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 240 | 3 | 65 | 3.2 | 3/4 | 240 | 3 | 65 | 3/4 | 3.7 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20650DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF20650DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20650DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20650DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF20650DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 240 | 3 | 65 | 6.0 | 1.5 | 240 | 3 | 65 | 1 1/2 | 6.9 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF09xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF12xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF18xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF09xxL | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF12xxL | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF18xxL | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF09xxD | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF12xxD | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF18xxD | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1000DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF09xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/A | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF09xxL | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/L | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF09xxD | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/D | 240 | 3 | 5 | 9.6 | 3 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF12xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF12xxL | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF12xxD | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF18xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF18xxL | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF18xxD | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1400DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 65 | 3 | 9.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800DPBF12xxA | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800DPBF12xxL | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800DPBF12xxD | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800DPBF18xxA | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800DPBF18xxL | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800DPBF18xxD | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 240 | 3 | 5 | 15.2 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E1800DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE1800 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 65 | 5 | 15.2 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2300DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE2300 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2300DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE2300 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2300DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE2300 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2300DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE2300 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2500DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE2500 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2500DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE2500 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 240 | 3 | 5 | 22.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2500DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE2500 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E2500DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE2500 | 240 | 3 | 30 | 22 | 7.5 | 240 | 3 | 30 | 7 1/2 | 22 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E3200DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE3200 | 240 | 3 | 10 | 28 | 10 | 240 | 3 | 10 | 10 | 28 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF2E3200DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE3200 | 240 | 3 | 10 | 28 | 10 | 240 | 3 | 10 | 10 | 28 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 240 | 3 | 5 | 28.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having an ampacity of
125 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor
controllers shall be considered in the end-product application.
|  | 6 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu) No. 14 AWG wire.
|  | 7 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu), for size of conductor see table below.
|  | 8 | Contactor DPBG12xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF09xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF12xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF18xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF26xx - The xx may be replaced with suffix 00 or T4 only.
Contactor DPBF32xx - The xx may be replaced with suffix 00 or T4 only.

## 480V
Issued: 2025-04-30
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Dimension (cu in) | Conditions of Use | File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Hp Rating | Current Rating, FLA or FLA/LRA |  |  | UL File Number | Volume / Section (Vol#).(Sec#)
480 V AC, 3-PHASE
LOVSF30016DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30016DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30016DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30016DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30016DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30025DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30025DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30025DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30025DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30025DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30040DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30040DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30040DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30040DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30040DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30063DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30063DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30063DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30063DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30063DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 480Y/277V | 3 | 65 | - | - | 480Y/277V | 3 | 65 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30100DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30100DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30100DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30100DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30100DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 480Y/277V | 3 | 65 | 1.1 | 1/2 | 480Y/277V | 3 | 65 | 1/2 | 1.1 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30160DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30160DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30160DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30160DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30160DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 480Y/277V | 3 | 65 | 1.6 | 3/4 | 480Y/277V | 3 | 65 | 3/4 | 1.6 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30250DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30250DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30250DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30250DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30250DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 480Y/277V | 3 | 65 | 2.1 | 1 | 480Y/277V | 3 | 65 | 1 | 2.1 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30400DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30400DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30400DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30400DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30400DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 480Y/277V | 3 | 65 | 3.4 | 2 | 480Y/277V | 3 | 65 | 2 | 3.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30650DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF30650DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30650DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30650DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF30650DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 480Y/277V | 3 | 65 | 4.8 | 3 | 480Y/277V | 3 | 65 | 3 | 4.8 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF09xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/A | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF12xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/A | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF18xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF09xxL | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/L | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF12xxL | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/L | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF18xxL | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF09xxD | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/D | 480 | 3 | 5 | 7.6 | 5 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF12xxD | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF12xx/D | 480 | 3 | 5 | 11.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF18xxD | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1000DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 480Y/277V | 3 | 65 | 7.6 | 5 | 480Y/277V | 3 | 65 | 5 | 7.6 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400DPBF18xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400DPBF18xxL | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400DPBF18xxD | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1400DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800DPBF18xxA | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800DPBF18xxL | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800DPBF18xxD | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 480 | 3 | 5 | 14.0 | 10 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E1800DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE1800 | 480Y/277V | 3 | 65 | 14 | 10 | 480Y/277V | 3 | 65 | 10 | 14 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2300DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE2300 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2300DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE2300 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2300DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE2300 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2300DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE2300 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2500DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE2500 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2500DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE2500 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 480 | 3 | 5 | 21.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2500DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE2500 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E2500DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE2500 | 480Y/277V | 3 | 30 | 21 | 15 | 480Y/277V | 3 | 30 | 15 | 21 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E3200DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE3200 | 480Y/277V | 3 | 10 | 27 | 20 | 480Y/277V | 3 | 10 | 20 | 27 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF3E3200DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE3200 | 480Y/277V | 3 | 10 | 27 | 20 | 480Y/277V | 3 | 10 | 20 | 27 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 480 | 3 | 5 | 27.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having an ampacity of
125 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor
controllers shall be considered in the end-product application.
|  | 6 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu) No. 14 AWG wire.
|  | 7 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu), for size of conductor see table below.
|  | 8 | Contactor DPBG12xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF09xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF12xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF18xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF26xx - The xx may be replaced with suffix 00 or T4 only.
Contactor DPBF32xx - The xx may be replaced with suffix 00 or T4 only.

## 600V
Issued: 2025-04-30
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Dimension (cu in) | Conditions of Use | File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Hp Rating | Current Rating, FLA or FLA/LRA |  |  | UL File Number | Volume / Section (Vol#).(Sec#)
600 V AC, 3-PHASE
LOVSF40016DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40016DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40016DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40016DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40016DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0016 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.16 / 0.96 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40025DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40025DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40025DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40025DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40025DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0025 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.25 / 1.5 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40040DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40040DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40040DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40040DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40040DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0040 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.4 / 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40063DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40063DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40063DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40063DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40063DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0063 | 600Y/347V | 3 | 50 | - | - | 600Y/347V | 3 | 50 | - | 0.63 / 3.78 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40100DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40100DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40100DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40100DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40100DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0100 | 600Y/347V | 3 | 50 | 0.9 | 1/2 | 600Y/347V | 3 | 50 | 1/2 | 0.9 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40160DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40160DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40160DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40160DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40160DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0160 | 600Y/347V | 3 | 50 | 1.7 | 1 | 600Y/347V | 3 | 50 | 1 | 1.7 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40250DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40250DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40250DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40250DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40250DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0250 | 600Y/347V | 3 | 30 | 2.4 | 1.5 | 600Y/347V | 3 | 30 | 1.5 | 2.4 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40400DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF12xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF12xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/A | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF12xxLR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF12xxL | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/L | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF12xxDR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF12xxD | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF12xx/D | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40400DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40400DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40400DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40400DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0400 | 600Y/347V | 3 | 30 | 3.9 | 3 | 600Y/347V | 3 | 30 | 3 | 3.9 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40650DPBG12xxR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650DPBG12xx | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBG12xx | 600 | 3 | 5 | 11.0 | 10 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3040R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650DPBF09xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650DPBF18xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650DPBF09xxL | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650DPBF18xxL | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650DPBF09xxD | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650DPBF18xxD | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 439 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 439
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 439
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 439
LOVSF40650DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40650DPBF26xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40650DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF40650DPBF32xxA | F | MSP | Lovato Electric SpA | SM1R0650 | 600Y/347V | 3 | 30 | 6.1 | 5 | 600Y/347V | 3 | 30 | 5 | 6.1 | 1172 | 1, 5, 6, 8 | E327729 | 1.3
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000DPBF09xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000DPBF09xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/A | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000DPBF18xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000DPBF09xxLR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000DPBF09xxL | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/L | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000DPBF18xxL | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000DPBF09xxDR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000DPBF09xxD | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF09xx/D | 600 | 3 | 5 | 9.0 | 7 1/2 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000DPBF18xxD | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1000DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE1000 | 600Y/347V | 3 | 30 | 9.0 | 7.5 | 600Y/347V | 3 | 30 | 7 1/2 | 9 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400DPBF18xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400DPBF18xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/A | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3141R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400DPBF18xxLR | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400DPBF18xxL | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/L | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400DPBF18xxDR | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400DPBF18xxD | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF18xx/D | 600 | 3 | 5 | 17.0 | 15 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3142R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400DPBF26xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400DPBF26xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF26xx/A | 600 | 3 | 5 | 22.0 | 20 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400DPBF32xxAR | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9000R | - | - | - | - | - |  |  | - | - | - | 1171
LOVSF4E1400DPBF32xxA | F | MSP | Lovato Electric SpA | SM1RE1400 | 600Y/347V | 3 | 30 | 11 | 10 | 600Y/347V | 3 | 30 | 10 | 11 | 1172 | 1, 5, 7, 8 | E327729 | 1.4
|  | MC | Lovato Electric SpA | DPBF32xx/A | 600 | 3 | 5 | 27.0 | 25 |  |  | - | - | - | 1171
|  | ACC (LINK) (OPTIONAL) | Lovato Electric SpA | SM1X3241R | - | - | - | - | - |  |  | - | - | - | 1171
|  | ACC (ADAPTOR) | Lovato Electric SpA | SM1X9050 | - | - | - | - | - |  |  | - | - | - | 1171
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having an ampacity of
125 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor
controllers shall be considered in the end-product application.
|  | 6 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu) No. 14 AWG wire.
|  | 7 | Cable between Type E and Contactor (AVLV2/8) or Listed 75°C copper (cu), for size of conductor see table below.
|  | 8 | Contactor DPBG12xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF09xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF12xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF18xx - The xx may be replaced with suffix 10, 01, or T4 only.
Contactor DPBF26xx - The xx may be replaced with suffix 00 or T4 only.
Contactor DPBF32xx - The xx may be replaced with suffix 00 or T4 only.