## C.O.A.
Conditions of Acceptability For Combination Motor Controllers:
Unless specified otherwise in the individual Recognitions, consideration is to be given to the following Conditions of Acceptability when these
components are employed as a combination motor controller in the end-use equipment: Specific Conditions of Use - Number refers to specific
condition number as defined below and number in parenthesis identifies specific information applicable to the combination motor controller.
C.O. A #:
1 | All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in
cubic inches with a continous piano hinge and 3 clamp style latches. Additional testing of the combination motor controller is not required when installed in an enclosure having the same or larger volume with similar door securements.
2 | Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current as indicated below and 90C minimum insulation rating.
| CMC HP Rating at 480V | Motor FLA | Wire size
| 40 | 52 | 6 AWG
| 60 | 77 | 3 AWG
| 75 | 96 | 1 AWG
| 100 | 124 | 2/0 AWG
| 125 | 156 | 3/0 AWG
| 150 | 180 | 4/0 AWG
3 | The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D Combination Motor Controllers).
4 | Intended for use with Class 9422 Model CSF30 operating mechanism manufactured by Schneider Electric USA, Inc. and Class 9422, Type A1 handle manufactured by Square D Co.
5 | Contactors LC1D80, D115, D150, G115, G150, G185, G265 and G330 must be used with terminals DZ2FG* (6-3/0 AWG) or DZ2FH* (6 AWG -300kcmil).
6 | Overload Relay LR2D3563 must be used with LA7D3064 terminals.
Overload Relays LR9G115 and LR9G225 must be used with DZ2FG* or DZ2FH* terminals.

## H&J MCP
[17 empty] | Issued: | 2026-02-27
| Listed Combination Motor Controller Information |  |  | Component Description | [6 empty] | Combination Motor Controller Ratings
Database Identification Number | UL File Number | Volume / Section (Vol#)/(Sec#) | Construction Type | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, phase | SCCR, kA | Full Load Current, A | HP | Voltage, V ac | Number of phases | Short Circuit Current Rating, kA | Current Rating, FLA or FLA/LRA | Horsepower Rating | Enclosure Volume, cubic inches | Conditions of Use | Schematic
SE309000.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | HLL36150M74 | 480, 3 | - | 150 | - | 480 | 3 | 100 | 96 | 75 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1-D115 | 480, 3 | 100 | 96 | 75
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G115 | 480, 3 | 100 | 28-115 | -
SE309001.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | HLL36150M74 | 480, 3 | - | 150 | - | 480 | 3 | 100 | 96 | 75 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1-D115 | 480, 3 | 100 | 96 | 75
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G225 | 480, 3 | 100 | 57-225 | -
SE309002.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | HLL36150M74 | 480, 3 | - | 150 | - | 480 | 3 | 100 | 96 | 75 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1-D150 | 480, 3 | 100 | 124 | 100
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G115 | 480, 3 | 100 | 28-115 | -
SE309003.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | HLL36150M74 | 480, 3 | - | 150 | - | 480 | 3 | 100 | 124 | 100 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1-D150 | 480, 3 | 100 | 124 | 100
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G225 | 480, 3 | 100 | 57-225 | -
SE309004.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | HLL36150M74 | 480, 3 | - | 150 | - | 480 | 3 | 100 | 52 | 40 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1-D80 | 480, 3 | 100 | 77 | 60
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G115 | 480, 3 | 100 | 28-115 | -
SE309005.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | HLL36150M74 | 480, 3 | - | 150 | - | 480 | 3 | 100 | 96 | 75 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G115 | 480, 3 | 100 | 96 | 75
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G115 | 480, 3 | 100 | 28-115 | -
SE309006.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | HLL36150M74 | 480, 3 | - | 150 | - | 480 | 3 | 100 | 96 | 75 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G115 | 480, 3 | 100 | 96 | 75
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G225 | 480, 3 | 100 | 57-225 | -
SE309007.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | HLL36150M74 | 480, 3 | - | 150 | - | 480 | 3 | 100 | 96 | 75 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G185 | 480, 3 | 100 | 156 | 125
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G115 | 480, 3 | 100 | 28-115 | -
SE309008.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | HLL36150M74 | 480, 3 | - | 150 | - | 480 | 3 | 100 | 124 | 100 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G185 | 480, 3 | 100 | 156 | 125
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G225 | 480, 3 | 100 | 57-225 | -
SE309009.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | HLL36150M74 | 480, 3 | - | 150 | - | 480 | 3 | 100 | 96 | 75 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G265 | 480, 3 | 100 | 240 | 200
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G115 | 480, 3 | 100 | 28-115 | -
SE309010.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | HLL36150M74 | 480, 3 | - | 150 | - | 480 | 3 | 100 | 124 | 100 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G265 | 480, 3 | 100 | 240 | 200
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G225 | 480, 3 | 100 | 57-225 | -
SE309011.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | HLL36150M74 | 480, 3 | - | 150 | - | 480 | 3 | 100 | 96 | 75 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G330 | 480, 3 | 100 | 302 | 250
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G115 | 480, 3 | 100 | 28-115 | -
SE309012.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | HLL36150M74 | 480, 3 | - | 150 | - | 480 | 3 | 100 | 124 | 100 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G330 | 480, 3 | 100 | 302 | 250
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G225 | 480, 3 | 100 | 57-225 | -
SE309013.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | JLL36250M75 | 480, 3 | - | 250 | - | 480 | 3 | 100 | 96 | 75 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1-D115 | 480, 3 | 100 | 96 | 75
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G115 | 480, 3 | 100 | 28-115 | -
SE309014.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | JLL36250M75 | 480, 3 | - | 250 | - | 480 | 3 | 100 | 96 | 75 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1-D115 | 480, 3 | 100 | 96 | 75
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G225 | 480, 3 | 100 | 57-225 | -
SE309015.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | JLL36250M75 | 480, 3 | - | 250 | - | 480 | 3 | 100 | 96 | 75 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1-D150 | 480, 3 | 100 | 124 | 100
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G115 | 480, 3 | 100 | 28-115 | -
SE309016.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | JLL36250M75 | 480, 3 | - | 250 | - | 480 | 3 | 100 | 124 | 100 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1-D150 | 480, 3 | 100 | 124 | 100
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G225 | 480, 3 | 100 | 57-225 | -
SE309017.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | JLL36250M75 | 480, 3 | - | 250 | - | 480 | 3 | 100 | 96 | 75 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G115 | 480, 3 | 100 | 96 | 75
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G115 | 480, 3 | 100 | 28-115 | -
SE309018.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | JLL36250M75 | 480, 3 | - | 250 | - | 480 | 3 | 100 | 96 | 75 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G115 | 480, 3 | 100 | 96 | 75
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G225 | 480, 3 | 100 | 57-225 | -
SE309019.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | JLL36250M75 | 480, 3 | - | 250 | - | 480 | 3 | 100 | 96 | 75 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G150 | 480, 3 | 100 | 124 | 100
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G115 | 480, 3 | 100 | 28-115 | -
SE309020.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | JLL36250M75 | 480, 3 | - | 250 | - | 480 | 3 | 100 | 124 | 100 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G150 | 480, 3 | 100 | 124 | 100
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G225 | 480, 3 | 100 | 57-225 | -
SE309021.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | JLL36250M75 | 480, 3 | - | 250 | - | 480 | 3 | 100 | 77 | 60 | 9137 | 1, 2, 3, 4, 5, 6
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G185 | 480, 3 | 100 | 156 | 125
|  |  |  | OLR | Schneider Electric Industries, SAS | LR2D3563 | 480, 3 | 100 | 63-80 | -
SE309022.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | JLL36250M75 | 480, 3 | - | 250 | - | 480 | 3 | 100 | 96 | 75 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G185 | 480, 3 | 100 | 156 | 125
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G115 | 480, 3 | 100 | 28-115 | -
SE309023.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | JLL36250M75 | 480, 3 | - | 250 | - | 480 | 3 | 100 | 156 | 125 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G185 | 480, 3 | 100 | 156 | 125
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G225 | 480, 3 | 100 | 57-225 | -
SE309024.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | JLL36250M75 | 480, 3 | - | 250 | - | 480 | 3 | 100 | 96 | 75 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G265 | 480, 3 | 100 | 240 | 200
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G115 | 480, 3 | 100 | 28-115 | -
SE309025.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | JLL36250M75 | 480, 3 | - | 250 | - | 480 | 3 | 100 | 180 | 150 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G265 | 480, 3 | 100 | 240 | 200
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G225 | 480, 3 | 100 | 57-225 | -
SE309026.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | JLL36250M75 | 480, 3 | - | 250 | - | 480 | 3 | 100 | 96 | 75 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G330 | 480, 3 | 100 | 302 | 250
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G115 | 480, 3 | 100 | 28-115 | -
SE309027.01 | E152395 | 4/6 | D | ICB | Schneider Electric USA, Inc. | JLL36250M75 | 480, 3 | - | 250 | - | 480 | 3 | 100 | 180 | 150 | 9137 | 1, 2, 3, 4, 5
|  |  |  | MC | Schneider Electric Industries, SAS | LC1G330 | 480, 3 | 100 | 302 | 250
|  |  |  | OLR | Schneider Electric Industries, SAS | LR9G225 | 480, 3 | 100 | 57-225 | -
Note on H1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Columns H, I, J and K to be hidden before publishing on website.