## Type C Combinations
Issued: 2020-08-01
|  |  | X | X | X | X | X | X | [16 empty] | X | X
(NOTE: The bracketed alphanumeric in each column heading and in example entries, such as [B1], corresponds to a section of the short circuit database submittal guideline document which provides further information concerning the expected content and format for entering data into the spreadsheet cells)
[B1] Database Identification Number | [B2] Listed Combination Motor Controller Information | [7 empty] | [B3] Construction Type | [B4] Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | [B8] Enclosure Volume, cubic inches | [B9] Conditions of Use | [B10] Schematic
| Listing Report Information |  |  |  |  | Enclosure or Unit Dimensions
| UL File Number | Report Issue Date YYYY-MM-DD | Volume / Section (Vol#).(Sec#) | Model Number or Product Style/ Designation | Product Description on Page/Figure/Ill. | Enclosure or Unit Height, inches | Width, inches | Depth, inches |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | [B7] Voltage, V | [B7] Number of Phases | [B5] SCCR, kA | [B6] Current Rating, FLA or FLA/LRA | [B6] Hp Rating |  |  |  | [B11] Other References
ABBCA2002N15E0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 200 | 3 | 65 | 2.5 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXE | 240 | 3 | 5 | 1.6-3.4
ABBCA2002N15FF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 200 | 3 | 65 | 3.7 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBCA2002N15F001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 200 | 3 | 65 | 4.8 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBCA2002N15G1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 200 | 3 | 65 | 6.9 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCA2082N15E0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 2.4 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXE | 240 | 3 | 5 | 1.6-3.4
ABBCA2082N15FF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 3.5 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBCA2082N15F001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 4.6 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBCA2082N15F1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 6.6 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBCA2082N15G1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 6.6 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCA2402N15E0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 220 - 240 (230) | 3 | 65 | 2.2 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXE | 240 | 3 | 5 | 1.6-3.4
ABBCA2402N15EF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 220 - 240 (230) | 3 | 65 | 3.2 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXE | 240 | 3 | 5 | 1.6-3.4
ABBCA2402N15FF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 220 - 240 (230) | 3 | 65 | 3.2 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBCA2402N15F001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 220 - 240 (230) | 3 | 65 | 4.2 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBCA2402N15F1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 220 - 240 (230) | 3 | 65 | 6 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBCA4802N15D0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 1.1 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 480 | 3 | 5 | 0.8-1.7
ABBCA4802N15DF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 1.6 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 480 | 3 | 5 | 0.8-1.7
ABBCA4802N15EF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 1.6 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBCA4802N15E001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 2.1 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBCA4802N15E1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 3 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBCA4802N15E002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 3.4 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBCA4802N15F002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 3.4 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXF | 480 | 3 | 5 | 3.2-6.8
ABBCA6002N15D0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 0.9 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 600 | 3 | 5 | 0.8-1.7
ABBCA6002N15DF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 1.3 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 600 | 3 | 5 | 0.8-1.7
ABBCA6002N15D001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 1.7 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 600 | 3 | 5 | 0.8-1.7
ABBCA6002N15E001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 1.7 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 600 | 3 | 5 | 1.6-3.4
ABBCA6002N15E1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 2.4 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 600 | 3 | 5 | 1.6-3.4
ABBCA6002N15E002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 2.7 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 600 | 3 | 5 | 1.6-3.4
ABBCA2002S15E0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 200 | 3 | 100 | 2.5 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXE | 240 | 3 | 5 | 1.6-3.4
ABBCA2002S15FF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 200 | 3 | 100 | 3.7 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBCA2002S15F001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 200 | 3 | 100 | 4.8 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBCA2002S15G1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 200 | 3 | 100 | 6.9 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCA2082S15E0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 2.4 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXE | 240 | 3 | 5 | 1.6-3.4
ABBCA2082S15FF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 3.5 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBCA2082S15F001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 4.6 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBCA2082S15F1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 6.6 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBCA2082S15G1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 6.6 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCA2402S15E0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 220 - 240 (230) | 3 | 100 | 2.2 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXE | 240 | 3 | 5 | 1.6-3.4
ABBCA2402S15EF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 220 - 240 (230) | 3 | 100 | 3.2 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXE | 240 | 3 | 5 | 1.6-3.4
ABBCA2402S15FF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 220 - 240 (230) | 3 | 100 | 3.2 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBCA2402S15F001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 220 - 240 (230) | 3 | 100 | 4.2 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBCA2402S15F1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 220 - 240 (230) | 3 | 100 | 6 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBCA4802S15D0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 1.1 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 480 | 3 | 5 | 0.8-1.7
ABBCA4802S15DF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 1.6 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 480 | 3 | 5 | 0.8-1.7
ABBCA4802S15EF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 1.6 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBCA4802S15E001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 2.1 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBCA4802S15E1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 3 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBCA4802S15E002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 3.4 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBCA4802S15F002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 3.4 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXF | 480 | 3 | 5 | 3.2-6.8
ABBCA6002S15D0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 0.9 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 600 | 3 | 5 | 0.8-1.7
ABBCA6002S15DF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 1.3 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 600 | 3 | 5 | 0.8-1.7
ABBCA6002S15D001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 1.7 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 600 | 3 | 5 | 0.8-1.7
ABBCA6002S15E001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 1.7 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 600 | 3 | 5 | 1.6-3.4
ABBCA6002S15E1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 2.4 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 600 | 3 | 5 | 1.6-3.4
ABBCA6002S15E002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 2.7 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 600 | 3 | 5 | 1.6-3.4
ABBCA4802H15D0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 1.1 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 480 | 3 | 5 | 0.8-1.7
ABBCA4802H15DF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 1.6 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 480 | 3 | 5 | 0.8-1.7
ABBCA4802H15EF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 1.6 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBCA4802H15E001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 2.1 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBCA4802H15E1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 3 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBCA4802H15E002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 3.4 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBCA4802H15F002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 3.4 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXF | 480 | 3 | 5 | 3.2-6.8
ABBCA6002H15D0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 0.9 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 600 | 3 | 5 | 0.8-1.7
ABBCA6002H15DF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 1.3 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 600 | 3 | 5 | 0.8-1.7
ABBCA6002H15D001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 1.7 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 600 | 3 | 5 | 0.8-1.7
ABBCA6002H15E001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 1.7 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 600 | 3 | 5 | 1.6-3.4
ABBCA6002H15E1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 2.4 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 600 | 3 | 5 | 1.6-3.4
ABBCA6002H15E002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 2.7 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 600 | 3 | 5 | 1.6-3.4
ABBCA4802L15D0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 1.1 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 480 | 3 | 5 | 0.8-1.7
ABBCA4802L15DF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 1.6 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 480 | 3 | 5 | 0.8-1.7
ABBCA4802L15EF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 1.6 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBCA4802L15E001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 2.1 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBCA4802L15E1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 3 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBCA4802L15E002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 3.4 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBCA4802L15F002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 3.4 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXF | 480 | 3 | 5 | 3.2-6.8
ABBCA2002N1510F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 200 | 3 | 65 | 2.5 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2002N151F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 200 | 3 | 65 | 3.7 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2002N151001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 200 | 3 | 65 | 4.8 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2002N1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 200 | 3 | 65 | 6.9 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2082N1510F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 2.4 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2082N151F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 3.5 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2082N151001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 4.6 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2082N1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 6.6 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2402N1510F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 220 - 240 (230) | 3 | 65 | 2.2 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2402N151F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 220 - 240 (230) | 3 | 65 | 3.2 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2402N151001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 220 - 240 (230) | 3 | 65 | 4.2 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2402N1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 220 - 240 (230) | 3 | 65 | 6 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA4802N1510F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 1.1 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA4802N151F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 1.6 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA4802N151001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 2.1 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA4802N1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 3 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA4802N151002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 3.4 | 2 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA6002N1510F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 0.9 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCA6002N151F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 1.3 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCA6002N151001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 1.7 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCA6002N1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 2.4 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCA6002N151002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 2.7 | 2 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCA2002S1510F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 200 | 3 | 100 | 2.5 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2002S151F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 200 | 3 | 100 | 3.7 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2002S151001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 200 | 3 | 100 | 4.8 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2002S1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 200 | 3 | 100 | 6.9 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2082S1510F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 2.4 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2082S151F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 3.5 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2082S151001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 4.6 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2082S1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 6.6 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2402S1510F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 220 - 240 (230) | 3 | 100 | 2.2 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2402S151F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 220 - 240 (230) | 3 | 100 | 3.2 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2402S151001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 220 - 240 (230) | 3 | 100 | 4.2 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA2402S1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 220 - 240 (230) | 3 | 100 | 6 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCA4802S1510F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 1.1 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA4802S151F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 1.6 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA4802S151001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 2.1 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA4802S1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 3 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA4802S151002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 3.4 | 2 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA6002S1510F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 0.9 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCA6002S151F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 1.3 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCA6002S151001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 1.7 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCA6002S1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 2.4 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCA6002S151002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 2.7 | 2 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCA4802H1510F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 1.1 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA4802H151F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 1.6 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA4802H151001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 2.1 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA4802H1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 3 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA4802H151002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 3.4 | 2 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA6002H1510F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 0.9 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCA6002H151F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 1.3 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCA6002H151001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 1.7 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCA6002H1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 2.4 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCA6002H151002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 2.7 | 2 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCA4802L1510F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 1.1 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA4802L151F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 1.6 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA4802L151001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 2.1 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA4802L1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 3 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCA4802L151002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 3.4 | 2 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCB2002N15G002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 200 | 3 | 65 | 7.8 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2002N20G002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 20 |  | 200 | 3 | 65 | 7.8 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2002N15G003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 200 | 3 | 65 | 11 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2002N20G003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 20 |  | 200 | 3 | 65 | 11 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2082N15G002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 7.5 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2082N20G002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 20 |  | 208 | 3 | 65 | 7.5 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2082N15G003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 10.6 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2082N20G003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 20 |  | 208 | 3 | 65 | 10.6 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2402N20F002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 20 |  | 220 - 240 (230) | 3 | 65 | 6.8 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBCB2402N20G002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 20 |  | 220 - 240 (230) | 3 | 65 | 6.8 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2402N15G003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 220 - 240 (230) | 3 | 65 | 9.6 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2402N20G003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 20 |  | 220 - 240 (230) | 3 | 65 | 9.6 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB4802N15F003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 4.8 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 480 | 3 | 5 | 3.2-6.8
ABBCB4802N15G005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 7.6 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCB4802N20G005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 20 |  | 440 - 480 (460) | 3 | 25 | 7.6 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCB6002N15F003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 3.9 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 600 | 3 | 5 | 3.2-6.8
ABBCB6002N15F005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 6.1 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 600 | 3 | 5 | 3.2-6.8
ABBCB6002N20F005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 20 |  | 550 - 600 (575) | 3 | 18 | 6.1 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 600 | 3 | 5 | 3.2-6.8
ABBCB2002S15G002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 200 | 3 | 100 | 7.8 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2002S20G002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 20 |  | 200 | 3 | 100 | 7.8 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2002S15G003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 200 | 3 | 100 | 11 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2002S20G003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 20 |  | 200 | 3 | 100 | 11 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2082S15G002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 7.5 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2082S20G002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 20 |  | 208 | 3 | 100 | 7.5 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2082S15G003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 10.6 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2082S20G003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 20 |  | 208 | 3 | 100 | 10.6 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2402S20F002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 20 |  | 220 - 240 (230) | 3 | 100 | 6.8 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBCB2402S20G002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 20 |  | 220 - 240 (230) | 3 | 100 | 6.8 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2402S15G003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 220 - 240 (230) | 3 | 100 | 9.6 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB2402S20G003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 20 |  | 220 - 240 (230) | 3 | 100 | 9.6 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBCB4802S15F003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 4.8 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 480 | 3 | 5 | 3.2-6.8
ABBCB4802S15G005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 7.6 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCB4802S20G005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 20 |  | 440 - 480 (460) | 3 | 35 | 7.6 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCB6002S15F003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 3.9 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 600 | 3 | 5 | 3.2-6.8
ABBCB6002S15F005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 6.1 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 600 | 3 | 5 | 3.2-6.8
ABBCB6002S20F005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 20 |  | 550 - 600 (575) | 3 | 22 | 6.1 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 600 | 3 | 5 | 3.2-6.8
ABBCB4802H15F003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 4.8 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 480 | 3 | 5 | 3.2-6.8
ABBCB4802H15G005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 7.6 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCB4802H20G005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 20 |  | 440 - 480 (460) | 3 | 65 | 7.6 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCB6002H15F003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 3.9 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 600 | 3 | 5 | 3.2-6.8
ABBCB6002H15F005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 6.1 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 600 | 3 | 5 | 3.2-6.8
ABBCB6002H20F005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 20 |  | 550 - 600 (575) | 3 | 25 | 6.1 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 600 | 3 | 5 | 3.2-6.8
ABBCB4802L15F003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 4.8 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 480 | 3 | 5 | 3.2-6.8
ABBCB4802L15G005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 7.6 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCB4802L20G005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 20 |  | 440 - 480 (460) | 3 | 100 | 7.6 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCB2002N151002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 200 | 3 | 65 | 7.8 | 2 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2002N201002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 20 |  | 200 | 3 | 65 | 7.8 | 2 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2002N151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 200 | 3 | 65 | 11 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2002N201003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 20 |  | 200 | 3 | 65 | 11 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2082N151002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 7.5 | 2 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2082N201002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 20 |  | 208 | 3 | 65 | 7.5 | 2 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2082N151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 10.6 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2082N201003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 20 |  | 208 | 3 | 65 | 10.6 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2402N201002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 20 |  | 220 - 240 (230) | 3 | 65 | 6.8 | 2 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2402N151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 220 - 240 (230) | 3 | 65 | 9.6 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2402N201003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 20 |  | 220 - 240 (230) | 3 | 65 | 9.6 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB4802N151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 4.8 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCB4802N151005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 7.6 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCB4802N201005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 20 |  | 440 - 480 (460) | 3 | 25 | 7.6 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCB6002N151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 3.9 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCB6002N151005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 6.1 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCB6002N201005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 20 |  | 550 - 600 (575) | 3 | 18 | 6.1 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCB2002S151002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 200 | 3 | 100 | 7.8 | 2 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2002S201002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 20 |  | 200 | 3 | 100 | 7.8 | 2 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2002S151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 200 | 3 | 100 | 11 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2002S201003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 20 |  | 200 | 3 | 100 | 11 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2082S151002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 7.5 | 2 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2082S201002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 20 |  | 208 | 3 | 100 | 7.5 | 2 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2082S151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 10.6 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2082S201003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 20 |  | 208 | 3 | 100 | 10.6 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2402S201002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 20 |  | 220 - 240 (230) | 3 | 100 | 6.8 | 2 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2402S151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 220 - 240 (230) | 3 | 100 | 9.6 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB2402S201003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 20 |  | 220 - 240 (230) | 3 | 100 | 9.6 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCB4802S151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 4.8 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCB4802S151005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 7.6 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCB4802S201005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 20 |  | 440 - 480 (460) | 3 | 35 | 7.6 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCB6002S151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 3.9 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCB6002S151005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 6.1 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCB6002S201005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 20 |  | 550 - 600 (575) | 3 | 22 | 6.1 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCB4802H151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 4.8 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCB4802H151005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 7.6 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCB4802H201005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 20 |  | 440 - 480 (460) | 3 | 65 | 7.6 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCB6002H151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 3.9 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCB6002H151005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 6.1 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCB6002H201005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 20 |  | 550 - 600 (575) | 3 | 25 | 6.1 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCB4802L151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 4.8 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCB4802L151005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 7.6 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCB4802L201005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 20 |  | 440 - 480 (460) | 3 | 100 | 7.6 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC2002N25H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 25 |  | 200 | 3 | 65 | 17.5 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2002N30H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 30 |  | 200 | 3 | 65 | 17.5 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2002N40H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 40 |  | 200 | 3 | 65 | 17.5 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2002N40H7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 40 |  | 200 | 3 | 65 | 25.3 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2002N60H7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 200 | 3 | 65 | 25.3 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2082N25H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 25 |  | 208 | 3 | 65 | 16.7 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2082N30H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 30 |  | 208 | 3 | 65 | 16.7 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2082N40H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 40 |  | 208 | 3 | 65 | 16.7 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2082N40H7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 40 |  | 208 | 3 | 65 | 24.2 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2082N60H7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 208 | 3 | 65 | 24.2 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2402N20H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 20 |  | 220 - 240 (230) | 3 | 65 | 15.2 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2402N25H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 25 |  | 220 - 240 (230) | 3 | 65 | 15.2 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2402N30H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 30 |  | 220 - 240 (230) | 3 | 65 | 15.2 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2402N40H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 40 |  | 220 - 240 (230) | 3 | 65 | 15.2 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2402N30H7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 30 |  | 220 - 240 (230) | 3 | 65 | 22 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2402N40H7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 40 |  | 220 - 240 (230) | 3 | 65 | 22 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC4802N15G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802N20G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 20 |  | 440 - 480 (460) | 3 | 25 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802N25G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 25 |  | 440 - 480 (460) | 3 | 25 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802N30G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 30 |  | 440 - 480 (460) | 3 | 25 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802N40G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 40 |  | 440 - 480 (460) | 3 | 25 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802N20H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 20 |  | 440 - 480 (460) | 3 | 25 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBCC4802N25H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 25 |  | 440 - 480 (460) | 3 | 25 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBCC4802N30H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 30 |  | 440 - 480 (460) | 3 | 25 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBCC4802N40H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 40 |  | 440 - 480 (460) | 3 | 25 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBCC6002N15G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 9 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002N20G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 20 |  | 550 - 600 (575) | 3 | 18 | 9 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002N25G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 25 |  | 550 - 600 (575) | 3 | 18 | 9 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002N30G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 30 |  | 550 - 600 (575) | 3 | 18 | 9 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002N15G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002N20G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 20 |  | 550 - 600 (575) | 3 | 18 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002N25G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 25 |  | 550 - 600 (575) | 3 | 18 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002N30G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 30 |  | 550 - 600 (575) | 3 | 18 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002N40G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 40 |  | 550 - 600 (575) | 3 | 18 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC2002S25H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 25 |  | 200 | 3 | 100 | 17.5 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2002S30H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 30 |  | 200 | 3 | 100 | 17.5 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2002S40H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 40 |  | 200 | 3 | 100 | 17.5 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2002S40H7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 40 |  | 200 | 3 | 100 | 25.3 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2002S60H7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 200 | 3 | 100 | 25.3 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2082S25H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 25 |  | 208 | 3 | 100 | 16.7 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2082S30H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 30 |  | 208 | 3 | 100 | 16.7 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2082S40H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 40 |  | 208 | 3 | 100 | 16.7 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2082S40H7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 40 |  | 208 | 3 | 100 | 24.2 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2082S60H7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 208 | 3 | 100 | 24.2 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2402S20H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 20 |  | 220 - 240 (230) | 3 | 100 | 15.2 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2402S25H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 25 |  | 220 - 240 (230) | 3 | 100 | 15.2 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2402S30H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 30 |  | 220 - 240 (230) | 3 | 100 | 15.2 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2402S40H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 40 |  | 220 - 240 (230) | 3 | 100 | 15.2 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2402S30H7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 30 |  | 220 - 240 (230) | 3 | 100 | 22 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC2402S40H7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 40 |  | 220 - 240 (230) | 3 | 100 | 22 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBCC4802S15G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802S20G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 20 |  | 440 - 480 (460) | 3 | 35 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802S25G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 25 |  | 440 - 480 (460) | 3 | 35 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802S30G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 30 |  | 440 - 480 (460) | 3 | 35 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802S40G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 40 |  | 440 - 480 (460) | 3 | 35 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802S20H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 20 |  | 440 - 480 (460) | 3 | 35 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBCC4802S25H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 25 |  | 440 - 480 (460) | 3 | 35 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBCC4802S30H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 30 |  | 440 - 480 (460) | 3 | 35 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBCC4802S40H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 40 |  | 440 - 480 (460) | 3 | 35 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBCC6002S15G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 9 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002S20G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 20 |  | 550 - 600 (575) | 3 | 22 | 9 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002S25G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 25 |  | 550 - 600 (575) | 3 | 22 | 9 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002S30G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 30 |  | 550 - 600 (575) | 3 | 22 | 9 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002S15G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002S20G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 20 |  | 550 - 600 (575) | 3 | 22 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002S25G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 25 |  | 550 - 600 (575) | 3 | 22 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002S30G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 30 |  | 550 - 600 (575) | 3 | 22 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002S40G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 40 |  | 550 - 600 (575) | 3 | 22 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC4802H15G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802H20G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 20 |  | 440 - 480 (460) | 3 | 65 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802H25G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 25 |  | 440 - 480 (460) | 3 | 65 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802H30G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 30 |  | 440 - 480 (460) | 3 | 65 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802H40G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 40 |  | 440 - 480 (460) | 3 | 65 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802H20H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 20 |  | 440 - 480 (460) | 3 | 65 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBCC4802H25H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 25 |  | 440 - 480 (460) | 3 | 65 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBCC4802H30H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 30 |  | 440 - 480 (460) | 3 | 65 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBCC4802H40H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 40 |  | 440 - 480 (460) | 3 | 65 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBCC6002H15G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 9 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002H20G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 20 |  | 550 - 600 (575) | 3 | 25 | 9 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002H25G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 25 |  | 550 - 600 (575) | 3 | 25 | 9 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002H30G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 30 |  | 550 - 600 (575) | 3 | 25 | 9 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002H15G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002H20G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 20 |  | 550 - 600 (575) | 3 | 25 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002H25G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 25 |  | 550 - 600 (575) | 3 | 25 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002H30G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 30 |  | 550 - 600 (575) | 3 | 25 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC6002H40G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 40 |  | 550 - 600 (575) | 3 | 25 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBCC4802L15G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802L20G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 20 |  | 440 - 480 (460) | 3 | 100 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802L25G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 25 |  | 440 - 480 (460) | 3 | 100 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802L30G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 30 |  | 440 - 480 (460) | 3 | 100 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802L40G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 40 |  | 440 - 480 (460) | 3 | 100 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBCC4802L20H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 20 |  | 440 - 480 (460) | 3 | 100 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBCC4802L25H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 25 |  | 440 - 480 (460) | 3 | 100 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBCC4802L30H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 30 |  | 440 - 480 (460) | 3 | 100 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBCC4802L40H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 40 |  | 440 - 480 (460) | 3 | 100 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBCC2002N251005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 25 |  | 200 | 3 | 65 | 17.5 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2002N301005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 30 |  | 200 | 3 | 65 | 17.5 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2002N401005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 40 |  | 200 | 3 | 65 | 17.5 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2002N4017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 40 |  | 200 | 3 | 65 | 25.3 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2002N6017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 200 | 3 | 65 | 25.3 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2082N251005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 25 |  | 208 | 3 | 65 | 16.7 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2082N301005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 30 |  | 208 | 3 | 65 | 16.7 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2082N401005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 40 |  | 208 | 3 | 65 | 16.7 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2082N4017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 40 |  | 208 | 3 | 65 | 24.2 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2082N6017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 208 | 3 | 65 | 24.2 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2402N201005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 20 |  | 220 - 240 (230) | 3 | 65 | 15.2 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2402N251005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 25 |  | 220 - 240 (230) | 3 | 65 | 15.2 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2402N301005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 30 |  | 220 - 240 (230) | 3 | 65 | 15.2 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2402N401005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 40 |  | 220 - 240 (230) | 3 | 65 | 15.2 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2402N3017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 30 |  | 220 - 240 (230) | 3 | 65 | 22 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2402N4017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 40 |  | 220 - 240 (230) | 3 | 65 | 22 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC4802N1517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802N2017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 20 |  | 440 - 480 (460) | 3 | 25 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802N2517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 25 |  | 440 - 480 (460) | 3 | 25 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802N3017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 30 |  | 440 - 480 (460) | 3 | 25 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802N4017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 40 |  | 440 - 480 (460) | 3 | 25 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802N201010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 20 |  | 440 - 480 (460) | 3 | 25 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802N251010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 25 |  | 440 - 480 (460) | 3 | 25 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802N301010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 30 |  | 440 - 480 (460) | 3 | 25 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802N401010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 40 |  | 440 - 480 (460) | 3 | 25 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC6002N1517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 9 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002N2017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 20 |  | 550 - 600 (575) | 3 | 18 | 9 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002N2517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 25 |  | 550 - 600 (575) | 3 | 18 | 9 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002N3017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 30 |  | 550 - 600 (575) | 3 | 18 | 9 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002N151010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002N201010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 20 |  | 550 - 600 (575) | 3 | 18 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002N251010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 25 |  | 550 - 600 (575) | 3 | 18 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002N301010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 30 |  | 550 - 600 (575) | 3 | 18 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002N401010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 40 |  | 550 - 600 (575) | 3 | 18 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC2002S251005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 25 |  | 200 | 3 | 100 | 17.5 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2002S301005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 30 |  | 200 | 3 | 100 | 17.5 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2002S401005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 40 |  | 200 | 3 | 100 | 17.5 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2002S4017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 40 |  | 200 | 3 | 100 | 25.3 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2002S6017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 200 | 3 | 100 | 25.3 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2082S251005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 25 |  | 208 | 3 | 100 | 16.7 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2082S301005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 30 |  | 208 | 3 | 100 | 16.7 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2082S401005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 40 |  | 208 | 3 | 100 | 16.7 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2082S4017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 40 |  | 208 | 3 | 100 | 24.2 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2082S6017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 208 | 3 | 100 | 24.2 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2402S201005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 20 |  | 220 - 240 (230) | 3 | 100 | 15.2 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2402S251005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 25 |  | 220 - 240 (230) | 3 | 100 | 15.2 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2402S301005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 30 |  | 220 - 240 (230) | 3 | 100 | 15.2 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2402S401005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 40 |  | 220 - 240 (230) | 3 | 100 | 15.2 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2402S3017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 30 |  | 220 - 240 (230) | 3 | 100 | 22 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC2402S4017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 40 |  | 220 - 240 (230) | 3 | 100 | 22 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBCC4802S1517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802S2017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 20 |  | 440 - 480 (460) | 3 | 35 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802S2517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 25 |  | 440 - 480 (460) | 3 | 35 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802S3017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 30 |  | 440 - 480 (460) | 3 | 35 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802S4017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 40 |  | 440 - 480 (460) | 3 | 35 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802S201010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 20 |  | 440 - 480 (460) | 3 | 35 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802S251010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 25 |  | 440 - 480 (460) | 3 | 35 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802S301010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 30 |  | 440 - 480 (460) | 3 | 35 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802S401010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 40 |  | 440 - 480 (460) | 3 | 35 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC6002S1517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 9 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002S2017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 20 |  | 550 - 600 (575) | 3 | 22 | 9 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002S2517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 25 |  | 550 - 600 (575) | 3 | 22 | 9 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002S3017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 30 |  | 550 - 600 (575) | 3 | 22 | 9 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002S151010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 15 |  | 550 - 600 (575) | 3 | 22 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002S201010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 20 |  | 550 - 600 (575) | 3 | 22 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002S251010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 25 |  | 550 - 600 (575) | 3 | 22 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002S301010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 30 |  | 550 - 600 (575) | 3 | 22 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002S401010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 40 |  | 550 - 600 (575) | 3 | 22 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC4802H1517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802H2017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 20 |  | 440 - 480 (460) | 3 | 65 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802H2517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 25 |  | 440 - 480 (460) | 3 | 65 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802H3017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 30 |  | 440 - 480 (460) | 3 | 65 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802H4017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 40 |  | 440 - 480 (460) | 3 | 65 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802H201010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 20 |  | 440 - 480 (460) | 3 | 65 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802H251010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 25 |  | 440 - 480 (460) | 3 | 65 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802H301010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 30 |  | 440 - 480 (460) | 3 | 65 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802H401010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 40 |  | 440 - 480 (460) | 3 | 65 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC6002H1517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 9 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002H2017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 20 |  | 550 - 600 (575) | 3 | 25 | 9 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002H2517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 25 |  | 550 - 600 (575) | 3 | 25 | 9 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002H3017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 30 |  | 550 - 600 (575) | 3 | 25 | 9 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002H151010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002H201010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 20 |  | 550 - 600 (575) | 3 | 25 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002H251010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 25 |  | 550 - 600 (575) | 3 | 25 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002H301010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 30 |  | 550 - 600 (575) | 3 | 25 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC6002H401010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 40 |  | 550 - 600 (575) | 3 | 25 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBCC4802L1517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802L2017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 20 |  | 440 - 480 (460) | 3 | 100 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802L2517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 25 |  | 440 - 480 (460) | 3 | 100 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802L3017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 30 |  | 440 - 480 (460) | 3 | 100 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802L4017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 40 |  | 440 - 480 (460) | 3 | 100 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802L201010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 20 |  | 440 - 480 (460) | 3 | 100 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802L251010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 25 |  | 440 - 480 (460) | 3 | 100 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802L301010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 30 |  | 440 - 480 (460) | 3 | 100 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCC4802L401010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 40 |  | 440 - 480 (460) | 3 | 100 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBCD2002N50J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 50 |  | 200 | 3 | 65 | 32.2 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2002N60J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 200 | 3 | 65 | 32.2 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2002N70J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 200 | 3 | 65 | 32.2 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2082N40J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 40 |  | 208 | 3 | 65 | 30.8 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2082N50J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 50 |  | 208 | 3 | 65 | 30.8 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2082N60J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 208 | 3 | 65 | 30.8 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2082N70J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 208 | 3 | 65 | 30.8 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2402N40J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 40 |  | 220 - 240 (230) | 3 | 65 | 28 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2402N50J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 50 |  | 220 - 240 (230) | 3 | 65 | 28 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2402N60J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 220 - 240 (230) | 3 | 65 | 28 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2402N70J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 220 - 240 (230) | 3 | 65 | 28 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2402N60J015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 220 - 240 (230) | 3 | 65 | 42 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2402N70J015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 220 - 240 (230) | 3 | 65 | 42 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD4802N30H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 30 |  | 440 - 480 (460) | 3 | 25 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802N40H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 40 |  | 440 - 480 (460) | 3 | 25 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802N50H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802N60H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802N70H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802N40H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 40 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802N50H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802N60H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802N70H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802N40J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 40 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802N50J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802N60J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802N70J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802N50J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802N60J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802N70J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD6002N30H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 30 |  | 550 - 600 (575) | 3 | 18 | 17 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002N40H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 40 |  | 550 - 600 (575) | 3 | 18 | 17 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002N50H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 17 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002N60H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 17 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002N30H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 30 |  | 550 - 600 (575) | 3 | 18 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002N40H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 40 |  | 550 - 600 (575) | 3 | 18 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002N50H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002N60H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002N70H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002N40H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 40 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002N50H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002N60H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002N70H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002N40J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 40 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBCD6002N50J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBCD6002N60J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBCD6002N70J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBCD2002S50J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 50 |  | 200 | 3 | 100 | 32.2 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2002S60J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 200 | 3 | 100 | 32.2 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2002S70J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 200 | 3 | 100 | 32.2 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2082S40J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 40 |  | 208 | 3 | 100 | 30.8 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2082S50J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 50 |  | 208 | 3 | 100 | 30.8 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2082S60J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 208 | 3 | 100 | 30.8 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2082S70J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 208 | 3 | 100 | 30.8 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2402S40J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 40 |  | 220 - 240 (230) | 3 | 100 | 28 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2402S50J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 50 |  | 220 - 240 (230) | 3 | 100 | 28 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2402S60J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 220 - 240 (230) | 3 | 100 | 28 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2402S70J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 220 - 240 (230) | 3 | 100 | 28 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2402S60J015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 220 - 240 (230) | 3 | 100 | 42 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD2402S70J015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 220 - 240 (230) | 3 | 100 | 42 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBCD4802S30H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 30 |  | 440 - 480 (460) | 3 | 35 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802S40H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 40 |  | 440 - 480 (460) | 3 | 35 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802S50H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802S60H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802S70H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802S40H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 40 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802S50H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802S60H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802S70H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802S40J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 40 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802S50J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802S60J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802S70J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802S50J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802S60J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802S70J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD6002S30H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 30 |  | 550 - 600 (575) | 3 | 22 | 17 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002S40H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 40 |  | 550 - 600 (575) | 3 | 22 | 17 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002S50H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 50 |  | 550 - 600 (575) | 3 | 22 | 17 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002S60H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 60 |  | 550 - 600 (575) | 3 | 22 | 17 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002S30H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 30 |  | 550 - 600 (575) | 3 | 22 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002S40H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 40 |  | 550 - 600 (575) | 3 | 22 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002S50H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 50 |  | 550 - 600 (575) | 3 | 22 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002S60H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 60 |  | 550 - 600 (575) | 3 | 22 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002S70H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 70 |  | 550 - 600 (575) | 3 | 22 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002S40H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 40 |  | 550 - 600 (575) | 3 | 22 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002S50H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 50 |  | 550 - 600 (575) | 3 | 22 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002S60H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 60 |  | 550 - 600 (575) | 3 | 22 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002S70H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 70 |  | 550 - 600 (575) | 3 | 22 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002S40J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 40 |  | 550 - 600 (575) | 3 | 22 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBCD6002S50J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 50 |  | 550 - 600 (575) | 3 | 22 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBCD6002S60J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 60 |  | 550 - 600 (575) | 3 | 22 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBCD6002S70J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 70 |  | 550 - 600 (575) | 3 | 22 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBCD4802H30H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 30 |  | 440 - 480 (460) | 3 | 65 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802H40H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 40 |  | 440 - 480 (460) | 3 | 65 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802H50H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802H60H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802H70H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802H40H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 40 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802H50H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802H60H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802H70H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802H40J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 40 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802H50J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802H60J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802H70J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802H50J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802H60J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802H70J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD6002H30H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 30 |  | 550 - 600 (575) | 3 | 25 | 17 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002H40H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 40 |  | 550 - 600 (575) | 3 | 25 | 17 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002H50H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 17 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002H60H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 17 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002H30H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 30 |  | 550 - 600 (575) | 3 | 25 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002H40H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 40 |  | 550 - 600 (575) | 3 | 25 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002H50H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002H60H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002H70H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002H40H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 40 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002H50H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002H60H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002H70H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBCD6002H40J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 40 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBCD6002H50J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBCD6002H60J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBCD6002H70J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBCD4802L30H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 30 |  | 440 - 480 (460) | 3 | 100 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802L40H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 40 |  | 440 - 480 (460) | 3 | 100 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802L50H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802L60H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802L70H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802L40H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 40 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802L50H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802L60H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802L70H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBCD4802L40J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 40 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802L50J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802L60J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802L70J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802L50J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802L60J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD4802L70J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBCD2002N501010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 50 |  | 200 | 3 | 65 | 32.2 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2002N601010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 200 | 3 | 65 | 32.2 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2002N701010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 200 | 3 | 65 | 32.2 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2082N401010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 40 |  | 208 | 3 | 65 | 30.8 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2082N501010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 50 |  | 208 | 3 | 65 | 30.8 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2082N601010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 208 | 3 | 65 | 30.8 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2082N701010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 208 | 3 | 65 | 30.8 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2402N401010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 40 |  | 220 - 240 (230) | 3 | 65 | 28 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2402N501010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 50 |  | 220 - 240 (230) | 3 | 65 | 28 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2402N601010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 220 - 240 (230) | 3 | 65 | 28 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2402N701010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 220 - 240 (230) | 3 | 65 | 28 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2402N601015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 220 - 240 (230) | 3 | 65 | 42 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2402N701015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 220 - 240 (230) | 3 | 65 | 42 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD4802N301015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 30 |  | 440 - 480 (460) | 3 | 25 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802N401015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 40 |  | 440 - 480 (460) | 3 | 25 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802N501015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802N601015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802N701015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802N401020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 40 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802N501020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802N601020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802N701020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802N501025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802N601025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802N701025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD6002N301015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 30 |  | 550 - 600 (575) | 3 | 18 | 17 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002N401015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 40 |  | 550 - 600 (575) | 3 | 18 | 17 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002N501015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 17 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002N601015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 17 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002N301020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 30 |  | 550 - 600 (575) | 3 | 18 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002N401020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 40 |  | 550 - 600 (575) | 3 | 18 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002N501020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002N601020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002N701020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002N401025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 40 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002N501025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002N601025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002N701025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD2002S501010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 50 |  | 200 | 3 | 100 | 32.2 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2002S601010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 200 | 3 | 100 | 32.2 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2002S701010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 200 | 3 | 100 | 32.2 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2082S401010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 40 |  | 208 | 3 | 100 | 30.8 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2082S501010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 50 |  | 208 | 3 | 100 | 30.8 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2082S601010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 208 | 3 | 100 | 30.8 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2082S701010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 208 | 3 | 100 | 30.8 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2402S401010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 40 |  | 220 - 240 (230) | 3 | 100 | 28 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2402S501010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 50 |  | 220 - 240 (230) | 3 | 100 | 28 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2402S601010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 220 - 240 (230) | 3 | 100 | 28 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2402S701010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 220 - 240 (230) | 3 | 100 | 28 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2402S601015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 220 - 240 (230) | 3 | 100 | 42 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD2402S701015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 220 - 240 (230) | 3 | 100 | 42 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBCD4802S301015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 30 |  | 440 - 480 (460) | 3 | 35 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802S401015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 40 |  | 440 - 480 (460) | 3 | 35 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802S501015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802S601015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802S701015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802S401020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 40 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802S501020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802S601020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802S701020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802S501025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802S601025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802S701025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD6002S301015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 30 |  | 550 - 600 (575) | 3 | 22 | 17 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002S401015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 40 |  | 550 - 600 (575) | 3 | 22 | 17 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002S501015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 50 |  | 550 - 600 (575) | 3 | 22 | 17 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002S601015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 60 |  | 550 - 600 (575) | 3 | 22 | 17 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002S301020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 30 |  | 550 - 600 (575) | 3 | 22 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002S401020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 40 |  | 550 - 600 (575) | 3 | 22 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002S501020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 50 |  | 550 - 600 (575) | 3 | 22 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002S601020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 60 |  | 550 - 600 (575) | 3 | 22 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002S701020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 70 |  | 550 - 600 (575) | 3 | 22 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002S401025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 40 |  | 550 - 600 (575) | 3 | 22 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002S501025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 50 |  | 550 - 600 (575) | 3 | 22 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002S601025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 60 |  | 550 - 600 (575) | 3 | 22 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002S701025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 70 |  | 550 - 600 (575) | 3 | 22 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD4802H301015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 30 |  | 440 - 480 (460) | 3 | 65 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802H401015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 40 |  | 440 - 480 (460) | 3 | 65 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802H501015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802H601015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802H701015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802H401020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 40 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802H501020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802H601020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802H701020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802H501025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802H601025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802H701025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD6002H301015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 30 |  | 550 - 600 (575) | 3 | 25 | 17 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002H401015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 40 |  | 550 - 600 (575) | 3 | 25 | 17 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002H501015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 17 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002H601015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 17 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002H301020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 30 |  | 550 - 600 (575) | 3 | 25 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002H401020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 40 |  | 550 - 600 (575) | 3 | 25 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002H501020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002H601020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002H701020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002H401025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 40 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002H501025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002H601025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD6002H701025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBCD4802L301015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 30 |  | 440 - 480 (460) | 3 | 100 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802L401015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 40 |  | 440 - 480 (460) | 3 | 100 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802L501015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802L601015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802L701015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802L401020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 40 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802L501020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802L601020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802L701020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802L501025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802L601025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBCD4802L701025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45 | [10 empty] | x
ABBCE2002N70L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002N80L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002N90L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 90 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002N100L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002N110L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002N125L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002N80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002N90L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 90 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002N100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002N110L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002N125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002N100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2002N110M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2002N125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2082N60L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082N70L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082N80L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082N90L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 90 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082N100L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082N110L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082N125L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082N80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082N90L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 90 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082N100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082N110L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082N125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082N100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2082N110M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2082N125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2402N70L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402N80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402N90L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 90 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402N100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402N110L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402N125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402N90L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 90 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402N100L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402N110L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402N125L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402N90M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 90 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2402N100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2402N110M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2402N125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2402N100M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2402N110M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2402N125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE4802N50L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802N60L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802N70L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802N80L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 80 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802N90L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 90 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802N100L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802N110L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802N125L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802N70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802N80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 80 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802N90L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 90 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802N100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802N110L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802N125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802N90L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 90 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802N100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802N110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802N125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802N90M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 90 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4802N100M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4802N110M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4802N125M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE6002N50K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002N60K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002N70K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002N80K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002N90K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 90 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002N100K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002N110K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002N125K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002N60L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002N70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002N80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002N90L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 90 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002N100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002N110L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002N125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002N70L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002N80L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002N90L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 90 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002N100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002N110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002N125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE2002S70L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002S80L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002S90L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 90 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002S100L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002S110L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002S125L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002S80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002S90L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 90 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002S100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002S110L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002S125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2002S100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2002S110M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2002S125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2082S60L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082S70L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082S80L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082S90L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 90 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082S100L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082S110L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082S125L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082S80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082S90L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 90 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082S100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082S110L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082S125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2082S100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2082S110M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2082S125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2402S70L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402S80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402S90L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 90 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402S100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402S110L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402S125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402S90L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 90 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402S100L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402S110L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402S125L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2402S90M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 90 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2402S100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2402S110M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2402S125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2402S100M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2402S110M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2402S125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE4802S50L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802S60L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802S70L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802S80L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 80 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802S90L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 90 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802S100L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802S110L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802S125L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802S70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802S80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 80 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802S90L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 90 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802S100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802S110L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802S125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802S90L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 90 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802S100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802S110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802S125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802S90M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 90 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4802S100M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4802S110M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4802S125M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE6002S50K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 50 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002S60K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 60 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002S70K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 70 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002S80K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 80 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002S90K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 90 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002S100K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002S110K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002S125K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002S60L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 60 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002S70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 70 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002S80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 80 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002S90L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 90 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002S100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002S110L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002S125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002S70L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 70 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002S80L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 80 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002S90L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 90 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002S100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002S110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002S125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE4802H50L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802H60L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802H70L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802H80L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 80 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802H90L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 90 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802H100L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802H110L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802H125L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802H70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802H80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 80 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802H90L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 90 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802H100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802H110L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802H125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802H90L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 90 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802H100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802H110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802H125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802H90M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 90 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4802H100M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4802H110M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4802H125M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE6002H50K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002H60K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002H70K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002H80K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002H90K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 90 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002H100K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002H110K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002H125K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6002H60L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002H70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002H80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002H90L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 90 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002H100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002H110L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002H125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002H70L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002H80L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002H90L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 90 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002H100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002H110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6002H125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE4802L50L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802L60L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802L70L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802L80L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 80 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802L90L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 90 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802L100L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802L110L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802L125L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802L70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802L80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 80 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802L90L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 90 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802L100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802L110L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802L125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802L90L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 90 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802L100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802L110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802L125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4802L90M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 90 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4802L100M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4802L110M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4802L125M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE2002N701015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002N801015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002N901015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 90 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002N1001015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002N1101015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002N1251015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002N801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002N901020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 90 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002N1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002N1101020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002N1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002N1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002N1101025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002N1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082N601015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082N701015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082N801015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082N901015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 90 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082N1001015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082N1101015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082N1251015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082N801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082N901020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 90 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082N1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082N1101020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082N1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082N1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082N1101025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082N1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402N701020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402N801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402N901020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 90 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402N1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402N1101020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402N1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402N901025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 90 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402N1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402N1101025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402N1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402N1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402N1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402N1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE4802N501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802N601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802N701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802N801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 80 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802N901030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 90 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802N1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802N1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802N1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802N701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802N801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 80 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802N901040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 90 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802N1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802N1101040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802N1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802N901050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 90 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802N1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802N1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802N1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE6002N501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N901030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 90 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N601040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N901040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 90 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N1101040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N701050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N801050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N901050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 90 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002N1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE2002S701015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002S801015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002S901015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 90 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002S1001015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002S1101015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002S1251015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002S801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002S901020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 90 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002S1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002S1101020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002S1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002S1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002S1101025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2002S1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082S601015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082S701015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082S801015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082S901015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 90 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082S1001015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082S1101015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082S1251015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082S801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082S901020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 90 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082S1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082S1101020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082S1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082S1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082S1101025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2082S1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402S701020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402S801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402S901020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 90 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402S1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402S1101020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402S1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402S901025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 90 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402S1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402S1101025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402S1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402S1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402S1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2402S1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE4802S501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802S601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802S701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802S801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 80 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802S901030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 90 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802S1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802S1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802S1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802S701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802S801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 80 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802S901040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 90 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802S1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802S1101040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802S1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802S901050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 90 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802S1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802S1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802S1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE6002S501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 50 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 60 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 70 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 80 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S901030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 90 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S601040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 60 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 70 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 80 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S901040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 90 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S1101040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S701050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 70 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S801050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 80 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S901050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 90 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002S1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE4802H501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802H601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802H701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802H801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 80 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802H901030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 90 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802H1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802H1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802H1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802H701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802H801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 80 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802H901040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 90 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802H1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802H1101040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802H1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802H901050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 90 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802H1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802H1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802H1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE6002H501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H901030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 90 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H601040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H901040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 90 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H1101040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H701050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H801050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H901050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 90 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6002H1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE4802L501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802L601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802L701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802L801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 80 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802L901030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 90 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802L1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802L1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802L1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802L701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802L801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 80 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802L901040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 90 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802L1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802L1101040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802L1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802L901050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 90 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802L1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802L1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4802L1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE2004N70L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 70 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004N80L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004N90L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 90 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004N100L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004N110L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004N125L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004N80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004N90L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 90 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004N100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004N110L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004N125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004N100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2004N110M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2004N125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2084N60L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 60 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084N70L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 70 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084N80L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084N90L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 90 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084N100L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084N110L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084N125L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084N80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084N90L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 90 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084N100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084N110L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084N125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084N100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2084N110M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2084N125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2404N70L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 70 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404N80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404N90L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 90 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404N100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404N110L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404N125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404N90L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 90 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404N100L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404N110L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404N125L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404N90M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 90 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2404N100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2404N110M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2404N125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2404N100M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2404N110M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2404N125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE4804N50L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804N60L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804N70L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804N80L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 80 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804N90L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 90 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804N100L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804N110L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804N125L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804N70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804N80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 80 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804N90L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 90 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804N100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804N110L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804N125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804N90L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 90 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804N100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804N110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804N125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804N90M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 90 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4804N100M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4804N110M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4804N125M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE6004N50K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004N60K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004N70K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004N80K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004N90K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 90 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004N100K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004N110K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004N125K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004N60L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004N70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004N80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004N90L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 90 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004N100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004N110L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004N125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004N70L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004N80L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004N90L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 90 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004N100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004N110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004N125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE2004S70L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 70 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004S80L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004S90L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 90 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004S100L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004S110L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004S125L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004S80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004S90L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 90 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004S100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004S110L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004S125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2004S100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2004S110M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2004S125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2084S60L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 60 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084S70L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 70 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084S80L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084S90L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 90 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084S100L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084S110L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084S125L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084S80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084S90L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 90 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084S100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084S110L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084S125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2084S100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2084S110M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2084S125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2404S70L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 70 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404S80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404S90L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 90 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404S100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404S110L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404S125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404S90L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 90 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404S100L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404S110L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404S125L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBCE2404S90M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 90 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2404S100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2404S110M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2404S125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2404S100M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2404S110M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE2404S125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBCE4804S50L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804S60L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804S70L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804S80L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 80 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804S90L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 90 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804S100L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804S110L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804S125L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804S70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804S80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 80 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804S90L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 90 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804S100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804S110L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804S125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804S90L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 90 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804S100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804S110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804S125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804S90M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 90 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4804S100M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4804S110M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4804S125M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE6004S50K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 50 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004S60K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 60 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004S70K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 70 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004S80K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 80 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004S90K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 90 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004S100K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004S110K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004S125K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004S60L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 60 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004S70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 70 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004S80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 80 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004S90L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 90 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004S100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004S110L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004S125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004S70L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 70 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004S80L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 80 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004S90L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 90 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004S100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004S110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004S125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE4804H50L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804H60L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804H70L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804H80L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 80 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804H90L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 90 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804H100L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804H110L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804H125L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804H70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804H80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 80 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804H90L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 90 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804H100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804H110L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804H125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804H90L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 90 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804H100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804H110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804H125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804H90M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 90 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4804H100M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4804H110M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4804H125M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE6004H50K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004H60K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004H70K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004H80K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004H90K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 90 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004H100K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004H110K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004H125K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBCE6004H60L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004H70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004H80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004H90L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 90 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004H100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004H110L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004H125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004H70L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004H80L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004H90L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 90 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004H100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004H110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE6004H125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBCE4804L50L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804L60L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804L70L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804L80L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 80 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804L90L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 90 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804L100L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804L110L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804L125L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804L70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804L80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 80 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804L90L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 90 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804L100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804L110L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804L125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804L90L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 90 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804L100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804L110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804L125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBCE4804L90M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 90 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4804L100M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4804L110M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE4804L125M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBCE2004N701015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 70 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004N801015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004N901015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 90 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004N1001015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004N1101015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004N1251015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004N801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004N901020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 90 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004N1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004N1101020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004N1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004N1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004N1101025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004N1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084N601015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 60 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084N701015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 70 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084N801015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084N901015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 90 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084N1001015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084N1101015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084N1251015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084N801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084N901020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 90 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084N1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084N1101020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084N1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084N1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084N1101025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084N1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404N701020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 70 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404N801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404N901020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 90 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404N1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404N1101020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404N1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404N901025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 90 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404N1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404N1101025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404N1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404N1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404N1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404N1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE4804N501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804N601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804N701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804N801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 80 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804N901030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 90 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804N1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804N1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804N1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804N701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804N801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 80 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804N901040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 90 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804N1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804N1101040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804N1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804N901050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 90 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804N1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804N1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804N1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE6004N501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N901030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 90 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N601040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N901040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 90 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N1101040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N701050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N801050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N901050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 90 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004N1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE2004S701015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 70 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004S801015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004S901015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 90 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004S1001015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004S1101015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004S1251015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004S801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004S901020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 90 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004S1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004S1101020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004S1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004S1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004S1101025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2004S1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084S601015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 60 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084S701015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 70 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084S801015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084S901015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 90 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084S1001015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084S1101015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084S1251015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084S801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084S901020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 90 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084S1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084S1101020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084S1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084S1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084S1101025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2084S1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404S701020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 70 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404S801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404S901020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 90 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404S1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404S1101020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404S1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404S901025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 90 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404S1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404S1101025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404S1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404S1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404S1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE2404S1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBCE4804S501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804S601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804S701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804S801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 80 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804S901030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 90 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804S1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804S1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804S1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804S701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804S801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 80 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804S901040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 90 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804S1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804S1101040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804S1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804S901050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 90 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804S1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804S1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804S1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE6004S501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 50 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 60 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 70 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 80 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S901030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 90 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S601040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 60 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 70 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 80 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S901040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 90 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S1101040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S701050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 70 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S801050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 80 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S901050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 90 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004S1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE4804H501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804H601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804H701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804H801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 80 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804H901030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 90 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804H1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804H1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804H1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804H701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804H801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 80 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804H901040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 90 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804H1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804H1101040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804H1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804H901050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 90 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804H1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804H1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804H1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE6004H501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H901030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 90 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H601040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H901040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 90 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H1101040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H701050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H801050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H901050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 90 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE6004H1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBCE4804L501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804L601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804L701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804L801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 80 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804L901030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 90 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804L1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804L1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804L1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804L701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804L801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 80 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804L901040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 90 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804L1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804L1101040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804L1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804L901050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 90 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804L1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804L1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCE4804L1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBCF2004N125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2004N150M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2004N175M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2004N200M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2004N150M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 200 | 3 | 65 | 120 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2004N175M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 200 | 3 | 65 | 120 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2004N200M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 200 | 3 | 65 | 120 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2084N110M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2084N125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2084N150M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2084N175M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2084N200M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2084N150M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 208 | 3 | 65 | 114 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2084N175M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 208 | 3 | 65 | 114 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2084N200M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 208 | 3 | 65 | 114 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2404N150M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 220 - 240 (230) | 3 | 65 | 104 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2404N175M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 220 - 240 (230) | 3 | 65 | 104 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2404N200M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 220 - 240 (230) | 3 | 65 | 104 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2404N175M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 220 - 240 (230) | 3 | 65 | 130 | 50 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2404N200M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 220 - 240 (230) | 3 | 65 | 130 | 50 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF4804N100M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804N110M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804N125M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804N150M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 150 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804N175M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 175 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804N200M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 200 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804N125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804N150M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 150 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804N175M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 175 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804N200M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 200 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804N175M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 175 |  | 440 - 480 (460) | 3 | 25 | 124 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804N200M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 200 |  | 440 - 480 (460) | 3 | 25 | 124 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF6004N100L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6004N110L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6004N125L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6004N150L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 150 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6004N175L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 175 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6004N200L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 200 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6004N100M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004N110M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004N125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004N150M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 150 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004N175M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 175 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004N200M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 200 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004N125M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004N150M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 150 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004N175M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 175 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004N200M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 200 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF2004S125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2004S150M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2004S175M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2004S200M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2004S150M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 200 | 3 | 100 | 120 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2004S175M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 200 | 3 | 100 | 120 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2004S200M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 200 | 3 | 100 | 120 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2084S110M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2084S125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2084S150M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2084S175M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2084S200M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2084S150M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 208 | 3 | 100 | 114 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2084S175M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 208 | 3 | 100 | 114 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2084S200M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 208 | 3 | 100 | 114 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2404S150M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 220 - 240 (230) | 3 | 100 | 104 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2404S175M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 220 - 240 (230) | 3 | 100 | 104 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2404S200M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 220 - 240 (230) | 3 | 100 | 104 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2404S175M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 220 - 240 (230) | 3 | 100 | 130 | 50 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2404S200M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 220 - 240 (230) | 3 | 100 | 130 | 50 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF4804S100M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804S110M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804S125M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804S150M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 150 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804S175M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 175 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804S200M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 200 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804S125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804S150M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 150 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804S175M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 175 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804S200M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 200 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804S175M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 175 |  | 440 - 480 (460) | 3 | 35 | 124 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804S200M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 200 |  | 440 - 480 (460) | 3 | 35 | 124 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF6004S100L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6004S110L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6004S125L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6004S150L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 150 |  | 550 - 600 (575) | 3 | 22 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6004S175L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 175 |  | 550 - 600 (575) | 3 | 22 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6004S200L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 200 |  | 550 - 600 (575) | 3 | 22 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6004S100M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004S110M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004S125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004S150M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 150 |  | 550 - 600 (575) | 3 | 22 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004S175M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 175 |  | 550 - 600 (575) | 3 | 22 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004S200M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 200 |  | 550 - 600 (575) | 3 | 22 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004S125M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004S150M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 150 |  | 550 - 600 (575) | 3 | 22 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004S175M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 175 |  | 550 - 600 (575) | 3 | 22 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004S200M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 200 |  | 550 - 600 (575) | 3 | 22 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF4804H100M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804H110M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804H125M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804H150M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 150 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804H175M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 175 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804H200M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 200 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804H125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804H150M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 150 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804H175M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 175 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804H200M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 200 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804H175M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 175 |  | 440 - 480 (460) | 3 | 65 | 124 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804H200M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 200 |  | 440 - 480 (460) | 3 | 65 | 124 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF6004H100L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6004H110L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6004H125L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6004H150L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 150 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6004H175L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 175 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6004H200L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 200 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6004H100M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004H110M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004H125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004H150M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 150 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004H175M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 175 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004H200M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 200 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004H125M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004H150M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 150 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004H175M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 175 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6004H200M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 200 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF4804L100M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804L110M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804L125M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804L150M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 150 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804L175M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 175 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804L200M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 200 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804L125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804L150M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 150 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804L175M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 175 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804L200M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 200 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804L175M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 175 |  | 440 - 480 (460) | 3 | 100 | 124 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4804L200M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 200 |  | 440 - 480 (460) | 3 | 100 | 124 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF2004N1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2004N1501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2004N1751030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2004N2001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2004N1501040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 200 | 3 | 65 | 120 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2004N1751040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 200 | 3 | 65 | 120 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2004N2001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 200 | 3 | 65 | 120 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2084N1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2084N1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2084N1501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2084N1751030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2084N2001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2084N1501040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 208 | 3 | 65 | 114 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2084N1751040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 208 | 3 | 65 | 114 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2084N2001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 208 | 3 | 65 | 114 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2404N1501040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 220 - 240 (230) | 3 | 65 | 104 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2404N1751040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 220 - 240 (230) | 3 | 65 | 104 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2404N2001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 220 - 240 (230) | 3 | 65 | 104 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2404N1751050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 220 - 240 (230) | 3 | 65 | 130 | 50 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2404N2001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 220 - 240 (230) | 3 | 65 | 130 | 50 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF4804N1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804N1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804N1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804N1501060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 150 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804N1751060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 175 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804N2001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 200 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804N1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804N1501075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 150 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804N1751075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 175 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804N2001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 200 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804N1751100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 175 |  | 440 - 480 (460) | 3 | 25 | 124 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804N2001100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 480 | 3 | 25 | 200 |  | 440 - 480 (460) | 3 | 25 | 124 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF6004N1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004N1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004N1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004N1501060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 150 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004N1751060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 175 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004N2001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 200 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004N1001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004N1101075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004N1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004N1501075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 150 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004N1751075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 175 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004N2001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 200 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004N1251100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004N1501100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 150 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004N1751100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 175 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004N2001100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4N*3* | 600 | 3 | 18 | 200 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF2004S1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2004S1501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2004S1751030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2004S2001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2004S1501040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 200 | 3 | 100 | 120 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2004S1751040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 200 | 3 | 100 | 120 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2004S2001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 200 | 3 | 100 | 120 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2084S1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2084S1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2084S1501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2084S1751030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2084S2001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2084S1501040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 208 | 3 | 100 | 114 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2084S1751040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 208 | 3 | 100 | 114 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2084S2001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 208 | 3 | 100 | 114 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2404S1501040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 220 - 240 (230) | 3 | 100 | 104 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2404S1751040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 220 - 240 (230) | 3 | 100 | 104 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2404S2001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 220 - 240 (230) | 3 | 100 | 104 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2404S1751050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 220 - 240 (230) | 3 | 100 | 130 | 50 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2404S2001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 220 - 240 (230) | 3 | 100 | 130 | 50 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF4804S1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804S1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804S1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804S1501060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 150 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804S1751060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 175 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804S2001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 200 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804S1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804S1501075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 150 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804S1751075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 175 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804S2001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 200 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804S1751100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 175 |  | 440 - 480 (460) | 3 | 35 | 124 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804S2001100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 480 | 3 | 35 | 200 |  | 440 - 480 (460) | 3 | 35 | 124 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF6004S1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004S1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004S1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004S1501060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 150 |  | 550 - 600 (575) | 3 | 22 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004S1751060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 175 |  | 550 - 600 (575) | 3 | 22 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004S2001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 200 |  | 550 - 600 (575) | 3 | 22 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004S1001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004S1101075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004S1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004S1501075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 150 |  | 550 - 600 (575) | 3 | 22 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004S1751075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 175 |  | 550 - 600 (575) | 3 | 22 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004S2001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 200 |  | 550 - 600 (575) | 3 | 22 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004S1251100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004S1501100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 150 |  | 550 - 600 (575) | 3 | 22 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004S1751100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 175 |  | 550 - 600 (575) | 3 | 22 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004S2001100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4S*3* | 600 | 3 | 22 | 200 |  | 550 - 600 (575) | 3 | 22 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF4804H1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804H1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804H1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804H1501060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 150 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804H1751060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 175 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804H2001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 200 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804H1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804H1501075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 150 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804H1751075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 175 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804H2001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 200 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804H1751100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 175 |  | 440 - 480 (460) | 3 | 65 | 124 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804H2001100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 480 | 3 | 65 | 200 |  | 440 - 480 (460) | 3 | 65 | 124 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF6004H1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004H1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004H1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004H1501060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 150 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004H1751060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 175 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004H2001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 200 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004H1001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004H1101075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004H1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004H1501075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 150 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004H1751075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 175 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004H2001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 200 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004H1251100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004H1501100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 150 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004H1751100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 175 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6004H2001100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4H*3* | 600 | 3 | 25 | 200 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF4804L1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804L1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804L1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804L1501060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 150 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804L1751060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 175 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804L2001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 200 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804L1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804L1501075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 150 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804L1751075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 175 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804L2001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 200 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804L1751100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 175 |  | 440 - 480 (460) | 3 | 100 | 124 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4804L2001100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT4L*3* | 480 | 3 | 100 | 200 |  | 440 - 480 (460) | 3 | 100 | 124 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF2002N125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2082N110M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2082N125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF4802N100M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4802N110M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4802N125M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4802N125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF6002N100L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6002N110L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6002N125L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6002N100M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6002N110M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6002N125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6002N125M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF2002S125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2082S110M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF2082S125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBCF4802S100M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4802S110M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4802S125M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4802S125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF6002S100L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6002S110L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6002S125L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6002S100M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6002S110M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6002S125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6002S125M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF4802H100M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4802H110M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4802H125M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4802H125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF6002H100L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6002H110L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6002H125L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBCF6002H100M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6002H110M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6002H125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF6002H125M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBCF4802L100M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4802L110M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4802L125M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF4802L125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBCF2002N1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2082N1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2082N1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF4802N1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4802N1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4802N1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4802N1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF6002N1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6002N1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6002N1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6002N1001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6002N1101075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6002N1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6002N1251100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2N*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF2002S1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2082S1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF2082S1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBCF4802S1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4802S1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4802S1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4802S1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF6002S1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6002S1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6002S1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6002S1001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 100 |  | 550 - 600 (575) | 3 | 22 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6002S1101075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 110 |  | 550 - 600 (575) | 3 | 22 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6002S1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6002S1251100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2S*3* | 600 | 3 | 22 | 125 |  | 550 - 600 (575) | 3 | 22 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF4802H1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4802H1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4802H1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4802H1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF6002H1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6002H1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6002H1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6002H1001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6002H1101075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6002H1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF6002H1251100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBCF4802L1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4802L1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4802L1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBCF4802L1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | C | CB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application.

## Bkr_Sizing (hidden)
|  |  | INDEX | Min. | 0.33 | 0.9 |  |  |  |  | 20 | 1.035 | 1.125 | 1.575 | 30 | 1.0311 | 0.94862 | 0.67758 | 30 | 14 | 1.125 |  |  | 15 | 5.4 | 0.68627 | 9 | 3.6 | 43 | 0 | 182 | 0 | XT2 | 125
|  |  |  | Max. | 400 | 480 |  |  |  |  | 375 | 552 | 600 | 840 | 800 | 28.9855 | 26.6667 | 19.0476 | 1200 | 2 x 350 | 600 |  |  | 800 | 2880 | 1.5347 | 4800 | 1440 | 2440 | 47.7778 | 8705 | 202.2222 | XT7 | 800
|  |  |  | Avg. | 37.9233 | 65.7146 |  |  |  |  | 124.5382 | 75.5718 | 82.1433 | 115.0006 | 142.6115 | 2.6539 | 2.4416 | 1.744 | 138.4395 | 22.3216 | 82.1433 |  |  | 114.934 | 394.2879 | 0.97552 | 657.1465 | 229.5561 | 341.0452 | 6.3927 | 1299.7452 | 26.6694 |  | 183.5191
[12 empty] | 1.15 | 1.25 | 1.75 | [6 empty] | 1.25 |  | Spectra breaker | Spectra breaker | 6 |  | 10 |  | Spectra Instantaneous |  |  |  | ABB Breaker | ABB Breaker | ABB Breaker | 1 |  | 10
Count | NEMA Size | Continuous Current | Volts | Phase | HP | NEC FLC | Max. FLC | LRA (UL508) | Contactor Catalog Number | Wire Size Range (75 Deg) AWG | Torque (Pounds-Inches) | Input Disconnect Minimum Rating (Ref. UL508A, 30.2.2 (b).2)<-115% Motor FLA)in Amps | 125% of FLA | 175% of FLA | Disconnect Sizing | % Against Minimum disconnect rating (115%) | % Against disconnect rating (125%) | % Against Maximum disconnect rating (175%) | Fuse Clip Size | Min. Power Cable AWG/kcmil (Ref. UL-508, Table 43.2) 75 Deg. C (Based on 1.2x FLC) | CB Frame Minimum Rating (Ref. UL508A, 30.2.1:<-80% FLA)in Amps | Breaker Catalog | CB Frame Size Designation | CB Rating Plug/Trip (in Amps) | 6x FLC | Percentage of 6x FLC against LRA | 10x FLC | <= 100 (4x) >100 (3x) | Min (~3 times) | Percentage of Min. against FLC | Max (~ 12 times) | Percentage of Max. against FLC | CB Frame Size Designation | CB Frame Size Amp Rating (in Amps) | Breaker Ampere Rating | Min (~1 times) | Percentage of Min. against FLC | Max (~ 10 times) | Percentage of Max. against FLC | Check on Min. (Spectra vs XT) | Check on Max. (Spectra vs XT) | Check on 10x FLA | Difference
1 | Size-00 | 9 | 200 | 3 | 0.5 | 2.5 | 6.9 | 23 | 305A002 | 14 - 8 | 20 | 2.875 | 3.125 | 4.375 | 30 | 10.4348 | 9.6 | 6.8571 | 30 | 14 | 3.125 |  | SE | 15 | 15 | 1.5333 | 25 | 10 | 43 | 17.2 | 182 | 72.8 | XT2 | 125 | 25 | 25 | 10 | 250 | 100 | TRUE | TRUE | TRUE | 27.2
2 | Size-00 | 9 | 200 | 3 | 0.75 | 3.7 |  | 28.8 | 305A002 | 14 - 8 | 20 | 4.255 | 4.625 | 6.475 | 30 | 7.0505 | 6.4865 | 4.6332 | 30 | 14 | 4.625 |  | SE | 15 | 22.2 | 1.2973 | 37 | 14.8 | 43 | 11.6216 | 182 | 49.1892 | XT2 | 125 | 25 | 25 | 6.7568 | 250 | 67.5676 | TRUE | TRUE | TRUE | 18.3784
3 | Size-00 | 9 | 200 | 3 | 1 | 4.8 |  | 34.5 | 305A002 | 14 - 8 | 20 | 5.52 | 6 | 8.4 | 30 | 5.4348 | 5 | 3.5714 | 30 | 14 | 6 |  | SE | 15 | 28.8 | 1.1979 | 48 | 19.2 | 43 | 8.9583 | 182 | 37.9167 | XT2 | 125 | 25 | 25 | 5.2083 | 250 | 52.0833 | TRUE | TRUE | TRUE | 14.1667
4 | Size-00 | 9 | 200 | 3 | 1.5 | 6.9 |  | 46 | 305A002 | 14 - 8 | 20 | 7.935 | 8.625 | 12.075 | 30 | 3.7807 | 3.4783 | 2.4845 | 30 | 14 | 8.625 |  | SE | 15 | 41.4 | 1.1111 | 69 | 27.6 | 43 | 6.2319 | 182 | 26.3768 | XT2 | 125 | 25 | 25 | 3.6232 | 250 | 36.2319 | TRUE | TRUE | TRUE | 9.8551
5 | Size-00 | 9 | 208 | 3 | 0.5 | 2.4 |  | 22.1 | 305A002 | 14 - 8 | 20 | 2.76 | 3 | 4.2 | 30 | 10.8696 | 10 | 7.1429 | 30 | 14 | 3 |  | SE | 15 | 14.4 | 1.5347 | 24 | 9.6 | 43 | 17.9167 | 182 | 75.8333 | XT2 | 125 | 25 | 25 | 10.4167 | 250 | 104.1667 | TRUE | TRUE | TRUE | 28.3333
6 | Size-00 | 9 | 208 | 3 | 0.75 | 3.5 |  | 27.6 | 305A002 | 14 - 8 | 20 | 4.025 | 4.375 | 6.125 | 30 | 7.4534 | 6.8571 | 4.898 | 30 | 14 | 4.375 |  | SE | 15 | 21 | 1.3143 | 35 | 14 | 43 | 12.2857 | 182 | 52 | XT2 | 125 | 25 | 25 | 7.1429 | 250 | 71.4286 | TRUE | TRUE | TRUE | 19.4286
7 | Size-00 | 9 | 208 | 3 | 1 | 4.6 |  | 33 | 305A002 | 14 - 8 | 20 | 5.29 | 5.75 | 8.05 | 30 | 5.6711 | 5.2174 | 3.7267 | 30 | 14 | 5.75 |  | SE | 15 | 27.6 | 1.1957 | 46 | 18.4 | 43 | 9.3478 | 182 | 39.5652 | XT2 | 125 | 25 | 25 | 5.4348 | 250 | 54.3478 | TRUE | TRUE | TRUE | 14.7826
8 | Size-00 | 9 | 208 | 3 | 1.5 | 6.6 |  | 44 | 305A002 | 14 - 8 | 20 | 7.59 | 8.25 | 11.55 | 30 | 3.9526 | 3.6364 | 2.5974 | 30 | 14 | 8.25 |  | SE | 15 | 39.6 | 1.1111 | 66 | 26.4 | 43 | 6.5152 | 182 | 27.5758 | XT2 | 125 | 25 | 25 | 3.7879 | 250 | 37.8788 | TRUE | TRUE | TRUE | 10.303
9 | Size-00 | 9 | 220 - 240 (230) | 3 | 0.5 | 2.2 |  | 20 | 305A002 | 14 - 8 | 20 | 2.53 | 2.75 | 3.85 | 30 | 11.8577 | 10.9091 | 7.7922 | 30 | 14 | 2.75 |  | SE | 15 | 13.2 | 1.5152 | 22 | 8.8 | 43 | 19.5455 | 182 | 82.7273 | XT2 | 125 | 25 | 25 | 11.3636 | 250 | 113.6364 | TRUE | TRUE | TRUE | 30.9091
10 | Size-00 | 9 | 220 - 240 (230) | 3 | 0.75 | 3.2 |  | 25 | 305A002 | 14 - 8 | 20 | 3.68 | 4 | 5.6 | 30 | 8.1522 | 7.5 | 5.3571 | 30 | 14 | 4 |  | SE | 15 | 19.2 | 1.3021 | 32 | 12.8 | 43 | 13.4375 | 182 | 56.875 | XT2 | 125 | 25 | 25 | 7.8125 | 250 | 78.125 | TRUE | TRUE | TRUE | 21.25
11 | Size-00 | 9 | 220 - 240 (230) | 3 | 1 | 4.2 |  | 30 | 305A002 | 14 - 8 | 20 | 4.83 | 5.25 | 7.35 | 30 | 6.2112 | 5.7143 | 4.0816 | 30 | 14 | 5.25 |  | SE | 15 | 25.2 | 1.1905 | 42 | 16.8 | 43 | 10.2381 | 182 | 43.3333 | XT2 | 125 | 25 | 25 | 5.9524 | 250 | 59.5238 | TRUE | TRUE | TRUE | 16.1905
12 | Size-00 | 9 | 220 - 240 (230) | 3 | 1.5 | 6 |  | 40 | 305A002 | 14 - 8 | 20 | 6.9 | 7.5 | 10.5 | 30 | 4.3478 | 4 | 2.8571 | 30 | 14 | 7.5 |  | SE | 15 | 36 | 1.1111 | 60 | 24 | 43 | 7.1667 | 182 | 30.3333 | XT2 | 125 | 25 | 25 | 4.1667 | 250 | 41.6667 | TRUE | TRUE | TRUE | 11.3333
13 | Size-00 | 9 | 440 - 480 (460) | 3 | 0.5 | 1.1 |  | 10 | 305A002 | 14 - 8 | 20 | 1.265 | 1.375 | 1.925 | 30 | 23.7154 | 21.8182 | 15.5844 | 30 | 14 | 1.375 |  | SE | 15 | 6.6 | 1.5152 | 11 | 4.4 | 43 | 39.0909 | 182 | 165.4545 | XT2 | 125 | 25 | 25 | 22.7273 | 250 | 227.2727 | TRUE | TRUE | TRUE | 61.8182
14 | Size-00 | 9 | 440 - 480 (460) | 3 | 0.75 | 1.6 |  | 12.5 | 305A002 | 14 - 8 | 20 | 1.84 | 2 | 2.8 | 30 | 16.3043 | 15 | 10.7143 | 30 | 14 | 2 |  | SE | 15 | 9.6 | 1.3021 | 16 | 6.4 | 43 | 26.875 | 182 | 113.75 | XT2 | 125 | 25 | 25 | 15.625 | 250 | 156.25 | TRUE | TRUE | TRUE | 42.5
15 | Size-00 | 9 | 440 - 480 (460) | 3 | 1 | 2.1 |  | 15 | 305A002 | 14 - 8 | 20 | 2.415 | 2.625 | 3.675 | 30 | 12.4224 | 11.4286 | 8.1633 | 30 | 14 | 2.625 |  | SE | 15 | 12.6 | 1.1905 | 21 | 8.4 | 43 | 20.4762 | 182 | 86.6667 | XT2 | 125 | 25 | 25 | 11.9048 | 250 | 119.0476 | TRUE | TRUE | TRUE | 32.381
16 | Size-00 | 9 | 440 - 480 (460) | 3 | 1.5 | 3 |  | 20 | 305A002 | 14 - 8 | 20 | 3.45 | 3.75 | 5.25 | 30 | 8.6957 | 8 | 5.7143 | 30 | 14 | 3.75 |  | SE | 15 | 18 | 1.1111 | 30 | 12 | 43 | 14.3333 | 182 | 60.6667 | XT2 | 125 | 25 | 25 | 8.3333 | 250 | 83.3333 | TRUE | TRUE | TRUE | 22.6667
17 | Size-00 | 9 | 440 - 480 (460) | 3 | 2 | 3.4 |  | 25 | 305A002 | 14 - 8 | 20 | 3.91 | 4.25 | 5.95 | 30 | 7.6726 | 7.0588 | 5.042 | 30 | 14 | 4.25 |  | SE | 15 | 20.4 | 1.2255 | 34 | 13.6 | 43 | 12.6471 | 182 | 53.5294 | XT2 | 125 | 25 | 25 | 7.3529 | 250 | 73.5294 | TRUE | TRUE | TRUE | 20
18 | Size-00 | 9 | 550 - 600 (575) | 3 | 0.5 | 0.9 |  | 8 | 305A002 | 14 - 8 | 20 | 1.035 | 1.125 | 1.575 | 30 | 28.9855 | 26.6667 | 19.0476 | 30 | 14 | 1.125 |  | SE | 15 | 5.4 | 1.4815 | 9 | 3.6 | 43 | 47.7778 | 182 | 202.2222 | XT2 | 125 | 25 | 25 | 27.7778 | 250 | 277.7778 | TRUE | TRUE | TRUE | 75.5556
19 | Size-00 | 9 | 550 - 600 (575) | 3 | 0.75 | 1.3 |  | 10 | 305A002 | 14 - 8 | 20 | 1.495 | 1.625 | 2.275 | 30 | 20.0669 | 18.4615 | 13.1868 | 30 | 14 | 1.625 |  | SE | 15 | 7.8 | 1.2821 | 13 | 5.2 | 43 | 33.0769 | 182 | 140 | XT2 | 125 | 25 | 25 | 19.2308 | 250 | 192.3077 | TRUE | TRUE | TRUE | 52.3077
20 | Size-00 | 9 | 550 - 600 (575) | 3 | 1 | 1.7 |  | 12 | 305A002 | 14 - 8 | 20 | 1.955 | 2.125 | 2.975 | 30 | 15.3453 | 14.1176 | 10.084 | 30 | 14 | 2.125 |  | SE | 15 | 10.2 | 1.1765 | 17 | 6.8 | 43 | 25.2941 | 182 | 107.0588 | XT2 | 125 | 25 | 25 | 14.7059 | 250 | 147.0588 | TRUE | TRUE | TRUE | 40
21 | Size-00 | 9 | 550 - 600 (575) | 3 | 1.5 | 2.4 |  | 16 | 305A002 | 14 - 8 | 20 | 2.76 | 3 | 4.2 | 30 | 10.8696 | 10 | 7.1429 | 30 | 14 | 3 |  | SE | 15 | 14.4 | 1.1111 | 24 | 9.6 | 43 | 17.9167 | 182 | 75.8333 | XT2 | 125 | 25 | 25 | 10.4167 | 250 | 104.1667 | TRUE | TRUE | TRUE | 28.3333
22 | Size-00 | 9 | 550 - 600 (575) | 3 | 2 | 2.7 |  | 20 | 305A002 | 14 - 8 | 20 | 3.105 | 3.375 | 4.725 | 30 | 9.6618 | 8.8889 | 6.3492 | 30 | 14 | 3.375 |  | SE | 15 | 16.2 | 1.2346 | 27 | 10.8 | 43 | 15.9259 | 182 | 67.4074 | XT2 | 125 | 25 | 25 | 9.2593 | 250 | 92.5926 | TRUE | TRUE | TRUE | 25.1852
23 | Size-0 | 18 | 200 | 3 | 2 | 7.8 | 11 | 57.5 | 305B002 | 14 - 8 | 20 | 8.97 | 9.75 | 13.65 | 30 | 3.3445 | 3.0769 | 2.1978 | 30 | 14 | 9.75 |  | SE | 15 | 46.8 | 1.2286 | 78 | 31.2 | 43 | 5.5128 | 182 | 23.3333 | XT2 | 125 | 25 | 25 | 3.2051 | 250 | 32.0513 | TRUE | TRUE | TRUE | 8.7179
23.1 | Size-0 | 18 | 200 | 3 | 2 | 7.8 | 17.5 | 57.5 | 305B002 | 14 - 8 | 20 | 8.97 | 9.75 | 13.65 | 30 | 3.3445 | 3.0769 | 2.1978 | 30 | 14 | 9.75 |  | SE | 20 | 46.8 | 1.2286 | 78 | 31.2 | 58 | 7.4359 | 254 | 32.5641 | XT2 | 125 | 25 | 25 | 3.2051 | 250 | 32.0513 | TRUE | FALSE | TRUE | -0.51282
24 | Size-0 | 18 | 200 | 3 | 3 | 11 |  | 73.6 | 305B002 | 14 - 8 | 20 | 12.65 | 13.75 | 19.25 | 30 | 2.3715 | 2.1818 | 1.5584 | 30 | 14 | 13.75 |  | SE | 15 | 66 | 1.1152 | 110 | 44 | 43 | 3.9091 | 182 | 16.5455 | XT2 | 125 | 25 | 25 | 2.2727 | 250 | 22.7273 | TRUE | TRUE | TRUE | 6.1818
24.1 | Size-0 | 18 | 200 | 3 | 3 | 11 |  | 73.6 | 305B002 | 14 - 8 | 20 | 12.65 | 13.75 | 19.25 | 30 | 2.3715 | 2.1818 | 1.5584 | 30 | 14 | 13.75 |  | SE | 20 | 66 | 1.1152 | 110 | 44 | 58 | 5.2727 | 254 | 23.0909 | XT2 | 125 | 25 | 25 | 2.2727 | 250 | 22.7273 | TRUE | FALSE | TRUE | -0.36364
25 | Size-0 | 18 | 208 | 3 | 2 | 7.5 |  | 55 | 305B002 | 14 - 8 | 20 | 8.625 | 9.375 | 13.125 | 30 | 3.4783 | 3.2 | 2.2857 | 30 | 14 | 9.375 |  | SE | 15 | 45 | 1.2222 | 75 | 30 | 43 | 5.7333 | 182 | 24.2667 | XT2 | 125 | 25 | 25 | 3.3333 | 250 | 33.3333 | TRUE | TRUE | TRUE | 9.0667
25.1 | Size-0 | 18 | 208 | 3 | 2 | 7.5 |  | 55 | 305B002 | 14 - 8 | 20 | 8.625 | 9.375 | 13.125 | 30 | 3.4783 | 3.2 | 2.2857 | 30 | 14 | 9.375 |  | SE | 20 | 45 | 1.2222 | 75 | 30 | 58 | 7.7333 | 254 | 33.8667 | XT2 | 125 | 25 | 25 | 3.3333 | 250 | 33.3333 | TRUE | FALSE | TRUE | -0.53333
26 | Size-0 | 18 | 208 | 3 | 3 | 10.6 |  | 71 | 305B002 | 14 - 8 | 20 | 12.19 | 13.25 | 18.55 | 30 | 2.461 | 2.2642 | 1.6173 | 30 | 14 | 13.25 |  | SE | 15 | 63.6 | 1.1164 | 106 | 42.4 | 43 | 4.0566 | 182 | 17.1698 | XT2 | 125 | 25 | 25 | 2.3585 | 250 | 23.5849 | TRUE | TRUE | TRUE | 6.4151
26.1 | Size-0 | 18 | 208 | 3 | 3 | 10.6 |  | 71 | 305B002 | 14 - 8 | 20 | 12.19 | 13.25 | 18.55 | 30 | 2.461 | 2.2642 | 1.6173 | 30 | 14 | 13.25 |  | SE | 20 | 63.6 | 1.1164 | 106 | 42.4 | 58 | 5.4717 | 254 | 23.9623 | XT2 | 125 | 25 | 25 | 2.3585 | 250 | 23.5849 | TRUE | FALSE | TRUE | -0.37736
27 | Size-0 | 18 | 220 - 240 (230) | 3 | 2 | 6.8 |  | 50 | 305B002 | 14 - 8 | 20 | 7.82 | 8.5 | 11.9 | 30 | 3.8363 | 3.5294 | 2.521 | 30 | 14 | 8.5 |  | SE | 20 | 40.8 | 1.2255 | 68 | 27.2 | 58 | 8.5294 | 254 | 37.3529 | XT2 | 125 | 25 | 25 | 3.6765 | 250 | 36.7647 | TRUE | FALSE | TRUE | -0.58824
28 | Size-0 | 18 | 220 - 240 (230) | 3 | 3 | 9.6 |  | 64 | 305B002 | 14 - 8 | 20 | 11.04 | 12 | 16.8 | 30 | 2.7174 | 2.5 | 1.7857 | 30 | 14 | 12 |  | SE | 15 | 57.6 | 1.1111 | 96 | 38.4 | 43 | 4.4792 | 182 | 18.9583 | XT2 | 125 | 25 | 25 | 2.6042 | 250 | 26.0417 | TRUE | TRUE | TRUE | 7.0833
28.1 | Size-0 | 18 | 220 - 240 (230) | 3 | 3 | 9.6 |  | 64 | 305B002 | 14 - 8 | 20 | 11.04 | 12 | 16.8 | 30 | 2.7174 | 2.5 | 1.7857 | 30 | 14 | 12 |  | SE | 20 | 57.6 | 1.1111 | 96 | 38.4 | 58 | 6.0417 | 254 | 26.4583 | XT2 | 125 | 25 | 25 | 2.6042 | 250 | 26.0417 | TRUE | FALSE | TRUE | -0.41667
29 | Size-0 | 18 | 440 - 480 (460) | 3 | 3 | 4.8 |  | 32 | 305B002 | 14 - 8 | 20 | 5.52 | 6 | 8.4 | 30 | 5.4348 | 5 | 3.5714 | 30 | 14 | 6 |  | SE | 15 | 28.8 | 1.1111 | 48 | 19.2 | 43 | 8.9583 | 182 | 37.9167 | XT2 | 125 | 25 | 25 | 5.2083 | 250 | 52.0833 | TRUE | TRUE | TRUE | 14.1667
30 | Size-0 | 18 | 440 - 480 (460) | 3 | 5 | 7.6 |  | 46 | 305B002 | 14 - 8 | 20 | 8.74 | 9.5 | 13.3 | 30 | 3.4325 | 3.1579 | 2.2556 | 30 | 14 | 9.5 |  | SE | 15 | 45.6 | 1.0088 | 76 | 30.4 | 43 | 5.6579 | 182 | 23.9474 | XT2 | 125 | 25 | 25 | 3.2895 | 250 | 32.8947 | TRUE | TRUE | TRUE | 8.9474
30.1 | Size-0 | 18 | 440 - 480 (460) | 3 | 5 | 7.6 |  | 46 | 305B002 | 14 - 8 | 20 | 8.74 | 9.5 | 13.3 | 30 | 3.4325 | 3.1579 | 2.2556 | 30 | 14 | 9.5 |  | SE | 20 | 45.6 | 1.0088 | 76 | 30.4 | 58 | 7.6316 | 254 | 33.4211 | XT2 | 125 | 25 | 25 | 3.2895 | 250 | 32.8947 | TRUE | FALSE | TRUE | -0.52632
31 | Size-0 | 18 | 550 - 600 (575) | 3 | 3 | 3.9 |  | 25.6 | 305B002 | 14 - 8 | 20 | 4.485 | 4.875 | 6.825 | 30 | 6.689 | 6.1538 | 4.3956 | 30 | 14 | 4.875 |  | SE | 15 | 23.4 | 1.094 | 39 | 15.6 | 43 | 11.0256 | 182 | 46.6667 | XT2 | 125 | 25 | 25 | 6.4103 | 250 | 64.1026 | TRUE | TRUE | TRUE | 17.4359
32 | Size-0 | 18 | 550 - 600 (575) | 3 | 5 | 6.1 |  | 36.8 | 305B002 | 14 - 8 | 20 | 7.015 | 7.625 | 10.675 | 30 | 4.2766 | 3.9344 | 2.8103 | 30 | 14 | 7.625 |  | SE | 15 | 36.6 | 1.0055 | 61 | 24.4 | 43 | 7.0492 | 182 | 29.8361 | XT2 | 125 | 25 | 25 | 4.0984 | 250 | 40.9836 | TRUE | TRUE | TRUE | 11.1475
32.1 | Size-0 | 18 | 550 - 600 (575) | 3 | 5 | 6.1 |  | 36.8 | 305B002 | 14 - 8 | 20 | 7.015 | 7.625 | 10.675 | 30 | 4.2766 | 3.9344 | 2.8103 | 30 | 14 | 7.625 |  | SE | 20 | 36.6 | 1.0055 | 61 | 24.4 | 58 | 9.5082 | 254 | 41.6393 | XT2 | 125 | 25 | 25 | 4.0984 | 250 | 40.9836 | TRUE | FALSE | TRUE | -0.65574
33 | Size-1 | 27 | 200 | 3 | 5 | 17.5 | 25.3 | 105.8 | 305C002 | 14 - 8 | 20 | 20.125 | 21.875 | 30.625 | 30 | 1.4907 | 1.3714 | 0.97959 | 30 | 10 | 21.875 |  | SE | 15 | 105 | 1.0076 | 175 | 70 | 43 | 2.4571 | 182 | 10.4 | XT2 | 125 | 25 | 25 | 1.4286 | 250 | 14.2857 | TRUE | TRUE | TRUE | 3.8857
33.1 | Size-1 | 27 | 200 | 3 | 5 | 17.5 | 32.2 | 105.8 | 305C002 | 14 - 8 | 20 | 20.125 | 21.875 | 30.625 | 30 | 1.4907 | 1.3714 | 0.97959 | 30 | 10 | 21.875 |  | SE | 20 | 105 | 1.0076 | 175 | 70 | 58 | 3.3143 | 254 | 14.5143 | XT2 | 125 | 25 | 25 | 1.4286 | 250 | 14.2857 | TRUE | FALSE | TRUE | -0.22857
33.2 | Size-1 | 27 | 200 | 3 | 5 | 17.5 | 32.2 | 105.8 | 305C002 | 14 - 8 | 20 | 20.125 | 21.875 | 30.625 | 30 | 1.4907 | 1.3714 | 0.97959 | 30 | 10 | 21.875 |  | SE | 25 | 105 | 1.0076 | 175 | 70 | 73 | 4.1714 | 332 | 18.9714 | XT2 | 125 | 25 | 25 | 1.4286 | 250 | 14.2857 | TRUE | FALSE | TRUE | -4.6857
33.3 | Size-1 | 27 | 200 | 3 | 5 | 17.5 | 32.2 | 105.8 | 305C002 | 14 - 8 | 20 | 20.125 | 21.875 | 30.625 | 30 | 1.4907 | 1.3714 | 0.97959 | 30 | 10 | 21.875 |  | SE | 30 | 105 | 1.0076 | 175 | 70 | 87 | 4.9714 | 415 | 23.7143 | XT2 | 125 | 60 | 60 | 3.4286 | 600 | 34.2857 | TRUE | TRUE | TRUE | 10.5714
33.4 | Size-1 | 27 | 200 | 3 | 5 | 17.5 | 42 | 105.8 | 305C002 | 14 - 8 | 20 | 20.125 | 21.875 | 30.625 | 30 | 1.4907 | 1.3714 | 0.97959 | 30 | 10 | 21.875 |  | SE | 40 | 105 | 1.0076 | 175 | 70 | 118 | 6.7429 | 501 | 28.6286 | XT2 | 125 | 60 | 60 | 3.4286 | 600 | 34.2857 | TRUE | TRUE | TRUE | 5.6571
34 | Size-1 | 27 | 200 | 3 | 7.5 | 25.3 |  | 146 | 305C002 | 14 - 8 | 20 | 29.095 | 31.625 | 44.275 | 30 | 1.0311 | 0.94862 | 0.67758 | 60 | 8 | 31.625 |  | SE | 40 | 151.8 | 0.96179 | 253 | 101.2 | 118 | 4.664 | 501 | 19.8024 | XT2 | 125 | 60 | 60 | 2.3715 | 600 | 23.7154 | TRUE | TRUE | TRUE | 3.913
34.1 | Size-1 | 27 | 200 | 3 | 7.5 | 25.3 |  | 146 | 305C002 | 14 - 8 | 20 | 29.095 | 31.625 | 44.275 | 30 | 1.0311 | 0.94862 | 0.67758 | 60 | 8 | 31.625 |  | SE | 60 | 151.8 | 0.96179 | 253 | 101.2 | 178 | 7.0356 | 777 | 30.7115 | XT2 | 125 | 60 | 60 | 2.3715 | 600 | 23.7154 | TRUE | FALSE | TRUE | -6.996
35 | Size-1 | 27 | 208 | 3 | 5 | 16.7 |  | 102 | 305C002 | 14 - 8 | 20 | 19.205 | 20.875 | 29.225 | 30 | 1.5621 | 1.4371 | 1.0265 | 30 | 10 | 20.875 |  | SE | 15 | 100.2 | 1.018 | 167 | 66.8 | 43 | 2.5749 | 182 | 10.8982 | XT2 | 125 | 25 | 25 | 1.497 | 250 | 14.9701 | TRUE | TRUE | TRUE | 4.0719
35.1 | Size-1 | 27 | 208 | 3 | 5 | 16.7 |  | 102 | 305C002 | 14 - 8 | 20 | 19.205 | 20.875 | 29.225 | 30 | 1.5621 | 1.4371 | 1.0265 | 30 | 10 | 20.875 |  | SE | 20 | 100.2 | 1.018 | 167 | 66.8 | 58 | 3.4731 | 254 | 15.2096 | XT2 | 125 | 25 | 25 | 1.497 | 250 | 14.9701 | TRUE | FALSE | TRUE | -0.23952
35.2 | Size-1 | 27 | 208 | 3 | 5 | 16.7 |  | 102 | 305C002 | 14 - 8 | 20 | 19.205 | 20.875 | 29.225 | 30 | 1.5621 | 1.4371 | 1.0265 | 30 | 10 | 20.875 |  | SE | 25 | 100.2 | 1.018 | 167 | 66.8 | 73 | 4.3713 | 332 | 19.8802 | XT2 | 125 | 25 | 25 | 1.497 | 250 | 14.9701 | TRUE | FALSE | TRUE | -4.9102
35.3 | Size-1 | 27 | 208 | 3 | 5 | 16.7 |  | 102 | 305C002 | 14 - 8 | 20 | 19.205 | 20.875 | 29.225 | 30 | 1.5621 | 1.4371 | 1.0265 | 30 | 10 | 20.875 |  | SE | 30 | 100.2 | 1.018 | 167 | 66.8 | 87 | 5.2096 | 415 | 24.8503 | XT2 | 125 | 60 | 60 | 3.5928 | 600 | 35.9281 | TRUE | TRUE | TRUE | 11.0778
35.4 | Size-1 | 27 | 208 | 3 | 5 | 16.7 |  | 102 | 305C002 | 14 - 8 | 20 | 19.205 | 20.875 | 29.225 | 30 | 1.5621 | 1.4371 | 1.0265 | 30 | 10 | 20.875 |  | SE | 40 | 100.2 | 1.018 | 167 | 66.8 | 118 | 7.0659 | 501 | 30 | XT2 | 125 | 60 | 60 | 3.5928 | 600 | 35.9281 | TRUE | TRUE | TRUE | 5.9281
36 | Size-1 | 27 | 208 | 3 | 7.5 | 24.2 |  | 140 | 305C002 | 14 - 8 | 20 | 27.83 | 30.25 | 42.35 | 30 | 1.078 | 0.99174 | 0.70838 | 30 | 8 | 30.25 |  | SE | 40 | 145.2 | 0.96419 | 242 | 96.8 | 118 | 4.876 | 501 | 20.7025 | XT2 | 125 | 60 | 60 | 2.4793 | 600 | 24.7934 | TRUE | TRUE | TRUE | 4.0909
36.1 | Size-1 | 27 | 208 | 3 | 7.5 | 24.2 |  | 140 | 305C002 | 14 - 8 | 20 | 27.83 | 30.25 | 42.35 | 30 | 1.078 | 0.99174 | 0.70838 | 30 | 8 | 30.25 |  | SE | 60 | 145.2 | 0.96419 | 242 | 96.8 | 178 | 7.3554 | 777 | 32.1074 | XT2 | 125 | 60 | 60 | 2.4793 | 600 | 24.7934 | TRUE | FALSE | TRUE | -7.314
37 | Size-1 | 27 | 220 - 240 (230) | 3 | 5 | 15.2 |  | 92 | 305C002 | 14 - 8 | 20 | 17.48 | 19 | 26.6 | 30 | 1.7162 | 1.5789 | 1.1278 | 30 | 12 | 19 |  | SE | 15 | 91.2 | 1.0088 | 152 | 60.8 | 43 | 2.8289 | 182 | 11.9737 | XT2 | 125 | 25 | 25 | 1.6447 | 250 | 16.4474 | TRUE | TRUE | TRUE | 4.4737
37.1 | Size-1 | 27 | 220 - 240 (230) | 3 | 5 | 15.2 |  | 92 | 305C002 | 14 - 8 | 20 | 17.48 | 19 | 26.6 | 30 | 1.7162 | 1.5789 | 1.1278 | 30 | 12 | 19 |  | SE | 20 | 91.2 | 1.0088 | 152 | 60.8 | 58 | 3.8158 | 254 | 16.7105 | XT2 | 125 | 25 | 25 | 1.6447 | 250 | 16.4474 | TRUE | FALSE | TRUE | -0.26316
37.2 | Size-1 | 27 | 220 - 240 (230) | 3 | 5 | 15.2 |  | 92 | 305C002 | 14 - 8 | 20 | 17.48 | 19 | 26.6 | 30 | 1.7162 | 1.5789 | 1.1278 | 30 | 12 | 19 |  | SE | 25 | 91.2 | 1.0088 | 152 | 60.8 | 73 | 4.8026 | 332 | 21.8421 | XT2 | 125 | 25 | 25 | 1.6447 | 250 | 16.4474 | TRUE | FALSE | TRUE | -5.3947
37.3 | Size-1 | 27 | 220 - 240 (230) | 3 | 5 | 15.2 |  | 92 | 305C002 | 14 - 8 | 20 | 17.48 | 19 | 26.6 | 30 | 1.7162 | 1.5789 | 1.1278 | 30 | 12 | 19 |  | SE | 30 | 91.2 | 1.0088 | 152 | 60.8 | 87 | 5.7237 | 415 | 27.3026 | XT2 | 125 | 60 | 60 | 3.9474 | 600 | 39.4737 | TRUE | TRUE | TRUE | 12.1711
37.4 | Size-1 | 27 | 220 - 240 (230) | 3 | 5 | 15.2 |  | 92 | 305C002 | 14 - 8 | 20 | 17.48 | 19 | 26.6 | 30 | 1.7162 | 1.5789 | 1.1278 | 30 | 12 | 19 |  | SE | 40 | 91.2 | 1.0088 | 152 | 60.8 | 118 | 7.7632 | 501 | 32.9605 | XT2 | 125 | 60 | 60 | 3.9474 | 600 | 39.4737 | TRUE | TRUE | TRUE | 6.5132
38 | Size-1 | 27 | 220 - 240 (230) | 3 | 7.5 | 22 |  | 127 | 305C002 | 14 - 8 | 20 | 25.3 | 27.5 | 38.5 | 30 | 1.1858 | 1.0909 | 0.77922 | 30 | 10 | 27.5 |  | SE | 30 | 132 | 0.96212 | 220 | 88 | 87 | 3.9545 | 415 | 18.8636 | XT2 | 125 | 60 | 60 | 2.7273 | 600 | 27.2727 | TRUE | TRUE | TRUE | 8.4091
38.1 | Size-1 | 27 | 220 - 240 (230) | 3 | 7.5 | 22 |  | 127 | 305C002 | 14 - 8 | 20 | 25.3 | 27.5 | 38.5 | 30 | 1.1858 | 1.0909 | 0.77922 | 30 | 10 | 27.5 |  | SE | 40 | 132 | 0.96212 | 220 | 88 | 118 | 5.3636 | 501 | 22.7727 | XT2 | 125 | 60 | 60 | 2.7273 | 600 | 27.2727 | TRUE | TRUE | TRUE | 4.5
39 | Size-1 | 27 | 440 - 480 (460) | 3 | 7.5 | 11 |  | 63.5 | 305C002 | 14 - 8 | 20 | 12.65 | 13.75 | 19.25 | 30 | 2.3715 | 2.1818 | 1.5584 | 30 | 14 | 13.75 |  | SE | 15 | 66 | 0.96212 | 110 | 44 | 43 | 3.9091 | 182 | 16.5455 | XT2 | 125 | 25 | 25 | 2.2727 | 250 | 22.7273 | TRUE | TRUE | TRUE | 6.1818
39.1 | Size-1 | 27 | 440 - 480 (460) | 3 | 7.5 | 11 |  | 63.5 | 305C002 | 14 - 8 | 20 | 12.65 | 13.75 | 19.25 | 30 | 2.3715 | 2.1818 | 1.5584 | 30 | 14 | 13.75 |  | SE | 20 | 66 | 0.96212 | 110 | 44 | 58 | 5.2727 | 254 | 23.0909 | XT2 | 125 | 25 | 25 | 2.2727 | 250 | 22.7273 | TRUE | FALSE | TRUE | -0.36364
39.2 | Size-1 | 27 | 440 - 480 (460) | 3 | 7.5 | 11 |  | 63.5 | 305C002 | 14 - 8 | 20 | 12.65 | 13.75 | 19.25 | 30 | 2.3715 | 2.1818 | 1.5584 | 30 | 14 | 13.75 |  | SE | 25 | 66 | 0.96212 | 110 | 44 | 73 | 6.6364 | 332 | 30.1818 | XT2 | 125 | 25 | 25 | 2.2727 | 250 | 22.7273 | TRUE | FALSE | TRUE | -7.4545
39.3 | Size-1 | 27 | 440 - 480 (460) | 3 | 7.5 | 11 |  | 63.5 | 305C002 | 14 - 8 | 20 | 12.65 | 13.75 | 19.25 | 30 | 2.3715 | 2.1818 | 1.5584 | 30 | 14 | 13.75 |  | SE | 30 | 66 | 0.96212 | 110 | 44 | 87 | 7.9091 | 415 | 37.7273 | XT2 | 125 | 60 | 60 | 5.4545 | 600 | 54.5455 | TRUE | TRUE | TRUE | 16.8182
39.4 | Size-1 | 27 | 440 - 480 (460) | 3 | 7.5 | 11 |  | 63.5 | 305C002 | 14 - 8 | 20 | 12.65 | 13.75 | 19.25 | 30 | 2.3715 | 2.1818 | 1.5584 | 30 | 14 | 13.75 |  | SE | 40 | 66 | 0.96212 | 110 | 44 | 118 | 10.7273 | 501 | 45.5455 | XT2 | 125 | 60 | 60 | 5.4545 | 600 | 54.5455 | TRUE | TRUE | TRUE | 9
40 | Size-1 | 27 | 440 - 480 (460) | 3 | 10 | 14 |  | 81 | 305C002 | 14 - 8 | 20 | 16.1 | 17.5 | 24.5 | 30 | 1.8634 | 1.7143 | 1.2245 | 30 | 12 | 17.5 |  | SE | 20 | 84 | 0.96429 | 140 | 56 | 58 | 4.1429 | 254 | 18.1429 | XT2 | 125 | 25 | 25 | 1.7857 | 250 | 17.8571 | TRUE | FALSE | TRUE | -0.28571
40.1 | Size-1 | 27 | 440 - 480 (460) | 3 | 10 | 14 |  | 81 | 305C002 | 14 - 8 | 20 | 16.1 | 17.5 | 24.5 | 30 | 1.8634 | 1.7143 | 1.2245 | 30 | 12 | 17.5 |  | SE | 25 | 84 | 0.96429 | 140 | 56 | 73 | 5.2143 | 332 | 23.7143 | XT2 | 125 | 25 | 25 | 1.7857 | 250 | 17.8571 | TRUE | FALSE | TRUE | -5.8571
40.2 | Size-1 | 27 | 440 - 480 (460) | 3 | 10 | 14 |  | 81 | 305C002 | 14 - 8 | 20 | 16.1 | 17.5 | 24.5 | 30 | 1.8634 | 1.7143 | 1.2245 | 30 | 12 | 17.5 |  | SE | 30 | 84 | 0.96429 | 140 | 56 | 87 | 6.2143 | 415 | 29.6429 | XT2 | 125 | 60 | 60 | 4.2857 | 600 | 42.8571 | TRUE | TRUE | TRUE | 13.2143
40.3 | Size-1 | 27 | 440 - 480 (460) | 3 | 10 | 14 |  | 81 | 305C002 | 14 - 8 | 20 | 16.1 | 17.5 | 24.5 | 30 | 1.8634 | 1.7143 | 1.2245 | 30 | 12 | 17.5 |  | SE | 40 | 84 | 0.96429 | 140 | 56 | 118 | 8.4286 | 501 | 35.7857 | XT2 | 125 | 60 | 60 | 4.2857 | 600 | 42.8571 | TRUE | TRUE | TRUE | 7.0714
41 | Size-1 | 27 | 550 - 600 (575) | 3 | 7.5 | 9 |  | 50.8 | 305C002 | 14 - 8 | 20 | 10.35 | 11.25 | 15.75 | 30 | 2.8986 | 2.6667 | 1.9048 | 30 | 14 | 11.25 |  | SE | 15 | 54 | 0.94074 | 90 | 36 | 43 | 4.7778 | 182 | 20.2222 | XT2 | 125 | 25 | 25 | 2.7778 | 250 | 27.7778 | TRUE | TRUE | TRUE | 7.5556
41.1 | Size-1 | 27 | 550 - 600 (575) | 3 | 7.5 | 9 |  | 50.8 | 305C002 | 14 - 8 | 20 | 10.35 | 11.25 | 15.75 | 30 | 2.8986 | 2.6667 | 1.9048 | 30 | 14 | 11.25 |  | SE | 20 | 54 | 0.94074 | 90 | 36 | 58 | 6.4444 | 254 | 28.2222 | XT2 | 125 | 25 | 25 | 2.7778 | 250 | 27.7778 | TRUE | FALSE | TRUE | -0.44444
41.2 | Size-1 | 27 | 550 - 600 (575) | 3 | 7.5 | 9 |  | 50.8 | 305C002 | 14 - 8 | 20 | 10.35 | 11.25 | 15.75 | 30 | 2.8986 | 2.6667 | 1.9048 | 30 | 14 | 11.25 |  | SE | 25 | 54 | 0.94074 | 90 | 36 | 73 | 8.1111 | 332 | 36.8889 | XT2 | 125 | 25 | 25 | 2.7778 | 250 | 27.7778 | TRUE | FALSE | TRUE | -9.1111
41.3 | Size-1 | 27 | 550 - 600 (575) | 3 | 7.5 | 9 |  | 50.8 | 305C002 | 14 - 8 | 20 | 10.35 | 11.25 | 15.75 | 30 | 2.8986 | 2.6667 | 1.9048 | 30 | 14 | 11.25 |  | SE | 30 | 54 | 0.94074 | 90 | 36 | 87 | 9.6667 | 415 | 46.1111 | XT2 | 125 | 60 | 60 | 6.6667 | 600 | 66.6667 | TRUE | TRUE | TRUE | 20.5556
41.4 | Size-1 | 27 | 550 - 600 (575) | 3 | 7.5 | 9 |  | 50.8 | 305C002 | 14 - 8 | 20 | 10.35 | 11.25 | 15.75 | 30 | 2.8986 | 2.6667 | 1.9048 | 30 | 14 | 11.25 |  | SE | 40 | 54 | 0.94074 | 90 | 36 | 118 | 13.1111 | 501 | 55.6667 | XT2 | 125 | 60 | 60 | 6.6667 | 600 | 66.6667 | TRUE | TRUE | TRUE | 11
42 | Size-1 | 27 | 550 - 600 (575) | 3 | 10 | 11 |  | 64.8 | 305C002 | 14 - 8 | 20 | 12.65 | 13.75 | 19.25 | 30 | 2.3715 | 2.1818 | 1.5584 | 30 | 14 | 13.75 |  | SE | 15 | 66 | 0.98182 | 110 | 44 | 43 | 3.9091 | 182 | 16.5455 | XT2 | 125 | 25 | 25 | 2.2727 | 250 | 22.7273 | TRUE | TRUE | TRUE | 6.1818
42.1 | Size-1 | 27 | 550 - 600 (575) | 3 | 10 | 11 |  | 64.8 | 305C002 | 14 - 8 | 20 | 12.65 | 13.75 | 19.25 | 30 | 2.3715 | 2.1818 | 1.5584 | 30 | 14 | 13.75 |  | SE | 20 | 66 | 0.98182 | 110 | 44 | 58 | 5.2727 | 254 | 23.0909 | XT2 | 125 | 25 | 25 | 2.2727 | 250 | 22.7273 | TRUE | FALSE | TRUE | -0.36364
42.2 | Size-1 | 27 | 550 - 600 (575) | 3 | 10 | 11 |  | 64.8 | 305C002 | 14 - 8 | 20 | 12.65 | 13.75 | 19.25 | 30 | 2.3715 | 2.1818 | 1.5584 | 30 | 14 | 13.75 |  | SE | 25 | 66 | 0.98182 | 110 | 44 | 73 | 6.6364 | 332 | 30.1818 | XT2 | 125 | 25 | 25 | 2.2727 | 250 | 22.7273 | TRUE | FALSE | TRUE | -7.4545
42.3 | Size-1 | 27 | 550 - 600 (575) | 3 | 10 | 11 |  | 64.8 | 305C002 | 14 - 8 | 20 | 12.65 | 13.75 | 19.25 | 30 | 2.3715 | 2.1818 | 1.5584 | 30 | 14 | 13.75 |  | SE | 30 | 66 | 0.98182 | 110 | 44 | 87 | 7.9091 | 415 | 37.7273 | XT2 | 125 | 60 | 60 | 5.4545 | 600 | 54.5455 | TRUE | TRUE | TRUE | 16.8182
42.4 | Size-1 | 27 | 550 - 600 (575) | 3 | 10 | 11 |  | 64.8 | 305C002 | 14 - 8 | 20 | 12.65 | 13.75 | 19.25 | 30 | 2.3715 | 2.1818 | 1.5584 | 30 | 14 | 13.75 |  | SE | 40 | 66 | 0.98182 | 110 | 44 | 118 | 10.7273 | 501 | 45.5455 | XT2 | 125 | 60 | 60 | 5.4545 | 600 | 54.5455 | TRUE | TRUE | TRUE | 9
43 | Size-2 | 45 | 200 | 3 | 10 | 32.2 | 42 | 186.3 | 305D002 | 14 - 4 | 50 | 37.03 | 40.25 | 56.35 | 60 | 1.6203 | 1.4907 | 1.0648 | 60 | 8 | 40.25 |  | SE | 30 | 193.2 | 0.96429 | 322 | 128.8 | 87 | 2.7019 | 415 | 12.8882 | XT2 | 125 | 60 | 60 | 1.8634 | 600 | 18.6335 | TRUE | TRUE | TRUE | 5.7453
43.1 | Size-2 | 45 | 200 | 3 | 10 | 32.2 | 48.3 | 186.3 | 305D002 | 14 - 4 | 50 | 37.03 | 40.25 | 56.35 | 60 | 1.6203 | 1.4907 | 1.0648 | 60 | 8 | 40.25 |  | SE | 40 | 193.2 | 0.96429 | 322 | 128.8 | 118 | 3.6646 | 501 | 15.559 | XT2 | 125 | 60 | 60 | 1.8634 | 600 | 18.6335 | TRUE | TRUE | TRUE | 3.0745
43.2 | Size-2 | 45 | 200 | 3 | 10 | 32.2 | 62.1 | 186.3 | 305D002 | 14 - 4 | 50 | 37.03 | 40.25 | 56.35 | 60 | 1.6203 | 1.4907 | 1.0648 | 60 | 8 | 40.25 |  | SE | 50 | 193.2 | 0.96429 | 322 | 128.8 | 148 | 4.5963 | 637 | 19.7826 | XT2 | 125 | 60 | 60 | 1.8634 | 600 | 18.6335 | TRUE | FALSE | TRUE | -1.1491
43.3 | Size-2 | 45 | 200 | 3 | 10 | 32.2 | 78.2 | 186.3 | 305D002 | 14 - 4 | 50 | 37.03 | 40.25 | 56.35 | 60 | 1.6203 | 1.4907 | 1.0648 | 60 | 8 | 40.25 |  | SE | 60 | 193.2 | 0.96429 | 322 | 128.8 | 178 | 5.528 | 777 | 24.1304 | XT2 | 125 | 60 | 60 | 1.8634 | 600 | 18.6335 | TRUE | FALSE | TRUE | -5.4969
43.4 | Size-2 | 45 | 200 | 3 | 10 | 32.2 | 78.2 | 186.3 | 305D002 | 14 - 4 | 50 | 37.03 | 40.25 | 56.35 | 60 | 1.6203 | 1.4907 | 1.0648 | 60 | 8 | 40.25 |  | SE | 70 | 193.2 | 0.96429 | 322 | 128.8 | 206 | 6.3975 | 863 | 26.8012 | XT2 | 125 | 100 | 100 | 3.1056 | 1000 | 31.0559 | TRUE | TRUE | TRUE | 4.2547
44 | Size-2 | 45 | 208 | 3 | 10 | 30.8 |  | 179 | 305D002 | 14 - 4 | 50 | 35.42 | 38.5 | 53.9 | 60 | 1.694 | 1.5584 | 1.1132 | 60 | 8 | 38.5 |  | SE | 30 | 184.8 | 0.96861 | 308 | 123.2 | 87 | 2.8247 | 415 | 13.474 | XT2 | 125 | 60 | 60 | 1.9481 | 600 | 19.4805 | TRUE | TRUE | TRUE | 6.0065
44.1 | Size-2 | 45 | 208 | 3 | 10 | 30.8 |  | 179 | 305D002 | 14 - 4 | 50 | 35.42 | 38.5 | 53.9 | 60 | 1.694 | 1.5584 | 1.1132 | 60 | 8 | 38.5 |  | SE | 40 | 184.8 | 0.96861 | 308 | 123.2 | 118 | 3.8312 | 501 | 16.2662 | XT2 | 125 | 60 | 60 | 1.9481 | 600 | 19.4805 | TRUE | TRUE | TRUE | 3.2143
44.2 | Size-2 | 45 | 208 | 3 | 10 | 30.8 |  | 179 | 305D002 | 14 - 4 | 50 | 35.42 | 38.5 | 53.9 | 60 | 1.694 | 1.5584 | 1.1132 | 60 | 8 | 38.5 |  | SE | 50 | 184.8 | 0.96861 | 308 | 123.2 | 148 | 4.8052 | 637 | 20.6818 | XT2 | 125 | 60 | 60 | 1.9481 | 600 | 19.4805 | TRUE | FALSE | TRUE | -1.2013
44.3 | Size-2 | 45 | 208 | 3 | 10 | 30.8 |  | 179 | 305D002 | 14 - 4 | 50 | 35.42 | 38.5 | 53.9 | 60 | 1.694 | 1.5584 | 1.1132 | 60 | 8 | 38.5 |  | SE | 60 | 184.8 | 0.96861 | 308 | 123.2 | 178 | 5.7792 | 777 | 25.2273 | XT2 | 125 | 60 | 60 | 1.9481 | 600 | 19.4805 | TRUE | FALSE | TRUE | -5.7468
44.4 | Size-2 | 45 | 208 | 3 | 10 | 30.8 |  | 179 | 305D002 | 14 - 4 | 50 | 35.42 | 38.5 | 53.9 | 60 | 1.694 | 1.5584 | 1.1132 | 60 | 8 | 38.5 |  | SE | 70 | 184.8 | 0.96861 | 308 | 123.2 | 206 | 6.6883 | 863 | 28.0195 | XT2 | 125 | 100 | 100 | 3.2468 | 1000 | 32.4675 | TRUE | TRUE | TRUE | 4.4481
45 | Size-2 | 45 | 220 - 240 (230) | 3 | 10 | 28 |  | 162 | 305D002 | 14 - 4 | 50 | 32.2 | 35 | 49 | 60 | 1.8634 | 1.7143 | 1.2245 | 60 | 8 | 35 |  | SE | 30 | 168 | 0.96429 | 280 | 112 | 87 | 3.1071 | 415 | 14.8214 | XT2 | 125 | 60 | 60 | 2.1429 | 600 | 21.4286 | TRUE | TRUE | TRUE | 6.6071
45.1 | Size-2 | 45 | 220 - 240 (230) | 3 | 10 | 28 |  | 162 | 305D002 | 14 - 4 | 50 | 32.2 | 35 | 49 | 60 | 1.8634 | 1.7143 | 1.2245 | 60 | 8 | 35 |  | SE | 40 | 168 | 0.96429 | 280 | 112 | 118 | 4.2143 | 501 | 17.8929 | XT2 | 125 | 60 | 60 | 2.1429 | 600 | 21.4286 | TRUE | TRUE | TRUE | 3.5357
45.2 | Size-2 | 45 | 220 - 240 (230) | 3 | 10 | 28 |  | 162 | 305D002 | 14 - 4 | 50 | 32.2 | 35 | 49 | 60 | 1.8634 | 1.7143 | 1.2245 | 60 | 8 | 35 |  | SE | 50 | 168 | 0.96429 | 280 | 112 | 148 | 5.2857 | 637 | 22.75 | XT2 | 125 | 60 | 60 | 2.1429 | 600 | 21.4286 | TRUE | FALSE | TRUE | -1.3214
45.3 | Size-2 | 45 | 220 - 240 (230) | 3 | 10 | 28 |  | 162 | 305D002 | 14 - 4 | 50 | 32.2 | 35 | 49 | 60 | 1.8634 | 1.7143 | 1.2245 | 60 | 8 | 35 |  | SE | 60 | 168 | 0.96429 | 280 | 112 | 178 | 6.3571 | 777 | 27.75 | XT2 | 125 | 60 | 60 | 2.1429 | 600 | 21.4286 | TRUE | FALSE | TRUE | -6.3214
45.4 | Size-2 | 45 | 220 - 240 (230) | 3 | 10 | 28 |  | 162 | 305D002 | 14 - 4 | 50 | 32.2 | 35 | 49 | 60 | 1.8634 | 1.7143 | 1.2245 | 60 | 8 | 35 |  | SE | 70 | 168 | 0.96429 | 280 | 112 | 206 | 7.3571 | 863 | 30.8214 | XT2 | 125 | 100 | 100 | 3.5714 | 1000 | 35.7143 | TRUE | TRUE | TRUE | 4.8929
46 | Size-2 | 45 | 220 - 240 (230) | 3 | 15 | 42 |  | 232 | 305D002 | 14 - 4 | 50 | 48.3 | 52.5 | 73.5 | 60 | 1.2422 | 1.1429 | 0.81633 | 60 | 6 | 52.5 |  | SE | 60 | 252 | 0.92063 | 420 | 168 | 178 | 4.2381 | 777 | 18.5 | XT2 | 125 | 60 | 60 | 1.4286 | 600 | 14.2857 | TRUE | FALSE | TRUE | -4.2143
46.1 | Size-2 | 45 | 220 - 240 (230) | 3 | 15 | 42 |  | 232 | 305D002 | 14 - 4 | 50 | 48.3 | 52.5 | 73.5 | 60 | 1.2422 | 1.1429 | 0.81633 | 60 | 6 | 52.5 |  | SE | 70 | 252 | 0.92063 | 420 | 168 | 206 | 4.9048 | 863 | 20.5476 | XT2 | 125 | 100 | 100 | 2.381 | 1000 | 23.8095 | TRUE | TRUE | TRUE | 3.2619
47 | Size-2 | 45 | 440 - 480 (460) | 3 | 15 | 21 |  | 116 | 305D002 | 14 - 4 | 50 | 24.15 | 26.25 | 36.75 | 60 | 2.4845 | 2.2857 | 1.6327 | 30 | 10 | 26.25 |  | SE | 30 | 126 | 0.92063 | 210 | 84 | 87 | 4.1429 | 415 | 19.7619 | XT2 | 125 | 60 | 60 | 2.8571 | 600 | 28.5714 | TRUE | TRUE | TRUE | 8.8095
47.1 | Size-2 | 45 | 440 - 480 (460) | 3 | 15 | 21 |  | 116 | 305D002 | 14 - 4 | 50 | 24.15 | 26.25 | 36.75 | 60 | 2.4845 | 2.2857 | 1.6327 | 30 | 10 | 26.25 |  | SE | 40 | 126 | 0.92063 | 210 | 84 | 118 | 5.619 | 501 | 23.8571 | XT2 | 125 | 60 | 60 | 2.8571 | 600 | 28.5714 | TRUE | TRUE | TRUE | 4.7143
47.2 | Size-2 | 45 | 440 - 480 (460) | 3 | 15 | 21 |  | 116 | 305D002 | 14 - 4 | 50 | 24.15 | 26.25 | 36.75 | 60 | 2.4845 | 2.2857 | 1.6327 | 30 | 10 | 26.25 |  | SE | 50 | 126 | 0.92063 | 210 | 84 | 148 | 7.0476 | 637 | 30.3333 | XT2 | 125 | 60 | 60 | 2.8571 | 600 | 28.5714 | TRUE | FALSE | TRUE | -1.7619
47.3 | Size-2 | 45 | 440 - 480 (460) | 3 | 15 | 21 |  | 116 | 305D002 | 14 - 4 | 50 | 24.15 | 26.25 | 36.75 | 60 | 2.4845 | 2.2857 | 1.6327 | 30 | 10 | 26.25 |  | SE | 60 | 126 | 0.92063 | 210 | 84 | 178 | 8.4762 | 777 | 37 | XT2 | 125 | 60 | 60 | 2.8571 | 600 | 28.5714 | TRUE | FALSE | TRUE | -8.4286
47.4 | Size-2 | 45 | 440 - 480 (460) | 3 | 15 | 21 |  | 116 | 305D002 | 14 - 4 | 50 | 24.15 | 26.25 | 36.75 | 60 | 2.4845 | 2.2857 | 1.6327 | 30 | 10 | 26.25 |  | SE | 70 | 126 | 0.92063 | 210 | 84 | 206 | 9.8095 | 863 | 41.0952 | XT2 | 125 | 100 | 100 | 4.7619 | 1000 | 47.619 | TRUE | TRUE | TRUE | 6.5238
48 | Size-2 | 45 | 440 - 480 (460) | 3 | 20 | 27 |  | 145 | 305D002 | 14 - 4 | 50 | 31.05 | 33.75 | 47.25 | 60 | 1.9324 | 1.7778 | 1.2698 | 60 | 8 | 33.75 |  | SE | 40 | 162 | 0.89506 | 270 | 108 | 118 | 4.3704 | 501 | 18.5556 | XT2 | 125 | 60 | 60 | 2.2222 | 600 | 22.2222 | TRUE | TRUE | TRUE | 3.6667
48.1 | Size-2 | 45 | 440 - 480 (460) | 3 | 20 | 27 |  | 145 | 305D002 | 14 - 4 | 50 | 31.05 | 33.75 | 47.25 | 60 | 1.9324 | 1.7778 | 1.2698 | 60 | 8 | 33.75 |  | SE | 50 | 162 | 0.89506 | 270 | 108 | 148 | 5.4815 | 637 | 23.5926 | XT2 | 125 | 60 | 60 | 2.2222 | 600 | 22.2222 | TRUE | FALSE | TRUE | -1.3704
48.2 | Size-2 | 45 | 440 - 480 (460) | 3 | 20 | 27 |  | 145 | 305D002 | 14 - 4 | 50 | 31.05 | 33.75 | 47.25 | 60 | 1.9324 | 1.7778 | 1.2698 | 60 | 8 | 33.75 |  | SE | 60 | 162 | 0.89506 | 270 | 108 | 178 | 6.5926 | 777 | 28.7778 | XT2 | 125 | 60 | 60 | 2.2222 | 600 | 22.2222 | TRUE | FALSE | TRUE | -6.5556
48.3 | Size-2 | 45 | 440 - 480 (460) | 3 | 20 | 27 |  | 145 | 305D002 | 14 - 4 | 50 | 31.05 | 33.75 | 47.25 | 60 | 1.9324 | 1.7778 | 1.2698 | 60 | 8 | 33.75 |  | SE | 70 | 162 | 0.89506 | 270 | 108 | 206 | 7.6296 | 863 | 31.963 | XT2 | 125 | 100 | 100 | 3.7037 | 1000 | 37.037 | TRUE | TRUE | TRUE | 5.0741
49 | Size-2 | 45 | 440 - 480 (460) | 3 | 25 | 34 |  | 183 | 305D002 | 14 - 4 | 50 | 39.1 | 42.5 | 59.5 | 60 | 1.5345 | 1.4118 | 1.0084 | 60 | 8 | 42.5 |  | SE | 50 | 204 | 0.89706 | 340 | 136 | 148 | 4.3529 | 637 | 18.7353 | XT2 | 125 | 60 | 60 | 1.7647 | 600 | 17.6471 | TRUE | FALSE | TRUE | -1.0882
49.1 | Size-2 | 45 | 440 - 480 (460) | 3 | 25 | 34 |  | 183 | 305D002 | 14 - 4 | 50 | 39.1 | 42.5 | 59.5 | 60 | 1.5345 | 1.4118 | 1.0084 | 60 | 8 | 42.5 |  | SE | 60 | 204 | 0.89706 | 340 | 136 | 178 | 5.2353 | 777 | 22.8529 | XT2 | 125 | 60 | 60 | 1.7647 | 600 | 17.6471 | TRUE | FALSE | TRUE | -5.2059
49.2 | Size-2 | 45 | 440 - 480 (460) | 3 | 25 | 34 |  | 183 | 305D002 | 14 - 4 | 50 | 39.1 | 42.5 | 59.5 | 60 | 1.5345 | 1.4118 | 1.0084 | 60 | 8 | 42.5 |  | SE | 70 | 204 | 0.89706 | 340 | 136 | 206 | 6.0588 | 863 | 25.3824 | XT2 | 125 | 100 | 100 | 2.9412 | 1000 | 29.4118 | TRUE | TRUE | TRUE | 4.0294
50 | Size-2 | 45 | 550 - 600 (575) | 3 | 15 | 17 |  | 93 | 305D002 | 14 - 4 | 50 | 19.55 | 21.25 | 29.75 | 60 | 3.0691 | 2.8235 | 2.0168 | 30 | 10 | 21.25 |  | SE | 30 | 102 | 0.91176 | 170 | 68 | 87 | 5.1176 | 415 | 24.4118 | XT2 | 125 | 60 | 60 | 3.5294 | 600 | 35.2941 | TRUE | TRUE | TRUE | 10.8824
50.1 | Size-2 | 45 | 550 - 600 (575) | 3 | 15 | 17 |  | 93 | 305D002 | 14 - 4 | 50 | 19.55 | 21.25 | 29.75 | 60 | 3.0691 | 2.8235 | 2.0168 | 30 | 10 | 21.25 |  | SE | 40 | 102 | 0.91176 | 170 | 68 | 118 | 6.9412 | 501 | 29.4706 | XT2 | 125 | 60 | 60 | 3.5294 | 600 | 35.2941 | TRUE | TRUE | TRUE | 5.8235
50.2 | Size-2 | 45 | 550 - 600 (575) | 3 | 15 | 17 |  | 93 | 305D002 | 14 - 4 | 50 | 19.55 | 21.25 | 29.75 | 60 | 3.0691 | 2.8235 | 2.0168 | 30 | 10 | 21.25 |  | SE | 50 | 102 | 0.91176 | 170 | 68 | 148 | 8.7059 | 637 | 37.4706 | XT2 | 125 | 60 | 60 | 3.5294 | 600 | 35.2941 | TRUE | FALSE | TRUE | -2.1765
50.3 | Size-2 | 45 | 550 - 600 (575) | 3 | 15 | 17 |  | 93 | 305D002 | 14 - 4 | 50 | 19.55 | 21.25 | 29.75 | 60 | 3.0691 | 2.8235 | 2.0168 | 30 | 10 | 21.25 |  | SE | 60 | 102 | 0.91176 | 170 | 68 | 178 | 10.4706 | 777 | 45.7059 | XT2 | 125 | 60 | 60 | 3.5294 | 600 | 35.2941 | TRUE | FALSE | TRUE | -10.4118
50.4 | Size-2 | 45 | 550 - 600 (575) | 3 | 15 | 17 |  | 93 | 305D002 | 14 - 4 | 50 | 19.55 | 21.25 | 29.75 | 60 | 3.0691 | 2.8235 | 2.0168 | 30 | 10 | 21.25 |  | SE | 70 | 102 | 0.91176 | 170 | 68 | 206 | 12.1176 | 863 | 50.7647 | XT2 | 125 | 100 | 100 | 5.8824 | 1000 | 58.8235 | TRUE | TRUE | TRUE | 8.0588
51 | Size-2 | 45 | 550 - 600 (575) | 3 | 20 | 22 |  | 116 | 305D002 | 14 - 4 | 50 | 25.3 | 27.5 | 38.5 | 60 | 2.3715 | 2.1818 | 1.5584 | 30 | 10 | 27.5 |  | SE | 30 | 132 | 0.87879 | 220 | 88 | 87 | 3.9545 | 415 | 18.8636 | XT2 | 125 | 60 | 60 | 2.7273 | 600 | 27.2727 | TRUE | TRUE | TRUE | 8.4091
51.1 | Size-2 | 45 | 550 - 600 (575) | 3 | 20 | 22 |  | 116 | 305D002 | 14 - 4 | 50 | 25.3 | 27.5 | 38.5 | 60 | 2.3715 | 2.1818 | 1.5584 | 30 | 10 | 27.5 |  | SE | 40 | 132 | 0.87879 | 220 | 88 | 118 | 5.3636 | 501 | 22.7727 | XT2 | 125 | 60 | 60 | 2.7273 | 600 | 27.2727 | TRUE | TRUE | TRUE | 4.5
51.2 | Size-2 | 45 | 550 - 600 (575) | 3 | 20 | 22 |  | 116 | 305D002 | 14 - 4 | 50 | 25.3 | 27.5 | 38.5 | 60 | 2.3715 | 2.1818 | 1.5584 | 30 | 10 | 27.5 |  | SE | 50 | 132 | 0.87879 | 220 | 88 | 148 | 6.7273 | 637 | 28.9545 | XT2 | 125 | 60 | 60 | 2.7273 | 600 | 27.2727 | TRUE | FALSE | TRUE | -1.6818
51.3 | Size-2 | 45 | 550 - 600 (575) | 3 | 20 | 22 |  | 116 | 305D002 | 14 - 4 | 50 | 25.3 | 27.5 | 38.5 | 60 | 2.3715 | 2.1818 | 1.5584 | 30 | 10 | 27.5 |  | SE | 60 | 132 | 0.87879 | 220 | 88 | 178 | 8.0909 | 777 | 35.3182 | XT2 | 125 | 60 | 60 | 2.7273 | 600 | 27.2727 | TRUE | FALSE | TRUE | -8.0455
51.4 | Size-2 | 45 | 550 - 600 (575) | 3 | 20 | 22 |  | 116 | 305D002 | 14 - 4 | 50 | 25.3 | 27.5 | 38.5 | 60 | 2.3715 | 2.1818 | 1.5584 | 30 | 10 | 27.5 |  | SE | 70 | 132 | 0.87879 | 220 | 88 | 206 | 9.3636 | 863 | 39.2273 | XT2 | 125 | 100 | 100 | 4.5455 | 1000 | 45.4545 | TRUE | TRUE | TRUE | 6.2273
52 | Size-2 | 45 | 550 - 600 (575) | 3 | 25 | 27 |  | 146 | 305D002 | 14 - 4 | 50 | 31.05 | 33.75 | 47.25 | 60 | 1.9324 | 1.7778 | 1.2698 | 60 | 8 | 33.75 |  | SE | 40 | 162 | 0.90123 | 270 | 108 | 118 | 4.3704 | 501 | 18.5556 | XT2 | 125 | 60 | 60 | 2.2222 | 600 | 22.2222 | TRUE | TRUE | TRUE | 3.6667
52.1 | Size-2 | 45 | 550 - 600 (575) | 3 | 25 | 27 |  | 146 | 305D002 | 14 - 4 | 50 | 31.05 | 33.75 | 47.25 | 60 | 1.9324 | 1.7778 | 1.2698 | 60 | 8 | 33.75 |  | SE | 50 | 162 | 0.90123 | 270 | 108 | 148 | 5.4815 | 637 | 23.5926 | XT2 | 125 | 60 | 60 | 2.2222 | 600 | 22.2222 | TRUE | FALSE | TRUE | -1.3704
52.2 | Size-2 | 45 | 550 - 600 (575) | 3 | 25 | 27 |  | 146 | 305D002 | 14 - 4 | 50 | 31.05 | 33.75 | 47.25 | 60 | 1.9324 | 1.7778 | 1.2698 | 60 | 8 | 33.75 |  | SE | 60 | 162 | 0.90123 | 270 | 108 | 178 | 6.5926 | 777 | 28.7778 | XT2 | 125 | 60 | 60 | 2.2222 | 600 | 22.2222 | TRUE | FALSE | TRUE | -6.5556
52.3 | Size-2 | 45 | 550 - 600 (575) | 3 | 25 | 27 |  | 146 | 305D002 | 14 - 4 | 50 | 31.05 | 33.75 | 47.25 | 60 | 1.9324 | 1.7778 | 1.2698 | 60 | 8 | 33.75 |  | SE | 70 | 162 | 0.90123 | 270 | 108 | 206 | 7.6296 | 863 | 31.963 | XT2 | 125 | 100 | 100 | 3.7037 | 1000 | 37.037 | TRUE | TRUE | TRUE | 5.0741
53 | Size-3 | 90 | 200 | 3 | 15 | 48.3 | 80 | 267 | 305E002 | 8 - 1/0 | 150 | 55.545 | 60.375 | 84.525 | 100 | 1.8003 | 1.6563 | 1.1831 | 100 | 6 | 60.375 |  | SE | 50 | 289.8 | 0.92133 | 483 | 193.2 | 148 | 3.0642 | 637 | 13.1884 | XT2 | 125 | 60 | 60 | 1.2422 | 600 | 12.4224 | TRUE | FALSE | TRUE | -0.76605
53.1 | Size-3 | 90 | 200 | 3 | 15 | 48.3 | 92 | 267 | 305E002 | 8 - 1/0 | 150 | 55.545 | 60.375 | 84.525 | 100 | 1.8003 | 1.6563 | 1.1831 | 100 | 6 | 60.375 |  | SE | 60 | 289.8 | 0.92133 | 483 | 193.2 | 178 | 3.6853 | 777 | 16.087 | XT2 | 125 | 60 | 60 | 1.2422 | 600 | 12.4224 | TRUE | FALSE | TRUE | -3.6646
53.2 | Size-3 | 90 | 200 | 3 | 15 | 48.3 | 120 | 267 | 305E002 | 8 - 1/0 | 150 | 55.545 | 60.375 | 84.525 | 100 | 1.8003 | 1.6563 | 1.1831 | 100 | 6 | 60.375 |  | SE | 70 | 289.8 | 0.92133 | 483 | 193.2 | 206 | 4.265 | 863 | 17.8675 | XT2 | 125 | 100 | 100 | 2.0704 | 1000 | 20.7039 | TRUE | TRUE | TRUE | 2.8364
53.3 | Size-3 | 90 | 200 | 3 | 15 | 48.3 | 120 | 267 | 305E002 | 8 - 1/0 | 150 | 55.545 | 60.375 | 84.525 | 100 | 1.8003 | 1.6563 | 1.1831 | 100 | 6 | 60.375 |  | SE | 80 | 289.8 | 0.92133 | 483 | 193.2 | 236 | 4.8861 | 999 | 20.6832 | XT2 | 125 | 100 | 100 | 2.0704 | 1000 | 20.7039 | TRUE | TRUE | TRUE | 0.020704
53.4 | Size-3 | 90 | 200 | 3 | 15 | 48.3 | 120 | 267 | 305E002 | 8 - 1/0 | 150 | 55.545 | 60.375 | 84.525 | 100 | 1.8003 | 1.6563 | 1.1831 | 100 | 6 | 60.375 |  | SE | 90 | 289.8 | 0.92133 | 483 | 193.2 | 267 | 5.528 | 1138 | 23.5611 | XT2 | 125 | 100 | 100 | 2.0704 | 1000 | 20.7039 | TRUE | FALSE | TRUE | -2.8571
53.5 | Size-3 | 90 | 200 | 3 | 15 | 48.3 | 120 | 267 | 305E002 | 8 - 1/0 | 150 | 55.545 | 60.375 | 84.525 | 100 | 1.8003 | 1.6563 | 1.1831 | 100 | 6 | 60.375 |  | SE | 100 | 289.8 | 0.92133 | 483 | 193.2 | 297 | 6.1491 | 1280 | 26.501 | XT2 | 125 | 100 | 100 | 2.0704 | 1000 | 20.7039 | TRUE | FALSE | TRUE | -5.7971
53.6 | Size-3 | 90 | 200 | 3 | 15 | 48.3 | 130 | 267 | 305E002 | 8 - 1/0 | 150 | 55.545 | 60.375 | 84.525 | 100 | 1.8003 | 1.6563 | 1.1831 | 100 | 6 | 60.375 |  | SE | 110 | 289.8 | 0.92133 | 483 | 193.2 | 328 | 6.7909 | 1426 | 29.5238 | XT2 | 125 | 125 | 125 | 2.588 | 1250 | 25.8799 | TRUE | FALSE | TRUE | -3.6439
53.7 | Size-3 | 90 | 200 | 3 | 15 | 48.3 | 130 | 267 | 305E002 | 8 - 1/0 | 150 | 55.545 | 60.375 | 84.525 | 100 | 1.8003 | 1.6563 | 1.1831 | 100 | 6 | 60.375 |  | SE | 125 | 289.8 | 0.92133 | 483 | 193.2 | 374 | 7.7433 | 1640 | 33.9545 | XT2 | 125 | 125 | 125 | 2.588 | 1250 | 25.8799 | TRUE | FALSE | TRUE | -8.0745
54 | Size-3 | 90 | 200 | 3 | 20 | 62.1 |  | 334 | 305E002 | 8 - 1/0 | 150 | 71.415 | 77.625 | 108.675 | 100 | 1.4003 | 1.2882 | 0.92017 | 100 | 4 | 77.625 |  | SE | 80 | 372.6 | 0.8964 | 621 | 248.4 | 236 | 3.8003 | 999 | 16.087 | XT2 | 125 | 100 | 100 | 1.6103 | 1000 | 16.1031 | TRUE | TRUE | TRUE | 0.016103
54.1 | Size-3 | 90 | 200 | 3 | 20 | 62.1 |  | 334 | 305E002 | 8 - 1/0 | 150 | 71.415 | 77.625 | 108.675 | 100 | 1.4003 | 1.2882 | 0.92017 | 100 | 4 | 77.625 |  | SE | 90 | 372.6 | 0.8964 | 621 | 248.4 | 267 | 4.2995 | 1138 | 18.3253 | XT2 | 125 | 100 | 100 | 1.6103 | 1000 | 16.1031 | TRUE | FALSE | TRUE | -2.2222
54.2 | Size-3 | 90 | 200 | 3 | 20 | 62.1 |  | 334 | 305E002 | 8 - 1/0 | 150 | 71.415 | 77.625 | 108.675 | 100 | 1.4003 | 1.2882 | 0.92017 | 100 | 4 | 77.625 |  | SE | 100 | 372.6 | 0.8964 | 621 | 248.4 | 297 | 4.7826 | 1280 | 20.6119 | XT2 | 125 | 100 | 100 | 1.6103 | 1000 | 16.1031 | TRUE | FALSE | TRUE | -4.5089
54.3 | Size-3 | 90 | 200 | 3 | 20 | 62.1 |  | 334 | 305E002 | 8 - 1/0 | 150 | 71.415 | 77.625 | 108.675 | 100 | 1.4003 | 1.2882 | 0.92017 | 100 | 4 | 77.625 |  | SE | 110 | 372.6 | 0.8964 | 621 | 248.4 | 328 | 5.2818 | 1426 | 22.963 | XT2 | 125 | 125 | 125 | 2.0129 | 1250 | 20.1288 | TRUE | FALSE | TRUE | -2.8341
54.4 | Size-3 | 90 | 200 | 3 | 20 | 62.1 |  | 334 | 305E002 | 8 - 1/0 | 150 | 71.415 | 77.625 | 108.675 | 100 | 1.4003 | 1.2882 | 0.92017 | 100 | 4 | 77.625 |  | SE | 125 | 372.6 | 0.8964 | 621 | 248.4 | 374 | 6.0225 | 1640 | 26.409 | XT2 | 125 | 125 | 125 | 2.0129 | 1250 | 20.1288 | TRUE | FALSE | TRUE | -6.2802
55 | Size-3 | 90 | 200 | 3 | 25 | 78.2 |  | 420 | 305E002 | 8 - 1/0 | 150 | 89.93 | 97.75 | 136.85 | 100 | 1.112 | 1.023 | 0.73073 | 100 | 3 | 97.75 |  | SE | 100 | 469.2 | 0.89514 | 782 | 312.8 | 297 | 3.798 | 1280 | 16.3683 | XT2 | 125 | 100 | 100 | 1.2788 | 1000 | 12.7877 | TRUE | FALSE | TRUE | -3.5806
55.1 | Size-3 | 90 | 200 | 3 | 25 | 78.2 |  | 420 | 305E002 | 8 - 1/0 | 150 | 89.93 | 97.75 | 136.85 | 100 | 1.112 | 1.023 | 0.73073 | 100 | 3 | 97.75 |  | SE | 110 | 469.2 | 0.89514 | 782 | 312.8 | 328 | 4.1944 | 1426 | 18.2353 | XT2 | 125 | 125 | 125 | 1.5985 | 1250 | 15.9847 | TRUE | FALSE | TRUE | -2.2506
55.2 | Size-3 | 90 | 200 | 3 | 25 | 78.2 |  | 420 | 305E002 | 8 - 1/0 | 150 | 89.93 | 97.75 | 136.85 | 100 | 1.112 | 1.023 | 0.73073 | 100 | 3 | 97.75 |  | SE | 125 | 469.2 | 0.89514 | 782 | 312.8 | 374 | 4.7826 | 1640 | 20.9719 | XT2 | 125 | 125 | 125 | 1.5985 | 1250 | 15.9847 | TRUE | FALSE | TRUE | -4.9872
56 | Size-3 | 90 | 208 | 3 | 15 | 46.2 |  | 257 | 305E002 | 8 - 1/0 | 150 | 53.13 | 57.75 | 80.85 | 100 | 1.8822 | 1.7316 | 1.2369 | 100 | 6 | 57.75 |  | SE | 50 | 277.2 | 0.92713 | 462 | 184.8 | 148 | 3.2035 | 637 | 13.7879 | XT2 | 125 | 60 | 60 | 1.2987 | 600 | 12.987 | TRUE | FALSE | TRUE | -0.80087
56.1 | Size-3 | 90 | 208 | 3 | 15 | 46.2 |  | 257 | 305E002 | 8 - 1/0 | 150 | 53.13 | 57.75 | 80.85 | 100 | 1.8822 | 1.7316 | 1.2369 | 100 | 6 | 57.75 |  | SE | 60 | 277.2 | 0.92713 | 462 | 184.8 | 178 | 3.8528 | 777 | 16.8182 | XT2 | 125 | 60 | 60 | 1.2987 | 600 | 12.987 | TRUE | FALSE | TRUE | -3.8312
56.2 | Size-3 | 90 | 208 | 3 | 15 | 46.2 |  | 257 | 305E002 | 8 - 1/0 | 150 | 53.13 | 57.75 | 80.85 | 100 | 1.8822 | 1.7316 | 1.2369 | 100 | 6 | 57.75 |  | SE | 70 | 277.2 | 0.92713 | 462 | 184.8 | 206 | 4.4589 | 863 | 18.6797 | XT2 | 125 | 100 | 100 | 2.1645 | 1000 | 21.645 | TRUE | TRUE | TRUE | 2.9654
56.3 | Size-3 | 90 | 208 | 3 | 15 | 46.2 |  | 257 | 305E002 | 8 - 1/0 | 150 | 53.13 | 57.75 | 80.85 | 100 | 1.8822 | 1.7316 | 1.2369 | 100 | 6 | 57.75 |  | SE | 80 | 277.2 | 0.92713 | 462 | 184.8 | 236 | 5.1082 | 999 | 21.6234 | XT2 | 125 | 100 | 100 | 2.1645 | 1000 | 21.645 | TRUE | TRUE | TRUE | 0.021645
56.4 | Size-3 | 90 | 208 | 3 | 15 | 46.2 |  | 257 | 305E002 | 8 - 1/0 | 150 | 53.13 | 57.75 | 80.85 | 100 | 1.8822 | 1.7316 | 1.2369 | 100 | 6 | 57.75 |  | SE | 90 | 277.2 | 0.92713 | 462 | 184.8 | 267 | 5.7792 | 1138 | 24.632 | XT2 | 125 | 100 | 100 | 2.1645 | 1000 | 21.645 | TRUE | FALSE | TRUE | -2.987
56.5 | Size-3 | 90 | 208 | 3 | 15 | 46.2 |  | 257 | 305E002 | 8 - 1/0 | 150 | 53.13 | 57.75 | 80.85 | 100 | 1.8822 | 1.7316 | 1.2369 | 100 | 6 | 57.75 |  | SE | 100 | 277.2 | 0.92713 | 462 | 184.8 | 297 | 6.4286 | 1280 | 27.7056 | XT2 | 125 | 100 | 100 | 2.1645 | 1000 | 21.645 | TRUE | FALSE | TRUE | -6.0606
56.6 | Size-3 | 90 | 208 | 3 | 15 | 46.2 |  | 257 | 305E002 | 8 - 1/0 | 150 | 53.13 | 57.75 | 80.85 | 100 | 1.8822 | 1.7316 | 1.2369 | 100 | 6 | 57.75 |  | SE | 110 | 277.2 | 0.92713 | 462 | 184.8 | 328 | 7.0996 | 1426 | 30.8658 | XT2 | 125 | 125 | 125 | 2.7056 | 1250 | 27.0563 | TRUE | FALSE | TRUE | -3.8095
56.7 | Size-3 | 90 | 208 | 3 | 15 | 46.2 |  | 257 | 305E002 | 8 - 1/0 | 150 | 53.13 | 57.75 | 80.85 | 100 | 1.8822 | 1.7316 | 1.2369 | 100 | 6 | 57.75 |  | SE | 125 | 277.2 | 0.92713 | 462 | 184.8 | 374 | 8.0952 | 1640 | 35.4978 | XT2 | 125 | 125 | 125 | 2.7056 | 1250 | 27.0563 | TRUE | FALSE | TRUE | -8.4416
57 | Size-3 | 90 | 208 | 3 | 20 | 59.4 |  | 321 | 305E002 | 8 - 1/0 | 150 | 68.31 | 74.25 | 103.95 | 100 | 1.4639 | 1.3468 | 0.962 | 100 | 4 | 74.25 |  | SE | 80 | 356.4 | 0.90067 | 594 | 237.6 | 236 | 3.9731 | 999 | 16.8182 | XT2 | 125 | 100 | 100 | 1.6835 | 1000 | 16.835 | TRUE | TRUE | TRUE | 0.016835
57.1 | Size-3 | 90 | 208 | 3 | 20 | 59.4 |  | 321 | 305E002 | 8 - 1/0 | 150 | 68.31 | 74.25 | 103.95 | 100 | 1.4639 | 1.3468 | 0.962 | 100 | 4 | 74.25 |  | SE | 90 | 356.4 | 0.90067 | 594 | 237.6 | 267 | 4.4949 | 1138 | 19.1582 | XT2 | 125 | 100 | 100 | 1.6835 | 1000 | 16.835 | TRUE | FALSE | TRUE | -2.3232
57.2 | Size-3 | 90 | 208 | 3 | 20 | 59.4 |  | 321 | 305E002 | 8 - 1/0 | 150 | 68.31 | 74.25 | 103.95 | 100 | 1.4639 | 1.3468 | 0.962 | 100 | 4 | 74.25 |  | SE | 100 | 356.4 | 0.90067 | 594 | 237.6 | 297 | 5 | 1280 | 21.5488 | XT2 | 125 | 100 | 100 | 1.6835 | 1000 | 16.835 | TRUE | FALSE | TRUE | -4.7138
57.3 | Size-3 | 90 | 208 | 3 | 20 | 59.4 |  | 321 | 305E002 | 8 - 1/0 | 150 | 68.31 | 74.25 | 103.95 | 100 | 1.4639 | 1.3468 | 0.962 | 100 | 4 | 74.25 |  | SE | 110 | 356.4 | 0.90067 | 594 | 237.6 | 328 | 5.5219 | 1426 | 24.0067 | XT2 | 125 | 125 | 125 | 2.1044 | 1250 | 21.0438 | TRUE | FALSE | TRUE | -2.963
57.4 | Size-3 | 90 | 208 | 3 | 20 | 59.4 |  | 321 | 305E002 | 8 - 1/0 | 150 | 68.31 | 74.25 | 103.95 | 100 | 1.4639 | 1.3468 | 0.962 | 100 | 4 | 74.25 |  | SE | 125 | 356.4 | 0.90067 | 594 | 237.6 | 374 | 6.2963 | 1640 | 27.6094 | XT2 | 125 | 125 | 125 | 2.1044 | 1250 | 21.0438 | TRUE | FALSE | TRUE | -6.5657
58 | Size-3 | 90 | 208 | 3 | 25 | 74.8 |  | 404 | 305E002 | 8 - 1/0 | 150 | 86.02 | 93.5 | 130.9 | 100 | 1.1625 | 1.0695 | 0.76394 | 100 | 3 | 93.5 |  | SE | 100 | 448.8 | 0.90018 | 748 | 299.2 | 297 | 3.9706 | 1280 | 17.1123 | XT2 | 125 | 100 | 100 | 1.3369 | 1000 | 13.369 | TRUE | FALSE | TRUE | -3.7433
58.1 | Size-3 | 90 | 208 | 3 | 25 | 74.8 |  | 404 | 305E002 | 8 - 1/0 | 150 | 86.02 | 93.5 | 130.9 | 100 | 1.1625 | 1.0695 | 0.76394 | 100 | 3 | 93.5 |  | SE | 110 | 448.8 | 0.90018 | 748 | 299.2 | 328 | 4.385 | 1426 | 19.0642 | XT2 | 125 | 125 | 125 | 1.6711 | 1250 | 16.7112 | TRUE | FALSE | TRUE | -2.3529
58.2 | Size-3 | 90 | 208 | 3 | 25 | 74.8 |  | 404 | 305E002 | 8 - 1/0 | 150 | 86.02 | 93.5 | 130.9 | 100 | 1.1625 | 1.0695 | 0.76394 | 100 | 3 | 93.5 |  | SE | 125 | 448.8 | 0.90018 | 748 | 299.2 | 374 | 5 | 1640 | 21.9251 | XT2 | 125 | 125 | 125 | 1.6711 | 1250 | 16.7112 | TRUE | FALSE | TRUE | -5.2139
59 | Size-3 | 90 | 220 - 240 (230) | 3 | 20 | 54 |  | 290 | 305E002 | 8 - 1/0 | 150 | 62.1 | 67.5 | 94.5 | 100 | 1.6103 | 1.4815 | 1.0582 | 100 | 4 | 67.5 |  | SE | 50 | 324 | 0.89506 | 540 | 216 | 148 | 2.7407 | 637 | 11.7963 | XT2 | 125 | 60 | 60 | 1.1111 | 600 | 11.1111 | TRUE | FALSE | TRUE | -0.68519
59.1 | Size-3 | 90 | 220 - 240 (230) | 3 | 20 | 54 |  | 290 | 305E002 | 8 - 1/0 | 150 | 62.1 | 67.5 | 94.5 | 100 | 1.6103 | 1.4815 | 1.0582 | 100 | 4 | 67.5 |  | SE | 60 | 324 | 0.89506 | 540 | 216 | 178 | 3.2963 | 777 | 14.3889 | XT2 | 125 | 60 | 60 | 1.1111 | 600 | 11.1111 | TRUE | FALSE | TRUE | -3.2778
59.2 | Size-3 | 90 | 220 - 240 (230) | 3 | 20 | 54 |  | 290 | 305E002 | 8 - 1/0 | 150 | 62.1 | 67.5 | 94.5 | 100 | 1.6103 | 1.4815 | 1.0582 | 100 | 4 | 67.5 |  | SE | 70 | 324 | 0.89506 | 540 | 216 | 206 | 3.8148 | 863 | 15.9815 | XT2 | 125 | 100 | 100 | 1.8519 | 1000 | 18.5185 | TRUE | TRUE | TRUE | 2.537
59.3 | Size-3 | 90 | 220 - 240 (230) | 3 | 20 | 54 |  | 290 | 305E002 | 8 - 1/0 | 150 | 62.1 | 67.5 | 94.5 | 100 | 1.6103 | 1.4815 | 1.0582 | 100 | 4 | 67.5 |  | SE | 80 | 324 | 0.89506 | 540 | 216 | 236 | 4.3704 | 999 | 18.5 | XT2 | 125 | 100 | 100 | 1.8519 | 1000 | 18.5185 | TRUE | TRUE | TRUE | 0.018519
59.4 | Size-3 | 90 | 220 - 240 (230) | 3 | 20 | 54 |  | 290 | 305E002 | 8 - 1/0 | 150 | 62.1 | 67.5 | 94.5 | 100 | 1.6103 | 1.4815 | 1.0582 | 100 | 4 | 67.5 |  | SE | 90 | 324 | 0.89506 | 540 | 216 | 267 | 4.9444 | 1138 | 21.0741 | XT2 | 125 | 100 | 100 | 1.8519 | 1000 | 18.5185 | TRUE | FALSE | TRUE | -2.5556
59.5 | Size-3 | 90 | 220 - 240 (230) | 3 | 20 | 54 |  | 290 | 305E002 | 8 - 1/0 | 150 | 62.1 | 67.5 | 94.5 | 100 | 1.6103 | 1.4815 | 1.0582 | 100 | 4 | 67.5 |  | SE | 100 | 324 | 0.89506 | 540 | 216 | 297 | 5.5 | 1280 | 23.7037 | XT2 | 125 | 100 | 100 | 1.8519 | 1000 | 18.5185 | TRUE | FALSE | TRUE | -5.1852
59.6 | Size-3 | 90 | 220 - 240 (230) | 3 | 20 | 54 |  | 290 | 305E002 | 8 - 1/0 | 150 | 62.1 | 67.5 | 94.5 | 100 | 1.6103 | 1.4815 | 1.0582 | 100 | 4 | 67.5 |  | SE | 110 | 324 | 0.89506 | 540 | 216 | 328 | 6.0741 | 1426 | 26.4074 | XT2 | 125 | 125 | 125 | 2.3148 | 1250 | 23.1481 | TRUE | FALSE | TRUE | -3.2593
59.7 | Size-3 | 90 | 220 - 240 (230) | 3 | 20 | 54 |  | 290 | 305E002 | 8 - 1/0 | 150 | 62.1 | 67.5 | 94.5 | 100 | 1.6103 | 1.4815 | 1.0582 | 100 | 4 | 67.5 |  | SE | 125 | 324 | 0.89506 | 540 | 216 | 374 | 6.9259 | 1640 | 30.3704 | XT2 | 125 | 125 | 125 | 2.3148 | 1250 | 23.1481 | TRUE | FALSE | TRUE | -7.2222
60 | Size-3 | 90 | 220 - 240 (230) | 3 | 25 | 68 |  | 365 | 305E002 | 8 - 1/0 | 150 | 78.2 | 85 | 119 | 100 | 1.2788 | 1.1765 | 0.84034 | 100 | 4 | 85 |  | SE | 90 | 408 | 0.89461 | 680 | 272 | 267 | 3.9265 | 1138 | 16.7353 | XT2 | 125 | 100 | 100 | 1.4706 | 1000 | 14.7059 | TRUE | FALSE | TRUE | -2.0294
60.1 | Size-3 | 90 | 220 - 240 (230) | 3 | 25 | 68 |  | 365 | 305E002 | 8 - 1/0 | 150 | 78.2 | 85 | 119 | 100 | 1.2788 | 1.1765 | 0.84034 | 100 | 4 | 85 |  | SE | 100 | 408 | 0.89461 | 680 | 272 | 297 | 4.3676 | 1280 | 18.8235 | XT2 | 125 | 100 | 100 | 1.4706 | 1000 | 14.7059 | TRUE | FALSE | TRUE | -4.1176
60.2 | Size-3 | 90 | 220 - 240 (230) | 3 | 25 | 68 |  | 365 | 305E002 | 8 - 1/0 | 150 | 78.2 | 85 | 119 | 100 | 1.2788 | 1.1765 | 0.84034 | 100 | 4 | 85 |  | SE | 110 | 408 | 0.89461 | 680 | 272 | 328 | 4.8235 | 1426 | 20.9706 | XT2 | 125 | 125 | 125 | 1.8382 | 1250 | 18.3824 | TRUE | FALSE | TRUE | -2.5882
60.3 | Size-3 | 90 | 220 - 240 (230) | 3 | 25 | 68 |  | 365 | 305E002 | 8 - 1/0 | 150 | 78.2 | 85 | 119 | 100 | 1.2788 | 1.1765 | 0.84034 | 100 | 4 | 85 |  | SE | 125 | 408 | 0.89461 | 680 | 272 | 374 | 5.5 | 1640 | 24.1176 | XT2 | 125 | 125 | 125 | 1.8382 | 1250 | 18.3824 | TRUE | FALSE | TRUE | -5.7353
61 | Size-3 | 90 | 220 - 240 (230) | 3 | 30 | 80 |  | 435 | 305E002 | 8 - 1/0 | 150 | 92 | 100 | 140 | 100 | 1.087 | 1 | 0.71429 | 100 | 3 | 100 |  | SE | 100 | 480 | 0.90625 | 800 | 320 | 297 | 3.7125 | 1280 | 16 | XT2 | 125 | 100 | 100 | 1.25 | 1000 | 12.5 | TRUE | FALSE | TRUE | -3.5
61.1 | Size-3 | 90 | 220 - 240 (230) | 3 | 30 | 80 |  | 435 | 305E002 | 8 - 1/0 | 150 | 92 | 100 | 140 | 100 | 1.087 | 1 | 0.71429 | 100 | 3 | 100 |  | SE | 110 | 480 | 0.90625 | 800 | 320 | 328 | 4.1 | 1426 | 17.825 | XT2 | 125 | 125 | 125 | 1.5625 | 1250 | 15.625 | TRUE | FALSE | TRUE | -2.2
61.2 | Size-3 | 90 | 220 - 240 (230) | 3 | 30 | 80 |  | 435 | 305E002 | 8 - 1/0 | 150 | 92 | 100 | 140 | 100 | 1.087 | 1 | 0.71429 | 100 | 3 | 100 |  | SE | 125 | 480 | 0.90625 | 800 | 320 | 374 | 4.675 | 1640 | 20.5 | XT2 | 125 | 125 | 125 | 1.5625 | 1250 | 15.625 | TRUE | FALSE | TRUE | -4.875
62 | Size-3 | 90 | 440 - 480 (460) | 3 | 30 | 40 |  | 218 | 305E002 | 8 - 1/0 | 150 | 46 | 50 | 70 | 100 | 2.1739 | 2 | 1.4286 | 60 | 8 | 50 |  | SE | 50 | 240 | 0.90833 | 400 | 160 | 148 | 3.7 | 637 | 15.925 | XT2 | 125 | 60 | 60 | 1.5 | 600 | 15 | TRUE | FALSE | TRUE | -0.925
62.1 | Size-3 | 90 | 440 - 480 (460) | 3 | 30 | 40 |  | 218 | 305E002 | 8 - 1/0 | 150 | 46 | 50 | 70 | 100 | 2.1739 | 2 | 1.4286 | 60 | 8 | 50 |  | SE | 60 | 240 | 0.90833 | 400 | 160 | 178 | 4.45 | 777 | 19.425 | XT2 | 125 | 60 | 60 | 1.5 | 600 | 15 | TRUE | FALSE | TRUE | -4.425
62.2 | Size-3 | 90 | 440 - 480 (460) | 3 | 30 | 40 |  | 218 | 305E002 | 8 - 1/0 | 150 | 46 | 50 | 70 | 100 | 2.1739 | 2 | 1.4286 | 60 | 8 | 50 |  | SE | 70 | 240 | 0.90833 | 400 | 160 | 206 | 5.15 | 863 | 21.575 | XT2 | 125 | 100 | 100 | 2.5 | 1000 | 25 | TRUE | TRUE | TRUE | 3.425
62.3 | Size-3 | 90 | 440 - 480 (460) | 3 | 30 | 40 |  | 218 | 305E002 | 8 - 1/0 | 150 | 46 | 50 | 70 | 100 | 2.1739 | 2 | 1.4286 | 60 | 8 | 50 |  | SE | 80 | 240 | 0.90833 | 400 | 160 | 236 | 5.9 | 999 | 24.975 | XT2 | 125 | 100 | 100 | 2.5 | 1000 | 25 | TRUE | TRUE | TRUE | 0.025
62.4 | Size-3 | 90 | 440 - 480 (460) | 3 | 30 | 40 |  | 218 | 305E002 | 8 - 1/0 | 150 | 46 | 50 | 70 | 100 | 2.1739 | 2 | 1.4286 | 60 | 8 | 50 |  | SE | 90 | 240 | 0.90833 | 400 | 160 | 267 | 6.675 | 1138 | 28.45 | XT2 | 125 | 100 | 100 | 2.5 | 1000 | 25 | TRUE | FALSE | TRUE | -3.45
62.5 | Size-3 | 90 | 440 - 480 (460) | 3 | 30 | 40 |  | 218 | 305E002 | 8 - 1/0 | 150 | 46 | 50 | 70 | 100 | 2.1739 | 2 | 1.4286 | 60 | 8 | 50 |  | SE | 100 | 240 | 0.90833 | 400 | 160 | 297 | 7.425 | 1280 | 32 | XT2 | 125 | 100 | 100 | 2.5 | 1000 | 25 | TRUE | FALSE | TRUE | -7
62.6 | Size-3 | 90 | 440 - 480 (460) | 3 | 30 | 40 |  | 218 | 305E002 | 8 - 1/0 | 150 | 46 | 50 | 70 | 100 | 2.1739 | 2 | 1.4286 | 60 | 8 | 50 |  | SE | 110 | 240 | 0.90833 | 400 | 160 | 328 | 8.2 | 1426 | 35.65 | XT2 | 125 | 125 | 125 | 3.125 | 1250 | 31.25 | TRUE | FALSE | TRUE | -4.4
62.7 | Size-3 | 90 | 440 - 480 (460) | 3 | 30 | 40 |  | 218 | 305E002 | 8 - 1/0 | 150 | 46 | 50 | 70 | 100 | 2.1739 | 2 | 1.4286 | 60 | 8 | 50 |  | SE | 125 | 240 | 0.90833 | 400 | 160 | 374 | 9.35 | 1640 | 41 | XT2 | 125 | 125 | 125 | 3.125 | 1250 | 31.25 | TRUE | FALSE | TRUE | -9.75
63 | Size-3 | 90 | 440 - 480 (460) | 3 | 40 | 52 |  | 290 | 305E002 | 8 - 1/0 | 150 | 59.8 | 65 | 91 | 100 | 1.6722 | 1.5385 | 1.0989 | 100 | 6 | 65 |  | SE | 70 | 312 | 0.92949 | 520 | 208 | 206 | 3.9615 | 863 | 16.5962 | XT2 | 125 | 100 | 100 | 1.9231 | 1000 | 19.2308 | TRUE | TRUE | TRUE | 2.6346
63.1 | Size-3 | 90 | 440 - 480 (460) | 3 | 40 | 52 |  | 290 | 305E002 | 8 - 1/0 | 150 | 59.8 | 65 | 91 | 100 | 1.6722 | 1.5385 | 1.0989 | 100 | 6 | 65 |  | SE | 80 | 312 | 0.92949 | 520 | 208 | 236 | 4.5385 | 999 | 19.2115 | XT2 | 125 | 100 | 100 | 1.9231 | 1000 | 19.2308 | TRUE | TRUE | TRUE | 0.019231
63.2 | Size-3 | 90 | 440 - 480 (460) | 3 | 40 | 52 |  | 290 | 305E002 | 8 - 1/0 | 150 | 59.8 | 65 | 91 | 100 | 1.6722 | 1.5385 | 1.0989 | 100 | 6 | 65 |  | SE | 90 | 312 | 0.92949 | 520 | 208 | 267 | 5.1346 | 1138 | 21.8846 | XT2 | 125 | 100 | 100 | 1.9231 | 1000 | 19.2308 | TRUE | FALSE | TRUE | -2.6538
63.3 | Size-3 | 90 | 440 - 480 (460) | 3 | 40 | 52 |  | 290 | 305E002 | 8 - 1/0 | 150 | 59.8 | 65 | 91 | 100 | 1.6722 | 1.5385 | 1.0989 | 100 | 6 | 65 |  | SE | 100 | 312 | 0.92949 | 520 | 208 | 297 | 5.7115 | 1280 | 24.6154 | XT2 | 125 | 100 | 100 | 1.9231 | 1000 | 19.2308 | TRUE | FALSE | TRUE | -5.3846
63.4 | Size-3 | 90 | 440 - 480 (460) | 3 | 40 | 52 |  | 290 | 305E002 | 8 - 1/0 | 150 | 59.8 | 65 | 91 | 100 | 1.6722 | 1.5385 | 1.0989 | 100 | 6 | 65 |  | SE | 110 | 312 | 0.92949 | 520 | 208 | 328 | 6.3077 | 1426 | 27.4231 | XT2 | 125 | 125 | 125 | 2.4038 | 1250 | 24.0385 | TRUE | FALSE | TRUE | -3.3846
63.5 | Size-3 | 90 | 440 - 480 (460) | 3 | 40 | 52 |  | 290 | 305E002 | 8 - 1/0 | 150 | 59.8 | 65 | 91 | 100 | 1.6722 | 1.5385 | 1.0989 | 100 | 6 | 65 |  | SE | 125 | 312 | 0.92949 | 520 | 208 | 374 | 7.1923 | 1640 | 31.5385 | XT2 | 125 | 125 | 125 | 2.4038 | 1250 | 24.0385 | TRUE | FALSE | TRUE | -7.5
64 | Size-3 | 90 | 440 - 480 (460) | 3 | 50 | 65 |  | 363 | 305E002 | 8 - 1/0 | 150 | 74.75 | 81.25 | 113.75 | 100 | 1.3378 | 1.2308 | 0.87912 | 100 | 4 | 81.25 |  | SE | 90 | 390 | 0.93077 | 650 | 260 | 267 | 4.1077 | 1138 | 17.5077 | XT2 | 125 | 100 | 100 | 1.5385 | 1000 | 15.3846 | TRUE | FALSE | TRUE | -2.1231
64.1 | Size-3 | 90 | 440 - 480 (460) | 3 | 50 | 65 |  | 363 | 305E002 | 8 - 1/0 | 150 | 74.75 | 81.25 | 113.75 | 100 | 1.3378 | 1.2308 | 0.87912 | 100 | 4 | 81.25 |  | SE | 100 | 390 | 0.93077 | 650 | 260 | 297 | 4.5692 | 1280 | 19.6923 | XT2 | 125 | 100 | 100 | 1.5385 | 1000 | 15.3846 | TRUE | FALSE | TRUE | -4.3077
64.2 | Size-3 | 90 | 440 - 480 (460) | 3 | 50 | 65 |  | 363 | 305E002 | 8 - 1/0 | 150 | 74.75 | 81.25 | 113.75 | 100 | 1.3378 | 1.2308 | 0.87912 | 100 | 4 | 81.25 |  | SE | 110 | 390 | 0.93077 | 650 | 260 | 328 | 5.0462 | 1426 | 21.9385 | XT2 | 125 | 125 | 125 | 1.9231 | 1250 | 19.2308 | TRUE | FALSE | TRUE | -2.7077
64.3 | Size-3 | 90 | 440 - 480 (460) | 3 | 50 | 65 |  | 363 | 305E002 | 8 - 1/0 | 150 | 74.75 | 81.25 | 113.75 | 100 | 1.3378 | 1.2308 | 0.87912 | 100 | 4 | 81.25 |  | SE | 125 | 390 | 0.93077 | 650 | 260 | 374 | 5.7538 | 1640 | 25.2308 | XT2 | 125 | 125 | 125 | 1.9231 | 1250 | 19.2308 | TRUE | FALSE | TRUE | -6
65 | Size-3 | 90 | 550 - 600 (575) | 3 | 30 | 32 |  | 174 | 305E002 | 8 - 1/0 | 150 | 36.8 | 40 | 56 | 100 | 2.7174 | 2.5 | 1.7857 | 60 | 8 | 40 |  | SE | 50 | 192 | 0.90625 | 320 | 128 | 148 | 4.625 | 637 | 19.9062 | XT2 | 125 | 60 | 60 | 1.875 | 600 | 18.75 | TRUE | FALSE | TRUE | -1.1562
65.1 | Size-3 | 90 | 550 - 600 (575) | 3 | 30 | 32 |  | 174 | 305E002 | 8 - 1/0 | 150 | 36.8 | 40 | 56 | 100 | 2.7174 | 2.5 | 1.7857 | 60 | 8 | 40 |  | SE | 60 | 192 | 0.90625 | 320 | 128 | 178 | 5.5625 | 777 | 24.2812 | XT2 | 125 | 60 | 60 | 1.875 | 600 | 18.75 | TRUE | FALSE | TRUE | -5.5312
65.2 | Size-3 | 90 | 550 - 600 (575) | 3 | 30 | 32 |  | 174 | 305E002 | 8 - 1/0 | 150 | 36.8 | 40 | 56 | 100 | 2.7174 | 2.5 | 1.7857 | 60 | 8 | 40 |  | SE | 70 | 192 | 0.90625 | 320 | 128 | 206 | 6.4375 | 863 | 26.9688 | XT2 | 125 | 100 | 100 | 3.125 | 1000 | 31.25 | TRUE | TRUE | TRUE | 4.2812
65.3 | Size-3 | 90 | 550 - 600 (575) | 3 | 30 | 32 |  | 174 | 305E002 | 8 - 1/0 | 150 | 36.8 | 40 | 56 | 100 | 2.7174 | 2.5 | 1.7857 | 60 | 8 | 40 |  | SE | 80 | 192 | 0.90625 | 320 | 128 | 236 | 7.375 | 999 | 31.2188 | XT2 | 125 | 100 | 100 | 3.125 | 1000 | 31.25 | TRUE | TRUE | TRUE | 0.03125
65.4 | Size-3 | 90 | 550 - 600 (575) | 3 | 30 | 32 |  | 174 | 305E002 | 8 - 1/0 | 150 | 36.8 | 40 | 56 | 100 | 2.7174 | 2.5 | 1.7857 | 60 | 8 | 40 |  | SE | 90 | 192 | 0.90625 | 320 | 128 | 267 | 8.3438 | 1138 | 35.5625 | XT2 | 125 | 100 | 100 | 3.125 | 1000 | 31.25 | TRUE | FALSE | TRUE | -4.3125
65.5 | Size-3 | 90 | 550 - 600 (575) | 3 | 30 | 32 |  | 174 | 305E002 | 8 - 1/0 | 150 | 36.8 | 40 | 56 | 100 | 2.7174 | 2.5 | 1.7857 | 60 | 8 | 40 |  | SE | 100 | 192 | 0.90625 | 320 | 128 | 297 | 9.2812 | 1280 | 40 | XT2 | 125 | 100 | 100 | 3.125 | 1000 | 31.25 | TRUE | FALSE | TRUE | -8.75
65.6 | Size-3 | 90 | 550 - 600 (575) | 3 | 30 | 32 |  | 174 | 305E002 | 8 - 1/0 | 150 | 36.8 | 40 | 56 | 100 | 2.7174 | 2.5 | 1.7857 | 60 | 8 | 40 |  | SE | 110 | 192 | 0.90625 | 320 | 128 | 328 | 10.25 | 1426 | 44.5625 | XT2 | 125 | 125 | 125 | 3.9062 | 1250 | 39.0625 | TRUE | FALSE | TRUE | -5.5
65.7 | Size-3 | 90 | 550 - 600 (575) | 3 | 30 | 32 |  | 174 | 305E002 | 8 - 1/0 | 150 | 36.8 | 40 | 56 | 100 | 2.7174 | 2.5 | 1.7857 | 60 | 8 | 40 |  | SE | 125 | 192 | 0.90625 | 320 | 128 | 374 | 11.6875 | 1640 | 51.25 | XT2 | 125 | 125 | 125 | 3.9062 | 1250 | 39.0625 | TRUE | FALSE | TRUE | -12.1875
66 | Size-3 | 90 | 550 - 600 (575) | 3 | 40 | 41 |  | 232 | 305E002 | 8 - 1/0 | 150 | 47.15 | 51.25 | 71.75 | 100 | 2.1209 | 1.9512 | 1.3937 | 60 | 6 | 51.25 |  | SE | 60 | 246 | 0.94309 | 410 | 164 | 178 | 4.3415 | 777 | 18.9512 | XT2 | 125 | 60 | 60 | 1.4634 | 600 | 14.6341 | TRUE | FALSE | TRUE | -4.3171
66.1 | Size-3 | 90 | 550 - 600 (575) | 3 | 40 | 41 |  | 232 | 305E002 | 8 - 1/0 | 150 | 47.15 | 51.25 | 71.75 | 100 | 2.1209 | 1.9512 | 1.3937 | 60 | 6 | 51.25 |  | SE | 70 | 246 | 0.94309 | 410 | 164 | 206 | 5.0244 | 863 | 21.0488 | XT2 | 125 | 100 | 100 | 2.439 | 1000 | 24.3902 | TRUE | TRUE | TRUE | 3.3415
66.2 | Size-3 | 90 | 550 - 600 (575) | 3 | 40 | 41 |  | 232 | 305E002 | 8 - 1/0 | 150 | 47.15 | 51.25 | 71.75 | 100 | 2.1209 | 1.9512 | 1.3937 | 60 | 6 | 51.25 |  | SE | 80 | 246 | 0.94309 | 410 | 164 | 236 | 5.7561 | 999 | 24.3659 | XT2 | 125 | 100 | 100 | 2.439 | 1000 | 24.3902 | TRUE | TRUE | TRUE | 0.02439
66.3 | Size-3 | 90 | 550 - 600 (575) | 3 | 40 | 41 |  | 232 | 305E002 | 8 - 1/0 | 150 | 47.15 | 51.25 | 71.75 | 100 | 2.1209 | 1.9512 | 1.3937 | 60 | 6 | 51.25 |  | SE | 90 | 246 | 0.94309 | 410 | 164 | 267 | 6.5122 | 1138 | 27.7561 | XT2 | 125 | 100 | 100 | 2.439 | 1000 | 24.3902 | TRUE | FALSE | TRUE | -3.3659
66.4 | Size-3 | 90 | 550 - 600 (575) | 3 | 40 | 41 |  | 232 | 305E002 | 8 - 1/0 | 150 | 47.15 | 51.25 | 71.75 | 100 | 2.1209 | 1.9512 | 1.3937 | 60 | 6 | 51.25 |  | SE | 100 | 246 | 0.94309 | 410 | 164 | 297 | 7.2439 | 1280 | 31.2195 | XT2 | 125 | 100 | 100 | 2.439 | 1000 | 24.3902 | TRUE | FALSE | TRUE | -6.8293
66.5 | Size-3 | 90 | 550 - 600 (575) | 3 | 40 | 41 |  | 232 | 305E002 | 8 - 1/0 | 150 | 47.15 | 51.25 | 71.75 | 100 | 2.1209 | 1.9512 | 1.3937 | 60 | 6 | 51.25 |  | SE | 110 | 246 | 0.94309 | 410 | 164 | 328 | 8 | 1426 | 34.7805 | XT2 | 125 | 125 | 125 | 3.0488 | 1250 | 30.4878 | TRUE | FALSE | TRUE | -4.2927
66.6 | Size-3 | 90 | 550 - 600 (575) | 3 | 40 | 41 |  | 232 | 305E002 | 8 - 1/0 | 150 | 47.15 | 51.25 | 71.75 | 100 | 2.1209 | 1.9512 | 1.3937 | 60 | 6 | 51.25 |  | SE | 125 | 246 | 0.94309 | 410 | 164 | 374 | 9.122 | 1640 | 40 | XT2 | 125 | 125 | 125 | 3.0488 | 1250 | 30.4878 | TRUE | FALSE | TRUE | -9.5122
67 | Size-3 | 90 | 550 - 600 (575) | 3 | 50 | 52 |  | 290 | 305E002 | 8 - 1/0 | 150 | 59.8 | 65 | 91 | 100 | 1.6722 | 1.5385 | 1.0989 | 100 | 6 | 65 |  | SE | 70 | 312 | 0.92949 | 520 | 208 | 206 | 3.9615 | 863 | 16.5962 | XT2 | 125 | 100 | 100 | 1.9231 | 1000 | 19.2308 | TRUE | TRUE | TRUE | 2.6346
67.1 | Size-3 | 90 | 550 - 600 (575) | 3 | 50 | 52 |  | 290 | 305E002 | 8 - 1/0 | 150 | 59.8 | 65 | 91 | 100 | 1.6722 | 1.5385 | 1.0989 | 100 | 6 | 65 |  | SE | 80 | 312 | 0.92949 | 520 | 208 | 236 | 4.5385 | 999 | 19.2115 | XT2 | 125 | 100 | 100 | 1.9231 | 1000 | 19.2308 | TRUE | TRUE | TRUE | 0.019231
67.2 | Size-3 | 90 | 550 - 600 (575) | 3 | 50 | 52 |  | 290 | 305E002 | 8 - 1/0 | 150 | 59.8 | 65 | 91 | 100 | 1.6722 | 1.5385 | 1.0989 | 100 | 6 | 65 |  | SE | 90 | 312 | 0.92949 | 520 | 208 | 267 | 5.1346 | 1138 | 21.8846 | XT2 | 125 | 100 | 100 | 1.9231 | 1000 | 19.2308 | TRUE | FALSE | TRUE | -2.6538
67.3 | Size-3 | 90 | 550 - 600 (575) | 3 | 50 | 52 |  | 290 | 305E002 | 8 - 1/0 | 150 | 59.8 | 65 | 91 | 100 | 1.6722 | 1.5385 | 1.0989 | 100 | 6 | 65 |  | SE | 100 | 312 | 0.92949 | 520 | 208 | 297 | 5.7115 | 1280 | 24.6154 | XT2 | 125 | 100 | 100 | 1.9231 | 1000 | 19.2308 | TRUE | FALSE | TRUE | -5.3846
67.4 | Size-3 | 90 | 550 - 600 (575) | 3 | 50 | 52 |  | 290 | 305E002 | 8 - 1/0 | 150 | 59.8 | 65 | 91 | 100 | 1.6722 | 1.5385 | 1.0989 | 100 | 6 | 65 |  | SE | 110 | 312 | 0.92949 | 520 | 208 | 328 | 6.3077 | 1426 | 27.4231 | XT2 | 125 | 125 | 125 | 2.4038 | 1250 | 24.0385 | TRUE | FALSE | TRUE | -3.3846
67.5 | Size-3 | 90 | 550 - 600 (575) | 3 | 50 | 52 |  | 290 | 305E002 | 8 - 1/0 | 150 | 59.8 | 65 | 91 | 100 | 1.6722 | 1.5385 | 1.0989 | 100 | 6 | 65 |  | SE | 125 | 312 | 0.92949 | 520 | 208 | 374 | 7.1923 | 1640 | 31.5385 | XT2 | 125 | 125 | 125 | 2.4038 | 1250 | 24.0385 | TRUE | FALSE | TRUE | -7.5
68 | Size-4 | 135 | 200 | 3 | 30 | 92 | 130 | 500 | 305F002 | 8 - 3/0 | 200 | 105.8 | 115 | 161 | 200 | 1.8904 | 1.7391 | 1.2422 | 200 | 2 | 115 |  | SF | 100 | 552 | 0.9058 | 920 | 368 | 297 | 3.2283 | 1280 | 13.913 | XT4 | 250 | 100 | 100 | 1.087 | 1000 | 10.8696 | TRUE | FALSE | TRUE | -3.0435
68.1 | Size-4 | 135 | 200 | 3 | 30 | 92 | 150 | 500 | 305F002 | 8 - 3/0 | 200 | 105.8 | 115 | 161 | 200 | 1.8904 | 1.7391 | 1.2422 | 200 | 2 | 115 |  | SF | 110 | 552 | 0.9058 | 920 | 368 | 328 | 3.5652 | 1426 | 15.5 | XT4 | 250 | 125 | 125 | 1.3587 | 1250 | 13.587 | TRUE | FALSE | TRUE | -1.913
68.2 | Size-4 | 135 | 200 | 3 | 30 | 92 | 150 | 500 | 305F002 | 8 - 3/0 | 200 | 105.8 | 115 | 161 | 200 | 1.8904 | 1.7391 | 1.2422 | 200 | 2 | 115 |  | SF | 125 | 552 | 0.9058 | 920 | 368 | 374 | 4.0652 | 1640 | 17.8261 | XT2 | 125 | 125 | 125 | 1.3587 | 1250 | 13.587 | TRUE | FALSE | TRUE | -4.2391
68.3 | Size-4 | 135 | 200 | 3 | 30 | 92 | 177 | 500 | 305F002 | 8 - 3/0 | 200 | 105.8 | 115 | 161 | 200 | 1.8904 | 1.7391 | 1.2422 | 200 | 2 | 115 |  | SF | 150 | 552 | 0.9058 | 920 | 368 | 450 | 4.8913 | 1991 | 21.6413 | XT4 | 250 | 150 | 150 | 1.6304 | 1500 | 16.3043 | TRUE | FALSE | TRUE | -5.337
68.4 | Size-4 | 135 | 200 | 3 | 30 | 92 | 221 | 500 | 305F002 | 8 - 3/0 | 200 | 105.8 | 115 | 161 | 200 | 1.8904 | 1.7391 | 1.2422 | 200 | 2 | 115 |  | SF | 175 | 552 | 0.9058 | 920 | 368 | 515 | 5.5978 | 1750 | 19.0217 | XT4 | 250 | 200 | 200 | 2.1739 | 2000 | 21.7391 | TRUE | TRUE | TRUE | 2.7174
68.5 | Size-4 | 135 | 200 | 3 | 30 | 92 | 221 | 500 | 305F002 | 8 - 3/0 | 200 | 105.8 | 115 | 161 | 200 | 1.8904 | 1.7391 | 1.2422 | 200 | 2 | 115 |  | SF | 200 | 552 | 0.9058 | 920 | 368 | 590 | 6.413 | 2000 | 21.7391 | XT4 | 250 | 200 | 200 | 2.1739 | 2000 | 21.7391 | TRUE | FALSE | TRUE | 0
69 | Size-4 | 135 | 200 | 3 | 40 | 120 |  | 667 | 305F002 | 8 - 3/0 | 200 | 138 | 150 | 210 | 200 | 1.4493 | 1.3333 | 0.95238 | 200 | 1/0 | 150 |  | SF | 150 | 720 | 0.92639 | 1200 | 360 | 450 | 3.75 | 1991 | 16.5917 | XT4 | 250 | 150 | 150 | 1.25 | 1500 | 12.5 | TRUE | FALSE | TRUE | -4.0917
69.1 | Size-4 | 135 | 200 | 3 | 40 | 120 |  | 667 | 305F002 | 8 - 3/0 | 200 | 138 | 150 | 210 | 200 | 1.4493 | 1.3333 | 0.95238 | 200 | 1/0 | 150 |  | SF | 175 | 720 | 0.92639 | 1200 | 360 | 515 | 4.2917 | 1750 | 14.5833 | XT4 | 250 | 200 | 200 | 1.6667 | 2000 | 16.6667 | TRUE | TRUE | TRUE | 2.0833
69.2 | Size-4 | 135 | 200 | 3 | 40 | 120 |  | 667 | 305F002 | 8 - 3/0 | 200 | 138 | 150 | 210 | 200 | 1.4493 | 1.3333 | 0.95238 | 200 | 1/0 | 150 |  | SF | 200 | 720 | 0.92639 | 1200 | 360 | 590 | 4.9167 | 2000 | 16.6667 | XT4 | 250 | 200 | 200 | 1.6667 | 2000 | 16.6667 | TRUE | FALSE | TRUE | 0
70 | Size-4 | 135 | 208 | 3 | 30 | 88 |  | 481 | 305F002 | 8 - 3/0 | 200 | 101.2 | 110 | 154 | 200 | 1.9763 | 1.8182 | 1.2987 | 200 | 2 | 110 |  | SF | 100 | 528 | 0.91098 | 880 | 352 | 297 | 3.375 | 1280 | 14.5455 | XT4 | 250 | 100 | 100 | 1.1364 | 1000 | 11.3636 | TRUE | FALSE | TRUE | -3.1818
70.1 | Size-4 | 135 | 208 | 3 | 30 | 88 |  | 481 | 305F002 | 8 - 3/0 | 200 | 101.2 | 110 | 154 | 200 | 1.9763 | 1.8182 | 1.2987 | 200 | 2 | 110 |  | SF | 110 | 528 | 0.91098 | 880 | 352 | 328 | 3.7273 | 1426 | 16.2045 | XT4 | 250 | 125 | 125 | 1.4205 | 1250 | 14.2045 | TRUE | FALSE | TRUE | -2
70.2 | Size-4 | 135 | 208 | 3 | 30 | 88 |  | 481 | 305F002 | 8 - 3/0 | 200 | 101.2 | 110 | 154 | 200 | 1.9763 | 1.8182 | 1.2987 | 200 | 2 | 110 |  | SF | 125 | 528 | 0.91098 | 880 | 352 | 374 | 4.25 | 1640 | 18.6364 | XT2 | 125 | 125 | 125 | 1.4205 | 1250 | 14.2045 | TRUE | FALSE | TRUE | -4.4318
70.3 | Size-4 | 135 | 208 | 3 | 30 | 88 |  | 481 | 305F002 | 8 - 3/0 | 200 | 101.2 | 110 | 154 | 200 | 1.9763 | 1.8182 | 1.2987 | 200 | 2 | 110 |  | SF | 150 | 528 | 0.91098 | 880 | 352 | 450 | 5.1136 | 1991 | 22.625 | XT4 | 250 | 150 | 150 | 1.7045 | 1500 | 17.0455 | TRUE | FALSE | TRUE | -5.5795
70.4 | Size-4 | 135 | 208 | 3 | 30 | 88 |  | 481 | 305F002 | 8 - 3/0 | 200 | 101.2 | 110 | 154 | 200 | 1.9763 | 1.8182 | 1.2987 | 200 | 2 | 110 |  | SF | 175 | 528 | 0.91098 | 880 | 352 | 515 | 5.8523 | 1750 | 19.8864 | XT4 | 250 | 200 | 200 | 2.2727 | 2000 | 22.7273 | TRUE | TRUE | TRUE | 2.8409
70.5 | Size-4 | 135 | 208 | 3 | 30 | 88 |  | 481 | 305F002 | 8 - 3/0 | 200 | 101.2 | 110 | 154 | 200 | 1.9763 | 1.8182 | 1.2987 | 200 | 2 | 110 |  | SF | 200 | 528 | 0.91098 | 880 | 352 | 590 | 6.7045 | 2000 | 22.7273 | XT4 | 250 | 200 | 200 | 2.2727 | 2000 | 22.7273 | TRUE | FALSE | TRUE | 0
71 | Size-4 | 135 | 208 | 3 | 40 | 114 |  | 641 | 305F002 | 8 - 3/0 | 200 | 131.1 | 142.5 | 199.5 | 200 | 1.5256 | 1.4035 | 1.0025 | 200 | 1/0 | 142.5 |  | SF | 150 | 684 | 0.93713 | 1140 | 342 | 450 | 3.9474 | 1991 | 17.4649 | XT4 | 250 | 150 | 150 | 1.3158 | 1500 | 13.1579 | TRUE | FALSE | TRUE | -4.307
71.1 | Size-4 | 135 | 208 | 3 | 40 | 114 |  | 641 | 305F002 | 8 - 3/0 | 200 | 131.1 | 142.5 | 199.5 | 200 | 1.5256 | 1.4035 | 1.0025 | 200 | 1/0 | 142.5 |  | SF | 175 | 684 | 0.93713 | 1140 | 342 | 515 | 4.5175 | 1750 | 15.3509 | XT4 | 250 | 200 | 200 | 1.7544 | 2000 | 17.5439 | TRUE | TRUE | TRUE | 2.193
71.2 | Size-4 | 135 | 208 | 3 | 40 | 114 |  | 641 | 305F002 | 8 - 3/0 | 200 | 131.1 | 142.5 | 199.5 | 200 | 1.5256 | 1.4035 | 1.0025 | 200 | 1/0 | 142.5 |  | SF | 200 | 684 | 0.93713 | 1140 | 342 | 590 | 5.1754 | 2000 | 17.5439 | XT4 | 250 | 200 | 200 | 1.7544 | 2000 | 17.5439 | TRUE | FALSE | TRUE | 0
72 | Size-4 | 135 | 220 - 240 (230) | 3 | 40 | 104 |  | 580 | 305F002 | 8 - 3/0 | 200 | 119.6 | 130 | 182 | 200 | 1.6722 | 1.5385 | 1.0989 | 200 | 1 | 130 |  | SF | 100 | 624 | 0.92949 | 1040 | 312 | 297 | 2.8558 | 1280 | 12.3077 | XT4 | 250 | 100 | 100 | 0.96154 | 1000 | 9.6154 | TRUE | FALSE | FALSE | -2.6923
72.1 | Size-4 | 135 | 220 - 240 (230) | 3 | 40 | 104 |  | 580 | 305F002 | 8 - 3/0 | 200 | 119.6 | 130 | 182 | 200 | 1.6722 | 1.5385 | 1.0989 | 200 | 1 | 130 |  | SF | 125 | 624 | 0.92949 | 1040 | 312 | 374 | 3.5962 | 1640 | 15.7692 | XT2 | 125 | 125 | 125 | 1.2019 | 1250 | 12.0192 | TRUE | FALSE | TRUE | -3.75
72.2 | Size-4 | 135 | 220 - 240 (230) | 3 | 40 | 104 |  | 580 | 305F002 | 8 - 3/0 | 200 | 119.6 | 130 | 182 | 200 | 1.6722 | 1.5385 | 1.0989 | 200 | 1 | 130 |  | SF | 150 | 624 | 0.92949 | 1040 | 312 | 450 | 4.3269 | 1991 | 19.1442 | XT4 | 250 | 150 | 150 | 1.4423 | 1500 | 14.4231 | TRUE | FALSE | TRUE | -4.7212
72.3 | Size-4 | 135 | 220 - 240 (230) | 3 | 40 | 104 |  | 580 | 305F002 | 8 - 3/0 | 200 | 119.6 | 130 | 182 | 200 | 1.6722 | 1.5385 | 1.0989 | 200 | 1 | 130 |  | SF | 175 | 624 | 0.92949 | 1040 | 312 | 515 | 4.9519 | 1750 | 16.8269 | XT4 | 250 | 200 | 200 | 1.9231 | 2000 | 19.2308 | TRUE | TRUE | TRUE | 2.4038
72.4 | Size-4 | 135 | 220 - 240 (230) | 3 | 40 | 104 |  | 580 | 305F002 | 8 - 3/0 | 200 | 119.6 | 130 | 182 | 200 | 1.6722 | 1.5385 | 1.0989 | 200 | 1 | 130 |  | SF | 200 | 624 | 0.92949 | 1040 | 312 | 590 | 5.6731 | 2000 | 19.2308 | XT4 | 250 | 200 | 200 | 1.9231 | 2000 | 19.2308 | TRUE | FALSE | TRUE | 0
73 | Size-4 | 135 | 220 - 240 (230) | 3 | 50 | 130 |  | 725 | 305F002 | 8 - 3/0 | 200 | 149.5 | 162.5 | 227.5 | 200 | 1.3378 | 1.2308 | 0.87912 | 200 | 2/0 | 162.5 |  | SF | 175 | 780 | 0.92949 | 1300 | 390 | 515 | 3.9615 | 1750 | 13.4615 | XT4 | 250 | 200 | 200 | 1.5385 | 2000 | 15.3846 | TRUE | TRUE | TRUE | 1.9231
73.1 | Size-4 | 135 | 220 - 240 (230) | 3 | 50 | 130 |  | 725 | 305F002 | 8 - 3/0 | 200 | 149.5 | 162.5 | 227.5 | 200 | 1.3378 | 1.2308 | 0.87912 | 200 | 2/0 | 162.5 |  | SF | 200 | 780 | 0.92949 | 1300 | 390 | 590 | 4.5385 | 2000 | 15.3846 | XT4 | 250 | 200 | 200 | 1.5385 | 2000 | 15.3846 | TRUE | FALSE | TRUE | 0
74 | Size-4 | 135 | 440 - 480 (460) | 3 | 60 | 77 |  | 435 | 305F002 | 8 - 3/0 | 200 | 88.55 | 96.25 | 134.75 | 200 | 2.2586 | 2.0779 | 1.4842 | 100 | 3 | 96.25 |  | SE | 100 | 462 | 0.94156 | 770 | 308 | 297 | 3.8571 | 1280 | 16.6234 | XT2 | 125 | 100 | 100 | 1.2987 | 1000 | 12.987 | TRUE | FALSE | TRUE | -3.6364
74.1 | Size-4 | 135 | 440 - 480 (460) | 3 | 60 | 77 |  | 435 | 305F002 | 8 - 3/0 | 200 | 88.55 | 96.25 | 134.75 | 200 | 2.2586 | 2.0779 | 1.4842 | 100 | 3 | 96.25 |  | SE | 110 | 462 | 0.94156 | 770 | 308 | 328 | 4.2597 | 1426 | 18.5195 | XT2 | 125 | 125 | 125 | 1.6234 | 1250 | 16.2338 | TRUE | FALSE | TRUE | -2.2857
74.2 | Size-4 | 135 | 440 - 480 (460) | 3 | 60 | 77 |  | 435 | 305F002 | 8 - 3/0 | 200 | 88.55 | 96.25 | 134.75 | 200 | 2.2586 | 2.0779 | 1.4842 | 100 | 3 | 96.25 |  | SE | 125 | 462 | 0.94156 | 770 | 308 | 374 | 4.8571 | 1640 | 21.2987 | XT2 | 125 | 125 | 125 | 1.6234 | 1250 | 16.2338 | TRUE | FALSE | TRUE | -5.0649
74.3 | Size-4 | 135 | 440 - 480 (460) | 3 | 60 | 77 |  | 435 | 305F002 | 8 - 3/0 | 200 | 88.55 | 96.25 | 134.75 | 200 | 2.2586 | 2.0779 | 1.4842 | 100 | 3 | 96.25 |  | SE | 150 | 462 | 0.94156 | 770 | 308 | 450 | 5.8442 | 1991 | 25.8571 | XT4 | 250 | 150 | 150 | 1.9481 | 1500 | 19.4805 | TRUE | FALSE | TRUE | -6.3766
74.4 | Size-4 | 135 | 440 - 480 (460) | 3 | 60 | 77 |  | 435 | 305F002 | 8 - 3/0 | 200 | 88.55 | 96.25 | 134.75 | 200 | 2.2586 | 2.0779 | 1.4842 | 100 | 3 | 96.25 |  | SE | 175 | 462 | 0.94156 | 770 | 308 | 515 | 6.6883 | 1750 | 22.7273 | XT4 | 250 | 200 | 200 | 2.5974 | 2000 | 25.974 | TRUE | TRUE | TRUE | 3.2468
74.5 | Size-4 | 135 | 440 - 480 (460) | 3 | 60 | 77 |  | 435 | 305F002 | 8 - 3/0 | 200 | 88.55 | 96.25 | 134.75 | 200 | 2.2586 | 2.0779 | 1.4842 | 100 | 3 | 96.25 |  | SE | 200 | 462 | 0.94156 | 770 | 308 | 590 | 7.6623 | 2000 | 25.974 | XT4 | 250 | 200 | 200 | 2.5974 | 2000 | 25.974 | TRUE | FALSE | TRUE | 0
75 | Size-4 | 135 | 440 - 480 (460) | 3 | 75 | 96 |  | 543 | 305F002 | 8 - 3/0 | 200 | 110.4 | 120 | 168 | 200 | 1.8116 | 1.6667 | 1.1905 | 200 | 1 | 120 |  | SE | 125 | 576 | 0.94271 | 960 | 384 | 374 | 3.8958 | 1640 | 17.0833 | XT2 | 125 | 125 | 125 | 1.3021 | 1250 | 13.0208 | TRUE | FALSE | TRUE | -4.0625
75.1 | Size-4 | 135 | 440 - 480 (460) | 3 | 75 | 96 |  | 543 | 305F002 | 8 - 3/0 | 200 | 110.4 | 120 | 168 | 200 | 1.8116 | 1.6667 | 1.1905 | 200 | 1 | 120 |  | SE | 150 | 576 | 0.94271 | 960 | 384 | 450 | 4.6875 | 1991 | 20.7396 | XT4 | 250 | 150 | 150 | 1.5625 | 1500 | 15.625 | TRUE | FALSE | TRUE | -5.1146
75.2 | Size-4 | 135 | 440 - 480 (460) | 3 | 75 | 96 |  | 543 | 305F002 | 8 - 3/0 | 200 | 110.4 | 120 | 168 | 200 | 1.8116 | 1.6667 | 1.1905 | 200 | 1 | 120 |  | SE | 175 | 576 | 0.94271 | 960 | 384 | 515 | 5.3646 | 1750 | 18.2292 | XT4 | 250 | 200 | 200 | 2.0833 | 2000 | 20.8333 | TRUE | TRUE | TRUE | 2.6042
75.3 | Size-4 | 135 | 440 - 480 (460) | 3 | 75 | 96 |  | 543 | 305F002 | 8 - 3/0 | 200 | 110.4 | 120 | 168 | 200 | 1.8116 | 1.6667 | 1.1905 | 200 | 1 | 120 |  | SE | 200 | 576 | 0.94271 | 960 | 384 | 590 | 6.1458 | 2000 | 20.8333 | XT4 | 250 | 200 | 200 | 2.0833 | 2000 | 20.8333 | TRUE | FALSE | TRUE | 0
76 | Size-4 | 135 | 440 - 480 (460) | 3 | 100 | 124 |  | 725 | 305F002 | 8 - 3/0 | 200 | 142.6 | 155 | 217 | 200 | 1.4025 | 1.2903 | 0.92166 | 200 | 2/0 | 155 |  | SF | 175 | 744 | 0.97446 | 1240 | 372 | 515 | 4.1532 | 1750 | 14.1129 | XT4 | 250 | 200 | 200 | 1.6129 | 2000 | 16.129 | TRUE | TRUE | TRUE | 2.0161
76.1 | Size-4 | 135 | 440 - 480 (460) | 3 | 100 | 124 |  | 725 | 305F002 | 8 - 3/0 | 200 | 142.6 | 155 | 217 | 200 | 1.4025 | 1.2903 | 0.92166 | 200 | 2/0 | 155 |  | SF | 200 | 744 | 0.97446 | 1240 | 372 | 590 | 4.7581 | 2000 | 16.129 | XT4 | 250 | 200 | 200 | 1.6129 | 2000 | 16.129 | TRUE | FALSE | TRUE | 0
77 | Size-4 | 135 | 550 - 600 (575) | 3 | 60 | 62 |  | 348 | 305F002 | 8 - 3/0 | 200 | 71.3 | 77.5 | 108.5 | 200 | 2.805 | 2.5806 | 1.8433 | 100 | 4 | 77.5 |  | SE | 100 | 372 | 0.93548 | 620 | 248 | 297 | 4.7903 | 1280 | 20.6452 | XT2 | 125 | 100 | 100 | 1.6129 | 1000 | 16.129 | TRUE | FALSE | TRUE | -4.5161
77.1 | Size-4 | 135 | 550 - 600 (575) | 3 | 60 | 62 |  | 348 | 305F002 | 8 - 3/0 | 200 | 71.3 | 77.5 | 108.5 | 200 | 2.805 | 2.5806 | 1.8433 | 100 | 4 | 77.5 |  | SE | 110 | 372 | 0.93548 | 620 | 248 | 328 | 5.2903 | 1426 | 23 | XT2 | 125 | 125 | 125 | 2.0161 | 1250 | 20.1613 | TRUE | FALSE | TRUE | -2.8387
77.2 | Size-4 | 135 | 550 - 600 (575) | 3 | 60 | 62 |  | 348 | 305F002 | 8 - 3/0 | 200 | 71.3 | 77.5 | 108.5 | 200 | 2.805 | 2.5806 | 1.8433 | 100 | 4 | 77.5 |  | SE | 125 | 372 | 0.93548 | 620 | 248 | 374 | 6.0323 | 1640 | 26.4516 | XT2 | 125 | 125 | 125 | 2.0161 | 1250 | 20.1613 | TRUE | FALSE | TRUE | -6.2903
77.3 | Size-4 | 135 | 550 - 600 (575) | 3 | 60 | 62 |  | 348 | 305F002 | 8 - 3/0 | 200 | 71.3 | 77.5 | 108.5 | 200 | 2.805 | 2.5806 | 1.8433 | 100 | 4 | 77.5 |  | SE | 150 | 372 | 0.93548 | 620 | 248 | 450 | 7.2581 | 1991 | 32.1129 | XT4 | 250 | 150 | 150 | 2.4194 | 1500 | 24.1935 | TRUE | FALSE | TRUE | -7.9194
77.4 | Size-4 | 135 | 550 - 600 (575) | 3 | 60 | 62 |  | 348 | 305F002 | 8 - 3/0 | 200 | 71.3 | 77.5 | 108.5 | 200 | 2.805 | 2.5806 | 1.8433 | 100 | 4 | 77.5 |  | SE | 175 | 372 | 0.93548 | 620 | 248 | 515 | 8.3065 | 1750 | 28.2258 | XT4 | 250 | 200 | 200 | 3.2258 | 2000 | 32.2581 | TRUE | TRUE | TRUE | 4.0323
77.5 | Size-4 | 135 | 550 - 600 (575) | 3 | 60 | 62 |  | 348 | 305F002 | 8 - 3/0 | 200 | 71.3 | 77.5 | 108.5 | 200 | 2.805 | 2.5806 | 1.8433 | 100 | 4 | 77.5 |  | SE | 200 | 372 | 0.93548 | 620 | 248 | 590 | 9.5161 | 2000 | 32.2581 | XT4 | 250 | 200 | 200 | 3.2258 | 2000 | 32.2581 | TRUE | FALSE | TRUE | 0
78 | Size-4 | 135 | 550 - 600 (575) | 3 | 75 | 77 |  | 434 | 305F002 | 8 - 3/0 | 200 | 88.55 | 96.25 | 134.75 | 200 | 2.2586 | 2.0779 | 1.4842 | 100 | 3 | 96.25 |  | SE | 100 | 462 | 0.93939 | 770 | 308 | 297 | 3.8571 | 1280 | 16.6234 | XT2 | 125 | 100 | 100 | 1.2987 | 1000 | 12.987 | TRUE | FALSE | TRUE | -3.6364
78.1 | Size-4 | 135 | 550 - 600 (575) | 3 | 75 | 77 |  | 434 | 305F002 | 8 - 3/0 | 200 | 88.55 | 96.25 | 134.75 | 200 | 2.2586 | 2.0779 | 1.4842 | 100 | 3 | 96.25 |  | SE | 110 | 462 | 0.93939 | 770 | 308 | 328 | 4.2597 | 1426 | 18.5195 | XT2 | 125 | 125 | 125 | 1.6234 | 1250 | 16.2338 | TRUE | FALSE | TRUE | -2.2857
78.2 | Size-4 | 135 | 550 - 600 (575) | 3 | 75 | 77 |  | 434 | 305F002 | 8 - 3/0 | 200 | 88.55 | 96.25 | 134.75 | 200 | 2.2586 | 2.0779 | 1.4842 | 100 | 3 | 96.25 |  | SE | 125 | 462 | 0.93939 | 770 | 308 | 374 | 4.8571 | 1640 | 21.2987 | XT2 | 125 | 125 | 125 | 1.6234 | 1250 | 16.2338 | TRUE | FALSE | TRUE | -5.0649
78.3 | Size-4 | 135 | 550 - 600 (575) | 3 | 75 | 77 |  | 434 | 305F002 | 8 - 3/0 | 200 | 88.55 | 96.25 | 134.75 | 200 | 2.2586 | 2.0779 | 1.4842 | 100 | 3 | 96.25 |  | SE | 150 | 462 | 0.93939 | 770 | 308 | 450 | 5.8442 | 1991 | 25.8571 | XT4 | 250 | 150 | 150 | 1.9481 | 1500 | 19.4805 | TRUE | FALSE | TRUE | -6.3766
78.4 | Size-4 | 135 | 550 - 600 (575) | 3 | 75 | 77 |  | 434 | 305F002 | 8 - 3/0 | 200 | 88.55 | 96.25 | 134.75 | 200 | 2.2586 | 2.0779 | 1.4842 | 100 | 3 | 96.25 |  | SE | 175 | 462 | 0.93939 | 770 | 308 | 515 | 6.6883 | 1750 | 22.7273 | XT4 | 250 | 200 | 200 | 2.5974 | 2000 | 25.974 | TRUE | TRUE | TRUE | 3.2468
78.5 | Size-4 | 135 | 550 - 600 (575) | 3 | 75 | 77 |  | 434 | 305F002 | 8 - 3/0 | 200 | 88.55 | 96.25 | 134.75 | 200 | 2.2586 | 2.0779 | 1.4842 | 100 | 3 | 96.25 |  | SE | 200 | 462 | 0.93939 | 770 | 308 | 590 | 7.6623 | 2000 | 25.974 | XT4 | 250 | 200 | 200 | 2.5974 | 2000 | 25.974 | TRUE | FALSE | TRUE | 0
79 | Size-4 | 135 | 550 - 600 (575) | 3 | 100 | 99 |  | 580 | 305F002 | 8 - 3/0 | 200 | 113.85 | 123.75 | 173.25 | 200 | 1.7567 | 1.6162 | 1.1544 | 200 | 1 | 123.75 |  | SE | 125 | 594 | 0.97643 | 990 | 396 | 374 | 3.7778 | 1640 | 16.5657 | XT2 | 125 | 125 | 125 | 1.2626 | 1250 | 12.6263 | TRUE | FALSE | TRUE | -3.9394
79.1 | Size-4 | 135 | 550 - 600 (575) | 3 | 100 | 99 |  | 580 | 305F002 | 8 - 3/0 | 200 | 113.85 | 123.75 | 173.25 | 200 | 1.7567 | 1.6162 | 1.1544 | 200 | 1 | 123.75 |  | SE | 150 | 594 | 0.97643 | 990 | 396 | 450 | 4.5455 | 1991 | 20.1111 | XT4 | 250 | 150 | 150 | 1.5152 | 1500 | 15.1515 | TRUE | FALSE | TRUE | -4.9596
79.2 | Size-4 | 135 | 550 - 600 (575) | 3 | 100 | 99 |  | 580 | 305F002 | 8 - 3/0 | 200 | 113.85 | 123.75 | 173.25 | 200 | 1.7567 | 1.6162 | 1.1544 | 200 | 1 | 123.75 |  | SE | 175 | 594 | 0.97643 | 990 | 396 | 515 | 5.202 | 1750 | 17.6768 | XT4 | 250 | 200 | 200 | 2.0202 | 2000 | 20.202 | TRUE | TRUE | TRUE | 2.5253
79.3 | Size-4 | 135 | 550 - 600 (575) | 3 | 100 | 99 |  | 580 | 305F002 | 8 - 3/0 | 200 | 113.85 | 123.75 | 173.25 | 200 | 1.7567 | 1.6162 | 1.1544 | 200 | 1 | 123.75 |  | SE | 200 | 594 | 0.97643 | 990 | 396 | 590 | 5.9596 | 2000 | 20.202 | XT4 | 250 | 200 | 200 | 2.0202 | 2000 | 20.202 | TRUE | FALSE | TRUE | 0
80 | Size-5 | 270 | 200 | 3 | 50 | 150 | 248 | 834 | 305G002 | 1/0 - 500MCM | 300 | 172.5 | 187.5 | 262.5 | 400 | 2.3188 | 2.1333 | 1.5238 | 200 | 3/0 | 187.5 |  | SF | 250 | 900 | 0.92667 | 1500 | 450 | 740 | 4.9333 | 2500 | 16.6667 | XT4 | 250 | 250 | 250 | 1.6667 | 2500 | 16.6667 | TRUE | FALSE | TRUE | 0
81 | Size-5 | 270 | 200 | 3 | 60 | 177 |  | 1001 | 305G002 | 1/0 - 500MCM | 300 | 203.55 | 221.25 | 309.75 | 400 | 1.9651 | 1.8079 | 1.2914 | 400 | 4/0 | 221.25 |  | SG | 300 | 1062 | 0.94256 | 1770 | 531 | 915 | 5.1695 | 3035 | 17.1469 | XT5 | 600 | 300 | 300 | 1.6949 | 3000 | 16.9492 | TRUE | FALSE | TRUE | -0.19774
82 | Size-5 | 270 | 200 | 3 | 75 | 221 |  | 1248 | 305G002 | 1/0 - 500MCM | 300 | 254.15 | 276.25 | 386.75 | 400 | 1.5739 | 1.448 | 1.0343 | 400 | 300 | 276.25 |  | SG | 400 | 1326 | 0.94118 | 2210 | 663 | 1220 | 5.5204 | 4050 | 18.3258 | XT5 | 600 | 400 | 400 | 1.81 | 4000 | 18.0995 | TRUE | FALSE | TRUE | -0.22624
83 | Size-5 | 270 | 208 | 3 | 50 | 143 |  | 802 | 305G002 | 1/0 - 500MCM | 300 | 164.45 | 178.75 | 250.25 | 400 | 2.4324 | 2.2378 | 1.5984 | 200 | 3/0 | 178.75 |  | SF | 250 | 858 | 0.93473 | 1430 | 429 | 740 | 5.1748 | 2500 | 17.4825 | XT4 | 250 | 250 | 250 | 1.7483 | 2500 | 17.4825 | TRUE | FALSE | TRUE | 0
84 | Size-5 | 270 | 208 | 3 | 60 | 169 |  | 962 | 305G002 | 1/0 - 500MCM | 300 | 194.35 | 211.25 | 295.75 | 400 | 2.0581 | 1.8935 | 1.3525 | 400 | 4/0 | 211.25 |  | SG | 300 | 1014 | 0.94872 | 1690 | 507 | 915 | 5.4142 | 3035 | 17.9586 | XT5 | 600 | 300 | 300 | 1.7751 | 3000 | 17.7515 | TRUE | FALSE | TRUE | -0.2071
85 | Size-5 | 270 | 208 | 3 | 75 | 211 |  | 1200 | 305G002 | 1/0 - 500MCM | 300 | 242.65 | 263.75 | 369.25 | 400 | 1.6485 | 1.5166 | 1.0833 | 400 | 300 | 263.75 |  | SG | 400 | 1266 | 0.94787 | 2110 | 633 | 1220 | 5.782 | 4050 | 19.1943 | XT5 | 600 | 400 | 400 | 1.8957 | 4000 | 18.9573 | TRUE | FALSE | TRUE | -0.23697
86 | Size-5 | 270 | 220 - 240 (230) | 3 | 60 | 154 |  | 870 | 305G002 | 1/0 - 500MCM | 300 | 177.1 | 192.5 | 269.5 | 400 | 2.2586 | 2.0779 | 1.4842 | 200 | 3/0 | 192.5 |  | SF | 250 | 924 | 0.94156 | 1540 | 462 | 740 | 4.8052 | 2500 | 16.2338 | XT4 | 250 | 250 | 250 | 1.6234 | 2500 | 16.2338 | TRUE | FALSE | TRUE | 0
87 | Size-5 | 270 | 220 - 240 (230) | 3 | 75 | 192 |  | 1085 | 305G002 | 1/0 - 500MCM | 300 | 220.8 | 240 | 336 | 400 | 1.8116 | 1.6667 | 1.1905 | 400 | 250 | 240 |  | SG | 300 | 1152 | 0.94184 | 1920 | 576 | 915 | 4.7656 | 3035 | 15.8073 | XT5 | 600 | 300 | 300 | 1.5625 | 3000 | 15.625 | TRUE | FALSE | TRUE | -0.18229
88 | Size-5 | 270 | 220 - 240 (230) | 3 | 100 | 248 |  | 1450 | 305G002 | 1/0 - 500MCM | 300 | 285.2 | 310 | 434 | 400 | 1.4025 | 1.2903 | 0.92166 | 400 | 350 | 310 |  | SG | 400 | 1488 | 0.97446 | 2480 | 744 | 1220 | 4.9194 | 4050 | 16.3306 | XT5 | 600 | 400 | 400 | 1.6129 | 4000 | 16.129 | TRUE | FALSE | TRUE | -0.20161
89 | Size-5 | 270 | 440 - 480 (460) | 3 | 125 | 156 |  | 908 | 305G002 | 1/0 - 500MCM | 300 | 179.4 | 195 | 273 | 400 | 2.2297 | 2.0513 | 1.4652 | 200 | 3/0 | 195 |  | SF | 250 | 936 | 0.97009 | 1560 | 468 | 740 | 4.7436 | 2500 | 16.0256 | XT4 | 250 | 250 | 250 | 1.6026 | 2500 | 16.0256 | TRUE | FALSE | TRUE | 0
90 | Size-5 | 270 | 440 - 480 (460) | 3 | 150 | 180 |  | 1085 | 305G002 | 1/0 - 500MCM | 300 | 207 | 225 | 315 | 400 | 1.9324 | 1.7778 | 1.2698 | 400 | 4/0 | 225 |  | SG | 300 | 1080 | 1.0046 | 1800 | 540 | 915 | 5.0833 | 3035 | 16.8611 | XT5 | 600 | 300 | 300 | 1.6667 | 3000 | 16.6667 | TRUE | FALSE | TRUE | -0.19444
91 | Size-5 | 270 | 440 - 480 (460) | 3 | 200 | 240 |  | 1450 | 305G002 | 1/0 - 500MCM | 300 | 276 | 300 | 420 | 400 | 1.4493 | 1.3333 | 0.95238 | 400 | 350 | 300 |  | SG | 400 | 1440 | 1.0069 | 2400 | 720 | 1220 | 5.0833 | 4050 | 16.875 | XT5 | 600 | 400 | 400 | 1.6667 | 4000 | 16.6667 | TRUE | FALSE | TRUE | -0.20833
92 | Size-5 | 270 | 550 - 600 (575) | 3 | 125 | 125 |  | 726 | 305G002 | 1/0 - 500MCM | 300 | 143.75 | 156.25 | 218.75 | 400 | 2.7826 | 2.56 | 1.8286 | 200 | 2/0 | 156.25 |  | SF | 250 | 750 | 0.968 | 1250 | 375 | 740 | 5.92 | 2500 | 20 | XT4 | 250 | 250 | 250 | 2 | 2500 | 20 | TRUE | FALSE | TRUE | 0
93 | Size-5 | 270 | 550 - 600 (575) | 3 | 150 | 144 |  | 868 | 305G002 | 1/0 - 500MCM | 300 | 165.6 | 180 | 252 | 400 | 2.4155 | 2.2222 | 1.5873 | 400 | 3/0 | 180 |  | SF | 250 | 864 | 1.0046 | 1440 | 432 | 740 | 5.1389 | 2500 | 17.3611 | XT4 | 250 | 250 | 250 | 1.7361 | 2500 | 17.3611 | TRUE | FALSE | TRUE | 0
94 | Size-5 | 270 | 550 - 600 (575) | 3 | 200 | 192 |  | 1160 | 305G002 | 1/0 - 500MCM | 300 | 220.8 | 240 | 336 | 400 | 1.8116 | 1.6667 | 1.1905 | 400 | 250 | 240 |  | SG | 300 | 1152 | 1.0069 | 1920 | 576 | 915 | 4.7656 | 3035 | 15.8073 | XT5 | 600 | 300 | 300 | 1.5625 | 3000 | 15.625 | TRUE | FALSE | TRUE | -0.18229
95 | Size-6 | 540 | 200 | 3 | 100 | 285 | 480 | 1668 | 305HH002 | 2 x (2/0 - 500MCM) | 375 | 327.75 | 356.25 | 498.75 | 800 | 2.4409 | 2.2456 | 1.604 | 800 | 500 | 356.25 |  | SG | 400 | 1710 | 0.97544 | 2850 | 855 | 1220 | 4.2807 | 4050 | 14.2105 | XT5 | 600 | 400 | 400 | 1.4035 | 4000 | 14.0351 | TRUE | FALSE | TRUE | -0.17544
96 | Size-6 | 540 | 200 | 3 | 125 | 359 |  | 2087 | 305HH002 | 2 x (2/0 - 500MCM) | 375 | 412.85 | 448.75 | 628.25 | 800 | 1.9377 | 1.7827 | 1.2734 | 1000 | 2 x 4/0 | 448.75 |  | SG | 600 | 2154 | 0.9689 | 3590 | 1077 | 1830 | 5.0975 | 6075 | 16.922 | XT5 | 600 | 600 | 600 | 1.6713 | 6000 | 16.7131 | TRUE | FALSE | TRUE | -0.20891
97 | Size-6 | 540 | 200 | 3 | 150 | 414 |  | 2496 | 305HH002 | 2 x (2/0 - 500MCM) | 375 | 476.1 | 517.5 | 724.5 | 800 | 1.6803 | 1.5459 | 1.1042 | 1200 | 2 x 300 | 517.5 |  | SG | 600 | 2484 | 1.0048 | 4140 | 1242 | 1830 | 4.4203 | 6075 | 14.6739 | XT5 | 600 | 600 | 600 | 1.4493 | 6000 | 14.4928 | TRUE | FALSE | TRUE | -0.18116
98 | Size-6 | 540 | 208 | 3 | 100 | 273 |  | 1603 | 305HH002 | 2 x (2/0 - 500MCM) | 375 | 313.95 | 341.25 | 477.75 | 800 | 2.5482 | 2.3443 | 1.6745 | 800 | 500 | 341.25 |  | SG | 400 | 1638 | 0.97863 | 2730 | 819 | 1220 | 4.4689 | 4050 | 14.8352 | XT5 | 600 | 400 | 400 | 1.4652 | 4000 | 14.652 | TRUE | FALSE | TRUE | -0.18315
99 | Size-6 | 540 | 208 | 3 | 125 | 343 |  | 2007 | 305HH002 | 2 x (2/0 - 500MCM) | 375 | 394.45 | 428.75 | 600.25 | 800 | 2.0281 | 1.8659 | 1.3328 | 1000 | 2 x 4/0 | 428.75 |  | SG | 600 | 2058 | 0.97522 | 3430 | 1029 | 1830 | 5.3353 | 6075 | 17.7114 | XT5 | 600 | 600 | 600 | 1.7493 | 6000 | 17.4927 | TRUE | FALSE | TRUE | -0.21866
100 | Size-6 | 540 | 208 | 3 | 150 | 396 |  | 2400 | 305HH002 | 2 x (2/0 - 500MCM) | 375 | 455.4 | 495 | 693 | 800 | 1.7567 | 1.6162 | 1.1544 | 1200 | 2 x 250 | 495 |  | SG | 600 | 2376 | 1.0101 | 3960 | 1188 | 1830 | 4.6212 | 6075 | 15.3409 | XT5 | 600 | 600 | 600 | 1.5152 | 6000 | 15.1515 | TRUE | FALSE | TRUE | -0.18939
101 | Size-6 | 540 | 220 - 240 (230) | 3 | 125 | 312 |  | 1815 | 305HH002 | 2 x (2/0 - 500MCM) | 375 | 358.8 | 390 | 546 | 800 | 2.2297 | 2.0513 | 1.4652 | 800 | 2 x 3/0 | 390 |  | SG | 600 | 1872 | 0.96955 | 3120 | 936 | 1830 | 5.8654 | 6075 | 19.4712 | XT5 | 600 | 600 | 600 | 1.9231 | 6000 | 19.2308 | TRUE | FALSE | TRUE | -0.24038
102 | Size-6 | 540 | 220 - 240 (230) | 3 | 150 | 360 |  | 2170 | 305HH002 | 2 x (2/0 - 500MCM) | 375 | 414 | 450 | 630 | 800 | 1.9324 | 1.7778 | 1.2698 | 1000 | 2 x 4/0 | 450 |  | SG | 600 | 2160 | 1.0046 | 3600 | 1080 | 1830 | 5.0833 | 6075 | 16.875 | XT5 | 600 | 600 | 600 | 1.6667 | 6000 | 16.6667 | TRUE | FALSE | TRUE | -0.20833
103 | Size-6 | 540 | 220 - 240 (230) | 3 | 200 | 480 |  | 2900 | 305HH002 | 2 x (2/0 - 500MCM) | 375 | 552 | 600 | 840 | 800 | 1.4493 | 1.3333 | 0.95238 | 1200 | 2 x 350 | 600 |  | SK | 800 | 2880 | 1.0069 | 4800 | 1440 | 2440 | 5.0833 | 8705 | 18.1354 | XT7 | 800 | 800 | 800 | 1.6667 | 8000 | 16.6667 | TRUE | FALSE | TRUE | -1.4688
104 | Size-6 | 540 | 440 - 480 (460) | 3 | 250 | 302 |  | 1825 | 305HH002 | 2 x (2/0 - 500MCM) | 375 | 347.3 | 377.5 | 528.5 | 800 | 2.3035 | 2.1192 | 1.5137 | 800 | 500 | 377.5 |  | SG | 600 | 1812 | 1.0072 | 3020 | 906 | 1830 | 6.0596 | 6075 | 20.1159 | XT5 | 600 | 600 | 600 | 1.9868 | 6000 | 19.8675 | TRUE | FALSE | TRUE | -0.24834
105 | Size-6 | 540 | 440 - 480 (460) | 3 | 300 | 361 |  | 2200 | 305HH002 | 2 x (2/0 - 500MCM) | 375 | 415.15 | 451.25 | 631.75 | 800 | 1.927 | 1.7729 | 1.2663 | 1000 | 2 x 4/0 | 451.25 |  | SG | 600 | 2166 | 1.0157 | 3610 | 1083 | 1830 | 5.0693 | 6075 | 16.8283 | XT5 | 600 | 600 | 600 | 1.662 | 6000 | 16.6205 | TRUE | FALSE | TRUE | -0.20776
106 | Size-6 | 540 | 440 - 480 (460) | 3 | 350 | 414 |  | 2550 | 305HH002 | 2 x (2/0 - 500MCM) | 375 | 476.1 | 517.5 | 724.5 | 800 | 1.6803 | 1.5459 | 1.1042 | 1200 | 2 x 300 | 517.5 |  | SG | 600 | 2484 | 1.0266 | 4140 | 1242 | 1830 | 4.4203 | 6075 | 14.6739 | XT5 | 600 | 600 | 600 | 1.4493 | 6000 | 14.4928 | TRUE | FALSE | TRUE | -0.18116
107 | Size-6 | 540 | 440 - 480 (460) | 3 | 400 | 477 |  | 2900 | 305HH002 | 2 x (2/0 - 500MCM) | 375 | 548.55 | 596.25 | 834.75 | 800 | 1.4584 | 1.3417 | 0.95837 | 1200 | 2 x 350 | 596.25 |  | SK | 800 | 2862 | 1.0133 | 4770 | 1431 | 2440 | 5.1153 | 8705 | 18.2495 | XT7 | 800 | 800 | 800 | 1.6771 | 8000 | 16.7715 | TRUE | FALSE | TRUE | -1.478
108 | Size-6 | 540 | 550 - 600 (575) | 3 | 250 | 242 |  | 1460 | 305HH002 | 2 x (2/0 - 500MCM) | 375 | 278.3 | 302.5 | 423.5 | 800 | 2.8746 | 2.6446 | 1.889 | 600 | 350 | 302.5 |  | SG | 400 | 1452 | 1.0055 | 2420 | 726 | 1220 | 5.0413 | 4050 | 16.7355 | XT5 | 600 | 400 | 400 | 1.6529 | 4000 | 16.5289 | TRUE | FALSE | TRUE | -0.20661
109 | Size-6 | 540 | 550 - 600 (575) | 3 | 300 | 289 |  | 1760 | 305HH002 | 2 x (2/0 - 500MCM) | 375 | 332.35 | 361.25 | 505.75 | 800 | 2.4071 | 2.2145 | 1.5818 | 800 | 500 | 361.25 |  | SG | 400 | 1734 | 1.015 | 2890 | 867 | 1220 | 4.2215 | 4050 | 14.0138 | XT5 | 600 | 400 | 400 | 1.3841 | 4000 | 13.8408 | TRUE | FALSE | TRUE | -0.17301
110 | Size-6 | 540 | 550 - 600 (575) | 3 | 350 | 336 |  | 2040 | 305HH002 | 2 x (2/0 - 500MCM) | 375 | 386.4 | 420 | 588 | 800 | 2.0704 | 1.9048 | 1.3605 | 800 | 2 x 4/0 | 420 |  | SG | 600 | 2016 | 1.0119 | 3360 | 1008 | 1830 | 5.4464 | 6075 | 18.0804 | XT5 | 600 | 600 | 600 | 1.7857 | 6000 | 17.8571 | TRUE | FALSE | TRUE | -0.22321
111 | Size-6 | 540 | 550 - 600 (575) | 3 | 400 | 382 |  | 2320 | 305HH002 | 2 x (2/0 - 500MCM) | 375 | 439.3 | 477.5 | 668.5 | 800 | 1.8211 | 1.6754 | 1.1967 | 1000 | 2 x 250 | 477.5 |  | SG | 600 | 2292 | 1.0122 | 3820 | 1146 | 1830 | 4.7906 | 6075 | 15.9031 | XT5 | 600 | 600 | 600 | 1.5707 | 6000 | 15.7068 | TRUE | FALSE | TRUE | -0.19634
112 | Size-00 | 9 | 115-120 | 1 | 0.33 | 7.2 | 8 | 50 | 305H002 | 14 - 8 | 20 | 8.28 | 9 | 12.6 | 30 | 3.6232 | 3.3333 | 2.381 | 30 | 14 | 9 |  | SE | 15 | 43.2 | 1.1574 | 72 | 28.8 | 43 | 5.9722 | 182 | 25.2778 | XT2 | 125 | 25 | 25 | 3.4722 | 250 | 34.7222 | TRUE | TRUE | TRUE | 9.4444
113 | Size-00 | 9 | 220 - 240 (230) | 1 | 0.33 | 3.6 |  | 21.6 | 305H002 | 14 - 8 | 20 | 4.14 | 4.5 | 6.3 | 30 | 7.2464 | 6.6667 | 4.7619 | 30 | 14 | 4.5 |  | SE | 15 | 21.6 | 1 | 36 | 14.4 | 43 | 11.9444 | 182 | 50.5556 | XT2 | 125 | 25 | 25 | 6.9444 | 250 | 69.4444 | TRUE | TRUE | TRUE | 18.8889
114 | Size-00 | 9 | 220 - 240 (230) | 1 | 0.5 | 4.9 |  | 29.4 | 305H002 | 14 - 8 | 20 | 5.635 | 6.125 | 8.575 | 30 | 5.3239 | 4.898 | 3.4985 | 30 | 14 | 6.125 |  | SE | 15 | 29.4 | 1 | 49 | 19.6 | 43 | 8.7755 | 182 | 37.1429 | XT2 | 125 | 25 | 25 | 5.102 | 250 | 51.0204 | TRUE | TRUE | TRUE | 13.8776
115 | Size-00 | 9 | 220 - 240 (230) | 1 | 0.75 | 6.9 |  | 41.4 | 305H002 | 14 - 8 | 20 | 7.935 | 8.625 | 12.075 | 30 | 3.7807 | 3.4783 | 2.4845 | 30 | 14 | 8.625 |  | SE | 15 | 41.4 | 1 | 69 | 27.6 | 43 | 6.2319 | 182 | 26.3768 | XT2 | 125 | 25 | 25 | 3.6232 | 250 | 36.2319 | TRUE | TRUE | TRUE | 9.8551
116 | Size-00 | 9 | 220 - 240 (230) | 1 | 1 | 8 |  | 45 | 305H002 | 14 - 8 | 20 | 9.2 | 10 | 14 | 30 | 3.2609 | 3 | 2.1429 | 30 | 14 | 10 |  | SE | 15 | 48 | 0.9375 | 80 | 32 | 43 | 5.375 | 182 | 22.75 | XT2 | 125 | 25 | 25 | 3.125 | 250 | 31.25 | TRUE | TRUE | TRUE | 8.5
117 | Size-0 | 18 | 115-120 | 1 | 0.5 | 9.8 | 16 | 58.8 | 305J002 | 14 - 8 | 20 | 11.27 | 12.25 | 17.15 | 30 | 2.6619 | 2.449 | 1.7493 | 30 | 14 | 12.25 |  | SE | 15 | 58.8 | 1 | 98 | 39.2 | 43 | 4.3878 | 182 | 18.5714 | XT2 | 125 | 25 | 25 | 2.551 | 250 | 25.5102 | TRUE | TRUE | TRUE | 6.9388
118 | Size-0 | 18 | 115-120 | 1 | 0.75 | 13.8 |  | 82.8 | 305J002 | 14 - 8 | 20 | 15.87 | 17.25 | 24.15 | 30 | 1.8904 | 1.7391 | 1.2422 | 30 | 12 | 17.25 |  | SE | 20 | 82.8 | 1 | 138 | 55.2 | 58 | 4.2029 | 254 | 18.4058 | XT2 | 125 | 25 | 25 | 1.8116 | 250 | 18.1159 | TRUE | FALSE | TRUE | -0.28986
119 | Size-0 | 18 | 115-120 | 1 | 1 | 16 |  | 80 | 305J002 | 14 - 8 | 20 | 18.4 | 20 | 28 | 30 | 1.6304 | 1.5 | 1.0714 | 30 | 12 | 20 |  | SE | 20 | 96 | 0.83333 | 160 | 64 | 58 | 3.625 | 254 | 15.875 | XT2 | 125 | 25 | 25 | 1.5625 | 250 | 15.625 | TRUE | FALSE | TRUE | -0.25
120 | Size-0 | 18 | 220 - 240 (230) | 1 | 1.5 | 10 |  | 60 | 305J002 | 14 - 8 | 20 | 11.5 | 12.5 | 17.5 | 30 | 2.6087 | 2.4 | 1.7143 | 30 | 14 | 12.5 |  | SE | 15 | 60 | 1 | 100 | 40 | 43 | 4.3 | 182 | 18.2 | XT2 | 125 | 25 | 25 | 2.5 | 250 | 25 | TRUE | TRUE | TRUE | 6.8
121 | Size-0 | 18 | 220 - 240 (230) | 1 | 2 | 12 |  | 65 | 305J002 | 14 - 8 | 20 | 13.8 | 15 | 21 | 30 | 2.1739 | 2 | 1.4286 | 30 | 14 | 15 |  | SE | 15 | 72 | 0.90278 | 120 | 48 | 43 | 3.5833 | 182 | 15.1667 | XT2 | 125 | 25 | 25 | 2.0833 | 250 | 20.8333 | TRUE | TRUE | TRUE | 5.6667
122 | Size-1 | 27 | 115-120 | 1 | 1.5 | 20 | 24 | 120 | 305K002 | 14 - 8 | 20 | 23 | 25 | 35 | 30 | 1.3043 | 1.2 | 0.85714 | 30 | 10 | 25 |  | SE |  | 120 | 1 | 200 | 80 | 118 | 5.9 | 501 | 25.05 | XT2 | 125 | [5 empty] | TRUE | FALSE | FALSE | -25.05
123 | Size-1 | 27 | 115-120 | 1 | 2 | 24 |  | 130 | 305K002 | 14 - 8 | 20 | 27.6 | 30 | 42 | 30 | 1.087 | 1 | 0.71429 | 30 | 10 | 30 |  | SE |  | 144 | 0.90278 | 240 | 96 | 118 | 4.9167 | 501 | 20.875 | XT2 | 125 | [5 empty] | TRUE | FALSE | FALSE | -20.875
124 | Size-1 | 27 | 220 - 240 (230) | 1 | 3 | 17 |  | 90 | 305K002 | 14 - 8 | 20 | 19.55 | 21.25 | 29.75 | 30 | 1.5345 | 1.4118 | 1.0084 | 30 | 10 | 21.25 |  | SE |  | 102 | 0.88235 | 170 | 68 | 118 | 6.9412 | 501 | 29.4706 | XT2 | 125 | [5 empty] | TRUE | FALSE | FALSE | -29.4706
125 | Size-1P | 36 | 115-120 | 1 | 3 | 34 | 34 | 140 | 306K102BKA | 14 - 8 | 20 | 39.1 | 42.5 | 59.5 | 60 | 1.5345 | 1.4118 | 1.0084 | 60 | 8 | 42.5 |  | SE |  | 204 | 0.68627 | 340 | 136 | 178 | 5.2353 | 777 | 22.8529 | XT2 | 125 | [5 empty] | TRUE | FALSE | FALSE | -22.8529
126 | Size-1P | 36 | 220 - 240 (230) | 1 | 5 | 28 |  | 135 | 306K102BKA | 14 - 8 | 20 | 32.2 | 35 | 49 | 60 | 1.8634 | 1.7143 | 1.2245 | 60 | 8 | 35 |  | SE |  | 168 | 0.80357 | 280 | 112 |  | 0 |  | 0 | XT2 | 125 | [5 empty] | FALSE | FALSE | FALSE | 0
127 | Size-2 | 45 | 115-120 | 1 | 3 | 34 | 40 | 250 | 305L002 | 14 - 4 | 50 | 39.1 | 42.5 | 59.5 | 60 | 1.5345 | 1.4118 | 1.0084 | 60 | 8 | 42.5 |  | SE |  | 204 | 1.2255 | 340 | 136 | 178 | 5.2353 | 777 | 22.8529 | XT2 | 125 | [5 empty] | TRUE | FALSE | FALSE | -22.8529
128 | Size-2 | 45 | 220 - 240 (230) | 1 | 7.5 | 40 |  | 250 | 305L002 | 14 - 4 | 50 | 46 | 50 | 70 | 60 | 1.3043 | 1.2 | 0.85714 | 60 | 8 | 50 |  | SE |  | 240 | 1.0417 | 400 | 160 |  | 0 |  | 0 | XT2 | 125 | [5 empty] | FALSE | FALSE | FALSE | 0
129 | Size-3 | 90 | 115-120 | 1 | 5 | 56 | 80 | 336 | 305M002 | 8 - 1/0 | 150 | 64.4 | 70 | 98 | 100 | 1.5528 | 1.4286 | 1.0204 | 100 | 4 | 70 |  | SE |  | 336 | 1 | 560 | 224 |  | 0 |  | 0 | XT2 | 125 | [5 empty] | FALSE | FALSE | FALSE | 0
130 | Size-3 | 90 | 115-120 | 1 | 7.5 | 80 |  | 500 | 305M002 | 8 - 1/0 | 150 | 92 | 100 | 140 | 100 | 1.087 | 1 | 0.71429 | 100 | 3 | 100 |  | SE |  | 480 | 1.0417 | 800 | 320 | 374 | 4.675 | 1640 | 20.5 | XT2 | 125 | [5 empty] | TRUE | FALSE | FALSE | -20.5
131 | Size-3 | 90 | 220 - 240 (230) | 1 | 10 | 50 |  | 300 | 305M002 | 8 - 1/0 | 150 | 57.5 | 62.5 | 87.5 | 100 | 1.7391 | 1.6 | 1.1429 | 100 | 6 | 62.5 |  | SE |  | 300 | 1 | 500 | 200 |  | 0 |  | 0 | XT2 | 125 | [5 empty] | FALSE | FALSE | FALSE | 0
132 | Size-3 | 90 | 220 - 240 (230) | 1 | 15 | 68 |  | 500 | 305M002 | 8 - 1/0 | 150 | 78.2 | 85 | 119 | 100 | 1.2788 | 1.1765 | 0.84034 | 100 | 4 | 85 |  | SE |  | 408 | 1.2255 | 680 | 272 | 374 | 5.5 | 1640 | 24.1176 | XT2 | 125 | [5 empty] | TRUE | FALSE | FALSE | -24.1176

## Type A Combinations (hidden)
Template for Submission of Combination Motor Controller
(NOTE: The bracketed alphanumeric in each column heading and in example entries, such as [B1], corresponds to a section of the short circuit database submittal guideline document which provides further information concerning the expected content and format for entering data into the spreadsheet cells)
[B1] Database Identification Number | [B2] Listed Combination Motor Controller Information | [7 empty] | [B3] Construction Type | [B4] Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | [B8] Enclosure Volume, cubic inches | [B9] Conditions of Use | [B10] Schematic
| Listing Report Information |  |  |  |  | Enclosure or Unit Dimensions
| UL File Number | Report Issue Date YYYY-MM-DD | Volume / Section (Vol#).(Sec#) | Model Number or Product Style/ Designation | Product Description on Page/Figure/Ill. | Enclosure or Unit Height, inches | Width, inches | Depth, inches |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of phases | SCCR, kA | Full Load Current, A | Hp Rating | [B7] Voltage, V | [B7] Number of Phases | [B5] SCCR, kA | [B6] Current Rating, FLA or FLA/LRA | [B6] Hp Rating |  |  |  | [B11] Other References
Example Layout 1 | E1234 | 2000-10-15 | 1.1 |  | P. 6/ Fig. 5A/Ill.15 | 10 | 10 | 6 | A [ version C1(a)] | FDS | Company 1 | DS | 240 |  | 10 | 100 |  | 240 | 3 | 10 | 28 |  | 600 | 1
[10 empty] | F | Any Listed Mfg | Any Class J Fuse | 250 |  | 200 | 80
[10 empty] | MC | Company 2 | MC1 | 240 |  | 5 | 28 | 10
[10 empty] | OLR | Company 2 | OL1 | 240 |  | 5 | 30
Example Layout 2 | [8 empty] | A [ version C1(b)] | DS
FH
F
MC
OLR
Example Layout 3 | [8 empty] | A [ version C1(c)] | FDS
F
STR
Example Layout 4 | [8 empty] | A [ version C1(d)] | DS
FH
F
STR
0
0
0
0
0
0
0
0
0

## Type D Combinations
Issued: 2020-08-01
|  |  | X | X | X | X | X | X | [16 empty] | X | X
(NOTE: The bracketed alphanumeric in each column heading and in example entries, such as [B1], corresponds to a section of the short circuit database submittal guideline document which provides further information concerning the expected content and format for entering data into the spreadsheet cells)
[B1] Database Identification Number | [B2] Listed Combination Motor Controller Information | [7 empty] | [B3] Construction Type | [B4] Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | [B8] Enclosure Volume, cubic inches | [B9] Conditions of Use | [B10] Schematic
| Listing Report Information |  |  |  |  | Enclosure or Unit Dimensions
| UL File Number | Report Issue Date YYYY-MM-DD | Volume / Section (Vol#).(Sec#) | Model Number or Product Style/ Designation | Product Description on Page/Figure/Ill. | Enclosure or Unit Height, inches | Width, inches | Depth, inches |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | [B7] Voltage, V | [B7] Number of Phases | [B5] SCCR, kA | [B6] Current Rating, FLA or FLA/LRA | [B6] Hp Rating |  |  |  | [B11] Other References
ABBDA2002N7E0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 7 |  | 200 | 3 | 65 | 2.5 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXE | 240 | 3 | 5 | 1.6-3.4
ABBDA2002N7FF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 7 |  | 200 | 3 | 65 | 3.7 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBDA2002N7F001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 7 |  | 200 | 3 | 65 | 4.8 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBDA2002N15G1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 200 | 3 | 65 | 6.9 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBDA2082N3E0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 3 |  | 208 | 3 | 65 | 2.4 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXE | 240 | 3 | 5 | 1.6-3.4
ABBDA2082N7FF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 7 |  | 208 | 3 | 65 | 3.5 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBDA2082N7F001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 7 |  | 208 | 3 | 65 | 4.6 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBDA2082N15F1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 6.6 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBDA2082N15G1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 6.6 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBDA2402N3E0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 3 |  | 220 - 240 (230) | 3 | 65 | 2.2 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXE | 240 | 3 | 5 | 1.6-3.4
ABBDA2402N7EF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 7 |  | 220 - 240 (230) | 3 | 65 | 3.2 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXE | 240 | 3 | 5 | 1.6-3.4
ABBDA2402N7FF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 7 |  | 220 - 240 (230) | 3 | 65 | 3.2 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBDA2402N7F001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 7 |  | 220 - 240 (230) | 3 | 65 | 4.2 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBDA2402N15F1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 220 - 240 (230) | 3 | 65 | 6 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBDA4802N3D0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 3 |  | 440 - 480 (460) | 3 | 25 | 1.1 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 480 | 3 | 5 | 0.8-1.7
ABBDA4802N3DF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 3 |  | 440 - 480 (460) | 3 | 25 | 1.6 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 480 | 3 | 5 | 0.8-1.7
ABBDA4802N3EF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 3 |  | 440 - 480 (460) | 3 | 25 | 1.6 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBDA4802N3E001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 3 |  | 440 - 480 (460) | 3 | 25 | 2.1 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBDA4802N7E1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 7 |  | 440 - 480 (460) | 3 | 25 | 3 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBDA4802N7E002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 7 |  | 440 - 480 (460) | 3 | 25 | 3.4 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBDA4802N7F002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 7 |  | 440 - 480 (460) | 3 | 25 | 3.4 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXF | 480 | 3 | 5 | 3.2-6.8
ABBDA6002N3D0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 3 |  | 550 - 600 (575) | 3 | 14 | 0.9 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 600 | 3 | 5 | 0.8-1.7
ABBDA6002N3DF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 3 |  | 550 - 600 (575) | 3 | 14 | 1.3 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 600 | 3 | 5 | 0.8-1.7
ABBDA6002N3D001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 3 |  | 550 - 600 (575) | 3 | 14 | 1.7 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 600 | 3 | 5 | 0.8-1.7
ABBDA6002N3E001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 3 |  | 550 - 600 (575) | 3 | 14 | 1.7 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 600 | 3 | 5 | 1.6-3.4
ABBDA6002N3E1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 3 |  | 550 - 600 (575) | 3 | 14 | 2.4 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 600 | 3 | 5 | 1.6-3.4
ABBDA6002N7E002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 7 |  | 550 - 600 (575) | 3 | 14 | 2.7 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 600 | 3 | 5 | 1.6-3.4
ABBDA2002S7E0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 7 |  | 200 | 3 | 100 | 2.5 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXE | 240 | 3 | 5 | 1.6-3.4
ABBDA2002S7FF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 7 |  | 200 | 3 | 100 | 3.7 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBDA2002S7F001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 7 |  | 200 | 3 | 100 | 4.8 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBDA2002S15G1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 200 | 3 | 100 | 6.9 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBDA2082S3E0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 3 |  | 208 | 3 | 100 | 2.4 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXE | 240 | 3 | 5 | 1.6-3.4
ABBDA2082S7FF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 7 |  | 208 | 3 | 100 | 3.5 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBDA2082S7F001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 7 |  | 208 | 3 | 100 | 4.6 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBDA2082S15F1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 6.6 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBDA2082S15G1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 6.6 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBDA2402S3E0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 3 |  | 220 - 240 (230) | 3 | 100 | 2.2 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXE | 240 | 3 | 5 | 1.6-3.4
ABBDA2402S7EF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 7 |  | 220 - 240 (230) | 3 | 100 | 3.2 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXE | 240 | 3 | 5 | 1.6-3.4
ABBDA2402S7FF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 7 |  | 220 - 240 (230) | 3 | 100 | 3.2 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBDA2402S7F001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 7 |  | 220 - 240 (230) | 3 | 100 | 4.2 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBDA2402S15F1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 220 - 240 (230) | 3 | 100 | 6 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBDA4802S3D0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 3 |  | 440 - 480 (460) | 3 | 35 | 1.1 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 480 | 3 | 5 | 0.8-1.7
ABBDA4802S3DF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 3 |  | 440 - 480 (460) | 3 | 35 | 1.6 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 480 | 3 | 5 | 0.8-1.7
ABBDA4802S3EF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 3 |  | 440 - 480 (460) | 3 | 35 | 1.6 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBDA4802S3E001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 3 |  | 440 - 480 (460) | 3 | 35 | 2.1 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBDA4802S7E1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 7 |  | 440 - 480 (460) | 3 | 35 | 3 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBDA4802S7E002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 7 |  | 440 - 480 (460) | 3 | 35 | 3.4 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBDA4802S7F002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 7 |  | 440 - 480 (460) | 3 | 35 | 3.4 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXF | 480 | 3 | 5 | 3.2-6.8
ABBDA6002S3D0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 3 |  | 550 - 600 (575) | 3 | 18 | 0.9 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 600 | 3 | 5 | 0.8-1.7
ABBDA6002S3DF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 3 |  | 550 - 600 (575) | 3 | 18 | 1.3 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 600 | 3 | 5 | 0.8-1.7
ABBDA6002S3D001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 3 |  | 550 - 600 (575) | 3 | 18 | 1.7 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 600 | 3 | 5 | 0.8-1.7
ABBDA6002S3E001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 3 |  | 550 - 600 (575) | 3 | 18 | 1.7 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 600 | 3 | 5 | 1.6-3.4
ABBDA6002S3E1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 3 |  | 550 - 600 (575) | 3 | 18 | 2.4 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 600 | 3 | 5 | 1.6-3.4
ABBDA6002S7E002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 7 |  | 550 - 600 (575) | 3 | 18 | 2.7 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 600 | 3 | 5 | 1.6-3.4
ABBDA4802H3D0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 3 |  | 440 - 480 (460) | 3 | 65 | 1.1 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 480 | 3 | 5 | 0.8-1.7
ABBDA4802H3DF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 3 |  | 440 - 480 (460) | 3 | 65 | 1.6 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 480 | 3 | 5 | 0.8-1.7
ABBDA4802H3EF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 3 |  | 440 - 480 (460) | 3 | 65 | 1.6 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBDA4802H3E001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 3 |  | 440 - 480 (460) | 3 | 65 | 2.1 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBDA4802H7E1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 7 |  | 440 - 480 (460) | 3 | 65 | 3 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBDA4802H7E002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 7 |  | 440 - 480 (460) | 3 | 65 | 3.4 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBDA4802H7F002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 7 |  | 440 - 480 (460) | 3 | 65 | 3.4 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXF | 480 | 3 | 5 | 3.2-6.8
ABBDA6002H3D0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 3 |  | 550 - 600 (575) | 3 | 25 | 0.9 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 600 | 3 | 5 | 0.8-1.7
ABBDA6002H3DF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 3 |  | 550 - 600 (575) | 3 | 25 | 1.3 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 600 | 3 | 5 | 0.8-1.7
ABBDA6002H3D001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 3 |  | 550 - 600 (575) | 3 | 25 | 1.7 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 600 | 3 | 5 | 0.8-1.7
ABBDA6002H3E001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 3 |  | 550 - 600 (575) | 3 | 25 | 1.7 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 600 | 3 | 5 | 1.6-3.4
ABBDA6002H3E1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 3 |  | 550 - 600 (575) | 3 | 25 | 2.4 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 600 | 3 | 5 | 1.6-3.4
ABBDA6002H7E002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 7 |  | 550 - 600 (575) | 3 | 25 | 2.7 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 600 | 3 | 5 | 1.6-3.4
ABBDA4802L3D0F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 3 |  | 440 - 480 (460) | 3 | 100 | 1.1 | 0.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 480 | 3 | 5 | 0.8-1.7
ABBDA4802L3DF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 3 |  | 440 - 480 (460) | 3 | 100 | 1.6 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXD | 480 | 3 | 5 | 0.8-1.7
ABBDA4802L3EF75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 3 |  | 440 - 480 (460) | 3 | 100 | 1.6 | 0.75 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBDA4802L3E001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 3 |  | 440 - 480 (460) | 3 | 100 | 2.1 | 1 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBDA4802L7E1F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 7 |  | 440 - 480 (460) | 3 | 100 | 3 | 1.5 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBDA4802L7E002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 7 |  | 440 - 480 (460) | 3 | 100 | 3.4 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXE | 480 | 3 | 5 | 1.6-3.4
ABBDA4802L7F002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 7 |  | 440 - 480 (460) | 3 | 100 | 3.4 | 2 | 1399.2 | 1,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324CXF | 480 | 3 | 5 | 3.2-6.8
ABBDA2002N710F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 7 |  | 200 | 3 | 65 | 2.5 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2002N71F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 7 |  | 200 | 3 | 65 | 3.7 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2002N71001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 7 |  | 200 | 3 | 65 | 4.8 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2002N1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 200 | 3 | 65 | 6.9 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2082N310F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 3 |  | 208 | 3 | 65 | 2.4 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2082N71F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 7 |  | 208 | 3 | 65 | 3.5 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2082N71001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 7 |  | 208 | 3 | 65 | 4.6 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2082N1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 6.6 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2402N310F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 3 |  | 220 - 240 (230) | 3 | 65 | 2.2 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2402N71F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 7 |  | 220 - 240 (230) | 3 | 65 | 3.2 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2402N71001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 7 |  | 220 - 240 (230) | 3 | 65 | 4.2 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2402N1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 220 - 240 (230) | 3 | 65 | 6 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA4802N310F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 3 |  | 440 - 480 (460) | 3 | 25 | 1.1 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA4802N31F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 3 |  | 440 - 480 (460) | 3 | 25 | 1.6 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA4802N31001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 3 |  | 440 - 480 (460) | 3 | 25 | 2.1 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA4802N711F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 7 |  | 440 - 480 (460) | 3 | 25 | 3 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA4802N71002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 7 |  | 440 - 480 (460) | 3 | 25 | 3.4 | 2 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA6002N310F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 3 |  | 550 - 600 (575) | 3 | 14 | 0.9 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDA6002N31F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 3 |  | 550 - 600 (575) | 3 | 14 | 1.3 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDA6002N31001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 3 |  | 550 - 600 (575) | 3 | 14 | 1.7 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDA6002N311F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 3 |  | 550 - 600 (575) | 3 | 14 | 2.4 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDA6002N71002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 7 |  | 550 - 600 (575) | 3 | 14 | 2.7 | 2 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDA2002S710F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 7 |  | 200 | 3 | 100 | 2.5 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2002S71F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 7 |  | 200 | 3 | 100 | 3.7 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2002S71001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 7 |  | 200 | 3 | 100 | 4.8 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2002S1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 200 | 3 | 100 | 6.9 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2082S310F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 3 |  | 208 | 3 | 100 | 2.4 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2082S71F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 7 |  | 208 | 3 | 100 | 3.5 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2082S71001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 7 |  | 208 | 3 | 100 | 4.6 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2082S1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 6.6 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2402S310F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 3 |  | 220 - 240 (230) | 3 | 100 | 2.2 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2402S71F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 7 |  | 220 - 240 (230) | 3 | 100 | 3.2 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2402S71001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 7 |  | 220 - 240 (230) | 3 | 100 | 4.2 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA2402S1511F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 220 - 240 (230) | 3 | 100 | 6 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 240 | 3 | 5 | 9 | 1.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDA4802S310F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 3 |  | 440 - 480 (460) | 3 | 35 | 1.1 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA4802S31F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 3 |  | 440 - 480 (460) | 3 | 35 | 1.6 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA4802S31001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 3 |  | 440 - 480 (460) | 3 | 35 | 2.1 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA4802S711F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 7 |  | 440 - 480 (460) | 3 | 35 | 3 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA4802S71002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 7 |  | 440 - 480 (460) | 3 | 35 | 3.4 | 2 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA6002S310F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 3 |  | 550 - 600 (575) | 3 | 18 | 0.9 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDA6002S31F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 3 |  | 550 - 600 (575) | 3 | 18 | 1.3 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDA6002S31001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 3 |  | 550 - 600 (575) | 3 | 18 | 1.7 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDA6002S311F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 3 |  | 550 - 600 (575) | 3 | 18 | 2.4 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDA6002S71002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 7 |  | 550 - 600 (575) | 3 | 18 | 2.7 | 2 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDA4802H310F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 3 |  | 440 - 480 (460) | 3 | 65 | 1.1 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA4802H31F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 3 |  | 440 - 480 (460) | 3 | 65 | 1.6 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA4802H31001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 3 |  | 440 - 480 (460) | 3 | 65 | 2.1 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA4802H711F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 7 |  | 440 - 480 (460) | 3 | 65 | 3 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA4802H71002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 7 |  | 440 - 480 (460) | 3 | 65 | 3.4 | 2 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA6002H310F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 3 |  | 550 - 600 (575) | 3 | 25 | 0.9 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDA6002H31F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 3 |  | 550 - 600 (575) | 3 | 25 | 1.3 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDA6002H31001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 3 |  | 550 - 600 (575) | 3 | 25 | 1.7 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDA6002H311F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 3 |  | 550 - 600 (575) | 3 | 25 | 2.4 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDA6002H71002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 7 |  | 550 - 600 (575) | 3 | 25 | 2.7 | 2 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 600 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDA4802L310F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 3 |  | 440 - 480 (460) | 3 | 100 | 1.1 | 0.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA4802L31F75 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 3 |  | 440 - 480 (460) | 3 | 100 | 1.6 | 0.75 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA4802L31001 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 3 |  | 440 - 480 (460) | 3 | 100 | 2.1 | 1 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA4802L711F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 7 |  | 440 - 480 (460) | 3 | 100 | 3 | 1.5 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDA4802L71002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 7 |  | 440 - 480 (460) | 3 | 100 | 3.4 | 2 | 1399.2 | 1,3,5 |  | Size-00
[10 empty] | MC | ABB | CR305A0 | 480 | 3 | 5 | 9 | 2
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDB2002N15G002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 200 | 3 | 65 | 7.8 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBDB2002N15G003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 200 | 3 | 65 | 11 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBDB2082N15G002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 7.5 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBDB2082N15G003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 10.6 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBDB2402N15F002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 220 - 240 (230) | 3 | 65 | 6.8 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBDB2402N15G002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 220 - 240 (230) | 3 | 65 | 6.8 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBDB2402N15G003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 220 - 240 (230) | 3 | 65 | 9.6 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBDB4802N15G005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 7.6 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBDB6002N7F003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 7 |  | 550 - 600 (575) | 3 | 14 | 3.9 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 600 | 3 | 5 | 3.2-6.8
ABBDB6002N15F005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 15 |  | 550 - 600 (575) | 3 | 14 | 6.1 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 600 | 3 | 5 | 3.2-6.8
ABBDB2002S15G002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 200 | 3 | 100 | 7.8 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBDB2002S15G003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 200 | 3 | 100 | 11 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBDB2082S15G002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 7.5 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBDB2082S15G003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 10.6 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBDB2402S15F002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 220 - 240 (230) | 3 | 100 | 6.8 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXF | 240 | 3 | 5 | 3.2-6.8
ABBDB2402S15G002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 220 - 240 (230) | 3 | 100 | 6.8 | 2 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBDB2402S15G003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 220 - 240 (230) | 3 | 100 | 9.6 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324CXG | 240 | 3 | 5 | 6.5-13.5
ABBDB4802S15G005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 7.6 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBDB6002S7F003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 7 |  | 550 - 600 (575) | 3 | 18 | 3.9 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 600 | 3 | 5 | 3.2-6.8
ABBDB6002S15F005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 6.1 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 600 | 3 | 5 | 3.2-6.8
ABBDB4802H15G005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 7.6 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBDB6002H7F003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 7 |  | 550 - 600 (575) | 3 | 25 | 3.9 | 3 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 600 | 3 | 5 | 3.2-6.8
ABBDB6002H15F005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 6.1 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXF | 600 | 3 | 5 | 3.2-6.8
ABBDB4802L15G005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 7.6 | 5 | 1399.2 | 1,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBDB2002N151002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 200 | 3 | 65 | 7.8 | 2 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDB2002N151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 200 | 3 | 65 | 11 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDB2082N151002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 7.5 | 2 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDB2082N151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 208 | 3 | 65 | 10.6 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDB2402N151002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 220 - 240 (230) | 3 | 65 | 6.8 | 2 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDB2402N151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 15 |  | 220 - 240 (230) | 3 | 65 | 9.6 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDB4802N151005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 7.6 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDB6002N71003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 7 |  | 550 - 600 (575) | 3 | 14 | 3.9 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDB6002N151005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 15 |  | 550 - 600 (575) | 3 | 14 | 6.1 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDB2002S151002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 200 | 3 | 100 | 7.8 | 2 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDB2002S151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 200 | 3 | 100 | 11 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDB2082S151002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 7.5 | 2 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDB2082S151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 208 | 3 | 100 | 10.6 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDB2402S151002 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 220 - 240 (230) | 3 | 100 | 6.8 | 2 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDB2402S151003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 15 |  | 220 - 240 (230) | 3 | 100 | 9.6 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 240 | 3 | 5 | 18 | 3
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDB4802S151005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 7.6 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDB6002S71003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 7 |  | 550 - 600 (575) | 3 | 18 | 3.9 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDB6002S151005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 6.1 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDB4802H151005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 7.6 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDB6002H71003 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 7 |  | 550 - 600 (575) | 3 | 25 | 3.9 | 3 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDB6002H151005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 6.1 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 600 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDB4802L151005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 7.6 | 5 | 1399.2 | 1,3,5 |  | Size-0
[10 empty] | MC | ABB | CR305B0 | 480 | 3 | 5 | 18 | 5
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDC2002N25H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 25 |  | 200 | 3 | 65 | 17.5 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBDC2002N30H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 30 |  | 200 | 3 | 65 | 17.5 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBDC2002N60H7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 200 | 3 | 65 | 25.3 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBDC2082N25H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 25 |  | 208 | 3 | 65 | 16.7 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBDC2082N30H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 30 |  | 208 | 3 | 65 | 16.7 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBDC2082N60H7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 208 | 3 | 65 | 24.2 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBDC2402N25H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 25 |  | 220 - 240 (230) | 3 | 65 | 15.2 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBDC2402N30H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 30 |  | 220 - 240 (230) | 3 | 65 | 15.2 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBDC2402N30H7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 30 |  | 220 - 240 (230) | 3 | 65 | 22 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBDC4802N15G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBDC4802N25G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 25 |  | 440 - 480 (460) | 3 | 25 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBDC4802N25H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 25 |  | 440 - 480 (460) | 3 | 25 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBDC4802N30H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 30 |  | 440 - 480 (460) | 3 | 25 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBDC6002N15G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 15 |  | 550 - 600 (575) | 3 | 14 | 9 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBDC6002N15G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 15 |  | 550 - 600 (575) | 3 | 14 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBDC6002N25G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 25 |  | 550 - 600 (575) | 3 | 14 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBDC2002S25H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 25 |  | 200 | 3 | 100 | 17.5 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBDC2002S30H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 30 |  | 200 | 3 | 100 | 17.5 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBDC2002S60H7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 200 | 3 | 100 | 25.3 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBDC2082S25H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 25 |  | 208 | 3 | 100 | 16.7 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBDC2082S30H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 30 |  | 208 | 3 | 100 | 16.7 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBDC2082S60H7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 208 | 3 | 100 | 24.2 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBDC2402S25H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 25 |  | 220 - 240 (230) | 3 | 100 | 15.2 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBDC2402S30H005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 30 |  | 220 - 240 (230) | 3 | 100 | 15.2 | 5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBDC2402S30H7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 30 |  | 220 - 240 (230) | 3 | 100 | 22 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324CXH | 240 | 3 | 5 | 13-27
ABBDC4802S15G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBDC4802S25G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 25 |  | 440 - 480 (460) | 3 | 35 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBDC4802S25H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 25 |  | 440 - 480 (460) | 3 | 35 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBDC4802S30H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 30 |  | 440 - 480 (460) | 3 | 35 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBDC6002S15G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 9 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBDC6002S15G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBDC6002S25G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 25 |  | 550 - 600 (575) | 3 | 18 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBDC4802H15G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBDC4802H25G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 25 |  | 440 - 480 (460) | 3 | 65 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBDC4802H25H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 25 |  | 440 - 480 (460) | 3 | 65 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBDC4802H30H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 30 |  | 440 - 480 (460) | 3 | 65 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBDC6002H15G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 9 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBDC6002H15G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBDC6002H25G010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 25 |  | 550 - 600 (575) | 3 | 25 | 11 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 600 | 3 | 5 | 6.5-13.5
ABBDC4802L15G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBDC4802L25G7F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 25 |  | 440 - 480 (460) | 3 | 100 | 11 | 7.5 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXG | 480 | 3 | 5 | 6.5-13.5
ABBDC4802L25H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 25 |  | 440 - 480 (460) | 3 | 100 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBDC4802L30H010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 30 |  | 440 - 480 (460) | 3 | 100 | 14 | 10 | 1399.2 | 1,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324CXH | 480 | 3 | 5 | 13-27
ABBDC2002N251005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 25 |  | 200 | 3 | 65 | 17.5 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDC2002N301005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 30 |  | 200 | 3 | 65 | 17.5 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDC2002N6017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 200 | 3 | 65 | 25.3 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDC2082N251005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 25 |  | 208 | 3 | 65 | 16.7 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDC2082N301005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 30 |  | 208 | 3 | 65 | 16.7 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDC2082N6017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 208 | 3 | 65 | 24.2 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDC2402N251005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 25 |  | 220 - 240 (230) | 3 | 65 | 15.2 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDC2402N301005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 30 |  | 220 - 240 (230) | 3 | 65 | 15.2 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDC2402N3017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 30 |  | 220 - 240 (230) | 3 | 65 | 22 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDC4802N1517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 15 |  | 440 - 480 (460) | 3 | 25 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDC4802N2517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 25 |  | 440 - 480 (460) | 3 | 25 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDC4802N251010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 25 |  | 440 - 480 (460) | 3 | 25 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDC4802N301010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 30 |  | 440 - 480 (460) | 3 | 25 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDC6002N1517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 15 |  | 550 - 600 (575) | 3 | 14 | 9 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDC6002N151010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 15 |  | 550 - 600 (575) | 3 | 14 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDC6002N251010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 25 |  | 550 - 600 (575) | 3 | 14 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDC2002S251005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 25 |  | 200 | 3 | 100 | 17.5 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDC2002S301005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 30 |  | 200 | 3 | 100 | 17.5 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDC2002S6017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 200 | 3 | 100 | 25.3 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDC2082S251005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 25 |  | 208 | 3 | 100 | 16.7 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDC2082S301005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 30 |  | 208 | 3 | 100 | 16.7 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDC2082S6017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 208 | 3 | 100 | 24.2 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDC2402S251005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 25 |  | 220 - 240 (230) | 3 | 100 | 15.2 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDC2402S301005 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 30 |  | 220 - 240 (230) | 3 | 100 | 15.2 | 5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDC2402S3017F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 30 |  | 220 - 240 (230) | 3 | 100 | 22 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 240 | 3 | 5 | 27 | 7.5
[10 empty] | OLR | ABB | CR324C | 240 | 3 | 5 | 27
ABBDC4802S1517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 15 |  | 440 - 480 (460) | 3 | 35 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDC4802S2517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 25 |  | 440 - 480 (460) | 3 | 35 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDC4802S251010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 25 |  | 440 - 480 (460) | 3 | 35 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDC4802S301010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 30 |  | 440 - 480 (460) | 3 | 35 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDC6002S1517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 9 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDC6002S151010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 15 |  | 550 - 600 (575) | 3 | 18 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDC6002S251010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 25 |  | 550 - 600 (575) | 3 | 18 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDC4802H1517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 15 |  | 440 - 480 (460) | 3 | 65 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDC4802H2517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 25 |  | 440 - 480 (460) | 3 | 65 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDC4802H251010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 25 |  | 440 - 480 (460) | 3 | 65 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDC4802H301010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 30 |  | 440 - 480 (460) | 3 | 65 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDC6002H1517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 9 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDC6002H151010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 15 |  | 550 - 600 (575) | 3 | 25 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDC6002H251010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 25 |  | 550 - 600 (575) | 3 | 25 | 11 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 600 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 600 | 3 | 5 | 27
ABBDC4802L1517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 15 |  | 440 - 480 (460) | 3 | 100 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDC4802L2517F5 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 25 |  | 440 - 480 (460) | 3 | 100 | 11 | 7.5 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDC4802L251010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 25 |  | 440 - 480 (460) | 3 | 100 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDC4802L301010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 30 |  | 440 - 480 (460) | 3 | 100 | 14 | 10 | 1399.2 | 1,3,5 |  | Size-1
[10 empty] | MC | ABB | CR305C0 | 480 | 3 | 5 | 27 | 10
[10 empty] | OLR | ABB | CR324C | 480 | 3 | 5 | 27
ABBDD2002N50J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 50 |  | 200 | 3 | 65 | 32.2 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2002N60J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 200 | 3 | 65 | 32.2 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2002N70J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 200 | 3 | 65 | 32.2 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2082N50J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 50 |  | 208 | 3 | 65 | 30.8 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2082N60J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 208 | 3 | 65 | 30.8 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2082N70J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 208 | 3 | 65 | 30.8 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2402N50J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 50 |  | 220 - 240 (230) | 3 | 65 | 28 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2402N60J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 220 - 240 (230) | 3 | 65 | 28 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2402N70J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 220 - 240 (230) | 3 | 65 | 28 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2402N60J015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 220 - 240 (230) | 3 | 65 | 42 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2402N70J015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 220 - 240 (230) | 3 | 65 | 42 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD4802N30H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 30 |  | 440 - 480 (460) | 3 | 25 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802N50H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802N50H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802N60H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802N70H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802N50J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802N60J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802N70J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802N50J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802N60J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802N70J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD6002N30H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 30 |  | 550 - 600 (575) | 3 | 14 | 17 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBDD6002N30H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 30 |  | 550 - 600 (575) | 3 | 14 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBDD6002N50H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 50 |  | 550 - 600 (575) | 3 | 14 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBDD6002N50H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 50 |  | 550 - 600 (575) | 3 | 14 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBDD6002N60H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 60 |  | 550 - 600 (575) | 3 | 14 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBDD6002N70H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 70 |  | 550 - 600 (575) | 3 | 14 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBDD6002N50J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 50 |  | 550 - 600 (575) | 3 | 14 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBDD6002N60J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 60 |  | 550 - 600 (575) | 3 | 14 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBDD6002N70J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 70 |  | 550 - 600 (575) | 3 | 14 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBDD2002S50J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 50 |  | 200 | 3 | 100 | 32.2 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2002S60J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 200 | 3 | 100 | 32.2 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2002S70J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 200 | 3 | 100 | 32.2 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2082S50J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 50 |  | 208 | 3 | 100 | 30.8 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2082S60J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 208 | 3 | 100 | 30.8 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2082S70J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 208 | 3 | 100 | 30.8 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2402S50J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 50 |  | 220 - 240 (230) | 3 | 100 | 28 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2402S60J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 220 - 240 (230) | 3 | 100 | 28 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2402S70J010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 220 - 240 (230) | 3 | 100 | 28 | 10 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2402S60J015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 220 - 240 (230) | 3 | 100 | 42 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD2402S70J015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 220 - 240 (230) | 3 | 100 | 42 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324DXJ | 240 | 3 | 5 | 25-50
ABBDD4802S30H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 30 |  | 440 - 480 (460) | 3 | 35 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802S50H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802S50H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802S60H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802S70H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802S50J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802S60J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802S70J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802S50J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802S60J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802S70J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD6002S30H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 30 |  | 550 - 600 (575) | 3 | 18 | 17 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBDD6002S30H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 30 |  | 550 - 600 (575) | 3 | 18 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBDD6002S50H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBDD6002S50H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBDD6002S60H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBDD6002S70H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBDD6002S50J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBDD6002S60J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBDD6002S70J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBDD4802H30H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 30 |  | 440 - 480 (460) | 3 | 65 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802H50H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802H50H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802H60H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802H70H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802H50J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802H60J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802H70J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802H50J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802H60J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802H70J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD6002H30H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 30 |  | 550 - 600 (575) | 3 | 25 | 17 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBDD6002H30H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 30 |  | 550 - 600 (575) | 3 | 25 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBDD6002H50H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 22 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBDD6002H50H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBDD6002H60H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBDD6002H70H025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 600 | 3 | 5 | 13-27
ABBDD6002H50J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBDD6002H60J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBDD6002H70J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 600 | 3 | 5 | 25-50
ABBDD4802L30H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 30 |  | 440 - 480 (460) | 3 | 100 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802L50H015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 21 | 15 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802L50H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802L60H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802L70H020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXH | 480 | 3 | 5 | 13-27
ABBDD4802L50J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802L60J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802L70J020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802L50J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802L60J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD4802L70J025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 34 | 25 | 1399.2 | 1,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324DXJ | 480 | 3 | 5 | 25-50
ABBDD2002N501010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 50 |  | 200 | 3 | 65 | 32.2 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2002N601010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 200 | 3 | 65 | 32.2 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2002N701010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 200 | 3 | 65 | 32.2 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2082N501010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 50 |  | 208 | 3 | 65 | 30.8 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2082N601010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 208 | 3 | 65 | 30.8 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2082N701010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 208 | 3 | 65 | 30.8 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2402N501010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 50 |  | 220 - 240 (230) | 3 | 65 | 28 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2402N601010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 220 - 240 (230) | 3 | 65 | 28 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2402N701010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 220 - 240 (230) | 3 | 65 | 28 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2402N601015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 220 - 240 (230) | 3 | 65 | 42 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2402N701015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 220 - 240 (230) | 3 | 65 | 42 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD4802N301015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 30 |  | 440 - 480 (460) | 3 | 25 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802N501015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802N501020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802N601020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802N701020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802N501025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802N601025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802N701025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD6002N301015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 30 |  | 550 - 600 (575) | 3 | 14 | 17 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBDD6002N301020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 30 |  | 550 - 600 (575) | 3 | 14 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBDD6002N501020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 50 |  | 550 - 600 (575) | 3 | 14 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBDD6002N501025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 50 |  | 550 - 600 (575) | 3 | 14 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBDD6002N601025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 60 |  | 550 - 600 (575) | 3 | 14 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBDD6002N701025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 70 |  | 550 - 600 (575) | 3 | 14 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBDD2002S501010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 50 |  | 200 | 3 | 100 | 32.2 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2002S601010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 200 | 3 | 100 | 32.2 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2002S701010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 200 | 3 | 100 | 32.2 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2082S501010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 50 |  | 208 | 3 | 100 | 30.8 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2082S601010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 208 | 3 | 100 | 30.8 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2082S701010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 208 | 3 | 100 | 30.8 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 10
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2402S501010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 50 |  | 220 - 240 (230) | 3 | 100 | 28 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2402S601010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 220 - 240 (230) | 3 | 100 | 28 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2402S701010 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 220 - 240 (230) | 3 | 100 | 28 | 10 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2402S601015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 220 - 240 (230) | 3 | 100 | 42 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD2402S701015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 220 - 240 (230) | 3 | 100 | 42 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 240 | 3 | 5 | 45 | 15
[10 empty] | OLR | ABB | CR324D | 240 | 3 | 5 | 45
ABBDD4802S301015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 30 |  | 440 - 480 (460) | 3 | 35 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802S501015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802S501020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802S601020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802S701020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802S501025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802S601025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802S701025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD6002S301015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 30 |  | 550 - 600 (575) | 3 | 18 | 17 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBDD6002S301020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 30 |  | 550 - 600 (575) | 3 | 18 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBDD6002S501020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBDD6002S501025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBDD6002S601025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBDD6002S701025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBDD4802H301015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 30 |  | 440 - 480 (460) | 3 | 65 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802H501015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802H501020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802H601020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802H701020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802H501025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802H601025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802H701025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD6002H301015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 30 |  | 550 - 600 (575) | 3 | 25 | 17 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBDD6002H301020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 30 |  | 550 - 600 (575) | 3 | 25 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBDD6002H501020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 22 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBDD6002H501025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBDD6002H601025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBDD6002H701025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 27 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 600 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 600 | 3 | 5 | 45
ABBDD4802L301015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 30 |  | 440 - 480 (460) | 3 | 100 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802L501015 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 21 | 15 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802L501020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802L601020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802L701020 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 27 | 20 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802L501025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802L601025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDD4802L701025 | E172253 | 2019-07-19 | Vol:2, Sec:3 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 34 | 25 | 1399.2 | 1,3,5 |  | Size-2
[10 empty] | MC | ABB | CR305D0 | 480 | 3 | 5 | 45 | 25
[10 empty] | OLR | ABB | CR324D | 480 | 3 | 5 | 45
ABBDE2002N70L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2002N80L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2002N100L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2002N125L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2002N80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2002N100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2002N125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2002N100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2002N125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2082N60L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2082N70L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2082N80L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2082N100L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2082N80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2082N100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2082N125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2082N100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2082N125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2402N70L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2402N80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2402N100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2402N125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2402N100L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2402N125L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2402N100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2402N125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2402N100M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2402N125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE4802N50L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802N60L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802N70L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802N80L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 80 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802N100L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802N70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802N80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 80 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802N100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802N125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802N100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802N125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802N100M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE4802N125M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE6002N50K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 50 |  | 550 - 600 (575) | 3 | 14 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6002N60K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 60 |  | 550 - 600 (575) | 3 | 14 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6002N70K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 70 |  | 550 - 600 (575) | 3 | 14 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6002N80K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 80 |  | 550 - 600 (575) | 3 | 14 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6002N60L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 60 |  | 550 - 600 (575) | 3 | 14 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002N70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 70 |  | 550 - 600 (575) | 3 | 14 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002N80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 80 |  | 550 - 600 (575) | 3 | 14 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002N100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 100 |  | 550 - 600 (575) | 3 | 14 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002N70L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 70 |  | 550 - 600 (575) | 3 | 14 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002N80L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 80 |  | 550 - 600 (575) | 3 | 14 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002N100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 100 |  | 550 - 600 (575) | 3 | 14 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002N125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 125 |  | 550 - 600 (575) | 3 | 14 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE2002S70L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2002S80L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2002S100L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2002S125L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2002S80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2002S100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2002S125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2002S100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2002S125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2082S60L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2082S70L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2082S80L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2082S100L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2082S80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2082S100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2082S125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2082S100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2082S125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2402S70L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2402S80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2402S100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2402S125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2402S100L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2402S125L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2402S100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2402S125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2402S100M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2402S125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE4802S50L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802S60L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802S70L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802S80L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 80 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802S100L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802S70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802S80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 80 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802S100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802S125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802S100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802S125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802S100M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE4802S125M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE6002S50K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6002S60K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6002S70K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6002S80K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6002S60L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002S70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002S80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002S100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002S70L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002S80L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002S100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002S125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE4802H50L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802H60L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802H70L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802H80L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 80 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802H100L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802H70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802H80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 80 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802H100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802H125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802H100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802H125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802H100M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE4802H125M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE6002H50K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6002H60K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6002H70K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6002H80K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6002H60L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002H70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002H80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002H100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002H70L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002H80L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002H100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6002H125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE4802L50L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802L60L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802L70L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802L80L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 80 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802L100L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802L70L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802L80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 80 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802L100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802L125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802L100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802L125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4802L100M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE4802L125M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE2002N701015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2002N801015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2002N1001015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2002N1251015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2002N801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2002N1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2002N1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2002N1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2002N1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2082N601015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 60 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2082N701015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2082N801015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2082N1001015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2082N801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2082N1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2082N1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2082N1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2082N1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2402N701020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 70 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2402N801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 80 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2402N1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2402N1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2402N1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2402N1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2402N1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2402N1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE4802N501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802N601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802N701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802N801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 80 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802N1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802N701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 70 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802N801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 80 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802N1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802N1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802N1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802N1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE6002N501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 50 |  | 550 - 600 (575) | 3 | 14 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002N601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 60 |  | 550 - 600 (575) | 3 | 14 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002N701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 70 |  | 550 - 600 (575) | 3 | 14 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002N801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 80 |  | 550 - 600 (575) | 3 | 14 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002N601040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 60 |  | 550 - 600 (575) | 3 | 14 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002N701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 70 |  | 550 - 600 (575) | 3 | 14 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002N801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 80 |  | 550 - 600 (575) | 3 | 14 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002N1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 100 |  | 550 - 600 (575) | 3 | 14 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002N701050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 70 |  | 550 - 600 (575) | 3 | 14 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002N801050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 80 |  | 550 - 600 (575) | 3 | 14 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002N1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 100 |  | 550 - 600 (575) | 3 | 14 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002N1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 125 |  | 550 - 600 (575) | 3 | 14 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE2002S701015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2002S801015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2002S1001015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2002S1251015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2002S801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2002S1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2002S1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2002S1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2002S1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2082S601015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 60 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2082S701015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2082S801015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2082S1001015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2082S801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2082S1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2082S1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2082S1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2082S1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2402S701020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 70 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2402S801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 80 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2402S1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2402S1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2402S1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2402S1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2402S1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2402S1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE4802S501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802S601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802S701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802S801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 80 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802S1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802S701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 70 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802S801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 80 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802S1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802S1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802S1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802S1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE6002S501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002S601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002S701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002S801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002S601040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002S701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002S801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002S1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002S701050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 70 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002S801050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002S1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002S1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE4802H501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802H601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802H701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802H801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 80 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802H1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802H701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 70 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802H801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 80 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802H1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802H1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802H1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802H1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE6002H501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002H601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002H701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002H801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002H601040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002H701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002H801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002H1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002H701050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 70 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002H801050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002H1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6002H1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE4802L501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802L601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802L701030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802L801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 80 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802L1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802L701040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 70 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802L801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 80 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802L1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802L1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802L1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4802L1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE2004N80L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2004N100L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2004N110L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2004N125L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2004N80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2004N100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2004N110L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2004N125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2004N100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2004N110M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2004N125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2084N60L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 60 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2084N80L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2084N100L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2084N110L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2084N80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2084N100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2084N110L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2084N125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2084N100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2084N110M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2084N125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2404N80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2404N100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2404N110L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2404N125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2404N100L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2404N110L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2404N125L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2404N100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2404N110M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2404N125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2404N100M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2404N110M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2404N125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE4804N50L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804N60L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804N80L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 80 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804N100L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804N80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 80 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804N100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804N110L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804N125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804N100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804N110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804N125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804N100M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE4804N110M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE4804N125M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE6004N50K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 50 |  | 550 - 600 (575) | 3 | 14 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6004N60K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 60 |  | 550 - 600 (575) | 3 | 14 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6004N80K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 80 |  | 550 - 600 (575) | 3 | 14 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6004N60L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 60 |  | 550 - 600 (575) | 3 | 14 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6004N80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 80 |  | 550 - 600 (575) | 3 | 14 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6004N100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 100 |  | 550 - 600 (575) | 3 | 14 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6004N80L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 80 |  | 550 - 600 (575) | 3 | 14 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6004N100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 100 |  | 550 - 600 (575) | 3 | 14 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6004N110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 110 |  | 550 - 600 (575) | 3 | 14 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6004N125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 125 |  | 550 - 600 (575) | 3 | 14 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE2004S80L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2004S100L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2004S110L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2004S125L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2004S80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2004S100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2004S110L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2004S125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2004S100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2004S110M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2004S125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2084S60L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 60 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2084S80L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2084S100L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2084S110L015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2084S80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2084S100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2084S110L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2084S125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2084S100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2084S110M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2084S125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2404S80L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2404S100L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2404S110L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2404S125L020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2404S100L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2404S110L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2404S125L025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXL | 240 | 3 | 5 | 35-70
ABBDE2404S100M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2404S110M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2404S125M025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2404S100M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2404S110M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE2404S125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 5 | 65-135
ABBDE4804S50L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804S60L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804S80L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 80 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804S100L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804S80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 80 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804S100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804S110L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804S125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804S100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804S110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804S125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804S100M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE4804S110M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE4804S125M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE6004S50K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6004S60K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6004S80K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6004S60L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6004S80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6004S100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6004S80L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6004S100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6004S110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6004S125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE4804H50L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804H60L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804H80L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 80 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804H100L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804H80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 80 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804H100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804H110L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804H125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804H100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804H110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804H125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804H100M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE4804H110M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE4804H125M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE6004H50K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6004H60K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6004H80K030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXK | 600 | 3 | 5 | 17-35
ABBDE6004H60L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6004H80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6004H100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6004H80L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6004H100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6004H110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE6004H125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 5 | 35-70
ABBDE4804L50L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804L60L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804L80L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 80 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804L100L030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804L80L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 80 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804L100L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804L110L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804L125L040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804L100L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804L110L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804L125L050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXL | 480 | 3 | 5 | 35-70
ABBDE4804L100M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE4804L110M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE4804L125M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 5 | 65-135
ABBDE2004N801015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004N1001015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004N1101015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004N1251015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004N801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004N1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004N1101020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004N1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004N1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004N1101025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004N1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084N601015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 60 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084N801015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084N1001015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084N1101015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084N801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084N1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084N1101020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084N1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084N1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084N1101025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084N1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404N801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 80 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404N1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404N1101020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404N1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404N1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404N1101025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404N1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404N1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 100 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404N1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404N1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 220 - 240 (230) | 3 | 65 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE4804N501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 50 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804N601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 60 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804N801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 80 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804N1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804N801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 80 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804N1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804N1101040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804N1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804N1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804N1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804N1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE6004N501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 50 |  | 550 - 600 (575) | 3 | 14 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004N601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 60 |  | 550 - 600 (575) | 3 | 14 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004N801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 80 |  | 550 - 600 (575) | 3 | 14 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004N601040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 60 |  | 550 - 600 (575) | 3 | 14 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004N801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 80 |  | 550 - 600 (575) | 3 | 14 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004N1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 100 |  | 550 - 600 (575) | 3 | 14 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004N801050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 80 |  | 550 - 600 (575) | 3 | 14 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004N1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 100 |  | 550 - 600 (575) | 3 | 14 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004N1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 110 |  | 550 - 600 (575) | 3 | 14 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004N1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 125 |  | 550 - 600 (575) | 3 | 14 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE2004S801015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004S1001015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004S1101015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004S1251015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 48.3 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004S801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004S1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004S1101020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004S1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 62.1 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004S1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004S1101025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2004S1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 78.2 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084S601015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 60 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084S801015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084S1001015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084S1101015 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 46.2 | 15 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084S801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084S1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084S1101020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084S1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 59.4 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084S1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084S1101025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2084S1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 74.8 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 25
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404S801020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 80 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404S1001020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404S1101020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404S1251020 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 54 | 20 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404S1001025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404S1101025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404S1251025 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 68 | 25 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404S1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 100 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404S1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE2404S1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 220 - 240 (230) | 3 | 100 | 80 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 240 | 3 | 5 | 90 | 30
[10 empty] | OLR | ABB | CR324E | 240 | 3 | 5 | 90
ABBDE4804S501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 50 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804S601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 60 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804S801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 80 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804S1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804S801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 80 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804S1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804S1101040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804S1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804S1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804S1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804S1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE6004S501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 50 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004S601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004S801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004S601040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 60 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004S801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004S1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004S801050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 80 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004S1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004S1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004S1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE4804H501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 50 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804H601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 60 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804H801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 80 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804H1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804H801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 80 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804H1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804H1101040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804H1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804H1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804H1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804H1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE6004H501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 50 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004H601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004H801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 32 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004H601040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 60 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004H801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004H1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 41 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004H801050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 80 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004H1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004H1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE6004H1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 52 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 600 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 600 | 3 | 5 | 90
ABBDE4804L501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 50 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804L601030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 60 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804L801030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 80 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804L1001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 40 | 30 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804L801040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 80 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804L1001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804L1101040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804L1251040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 52 | 40 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804L1001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804L1101050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDE4804L1251050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 65 | 50 | 5288.35 | 1,3,5 |  | Size-3
[10 empty] | MC | ABB | CR305E0 | 480 | 3 | 5 | 90 | 50
[10 empty] | OLR | ABB | CR324E | 480 | 3 | 5 | 90
ABBDF2004N125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2004N150M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2004N175M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2004N200M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2004N150M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 200 | 3 | 65 | 120 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2004N175M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 200 | 3 | 65 | 120 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2004N200M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 200 | 3 | 65 | 120 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2084N110M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2084N125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2084N150M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2084N175M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2084N200M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2084N150M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 208 | 3 | 65 | 114 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2084N175M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 208 | 3 | 65 | 114 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2084N200M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 208 | 3 | 65 | 114 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2404N150M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 220 - 240 (230) | 3 | 65 | 104 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2404N175M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 220 - 240 (230) | 3 | 65 | 104 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2404N200M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 220 - 240 (230) | 3 | 65 | 104 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2404N175M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 220 - 240 (230) | 3 | 65 | 130 | 50 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2404N200M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 220 - 240 (230) | 3 | 65 | 130 | 50 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF4804N100M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804N110M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804N125M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804N150M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 150 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804N175M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 175 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804N200M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 200 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804N125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804N150M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 150 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804N175M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 175 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804N200M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 200 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804N175M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 175 |  | 440 - 480 (460) | 3 | 25 | 124 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804N200M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 200 |  | 440 - 480 (460) | 3 | 25 | 124 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF6004N100L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 100 |  | 550 - 600 (575) | 3 | 14 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBDF6004N110L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 110 |  | 550 - 600 (575) | 3 | 14 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBDF6004N125L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 125 |  | 550 - 600 (575) | 3 | 14 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBDF6004N150L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 150 |  | 550 - 600 (575) | 3 | 14 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBDF6004N100M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 100 |  | 550 - 600 (575) | 3 | 14 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004N110M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 110 |  | 550 - 600 (575) | 3 | 14 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004N125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 125 |  | 550 - 600 (575) | 3 | 14 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004N150M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 150 |  | 550 - 600 (575) | 3 | 14 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004N175M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 175 |  | 550 - 600 (575) | 3 | 14 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004N200M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 200 |  | 550 - 600 (575) | 3 | 14 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004N125M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 125 |  | 550 - 600 (575) | 3 | 14 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004N150M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 150 |  | 550 - 600 (575) | 3 | 14 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004N175M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 175 |  | 550 - 600 (575) | 3 | 14 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004N200M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 200 |  | 550 - 600 (575) | 3 | 14 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF2004S125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2004S150M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2004S175M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2004S200M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2004S150M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 200 | 3 | 100 | 120 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2004S175M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 200 | 3 | 100 | 120 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2004S200M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 200 | 3 | 100 | 120 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2084S110M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2084S125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2084S150M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2084S175M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2084S200M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2084S150M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 208 | 3 | 100 | 114 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2084S175M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 208 | 3 | 100 | 114 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2084S200M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 208 | 3 | 100 | 114 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2404S150M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 220 - 240 (230) | 3 | 100 | 104 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2404S175M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 220 - 240 (230) | 3 | 100 | 104 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2404S200M040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 220 - 240 (230) | 3 | 100 | 104 | 40 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2404S175M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 220 - 240 (230) | 3 | 100 | 130 | 50 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2404S200M050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 220 - 240 (230) | 3 | 100 | 130 | 50 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF4804S100M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804S110M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804S125M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804S150M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 150 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804S175M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 175 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804S200M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 200 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804S125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804S150M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 150 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804S175M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 175 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804S200M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 200 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804S175M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 175 |  | 440 - 480 (460) | 3 | 35 | 124 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804S200M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 200 |  | 440 - 480 (460) | 3 | 35 | 124 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF6004S100L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBDF6004S110L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBDF6004S125L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBDF6004S150L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 150 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBDF6004S100M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004S110M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004S125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004S150M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 150 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004S175M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 175 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004S200M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 200 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004S125M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004S150M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 150 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004S175M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 175 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004S200M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 200 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF4804H100M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804H110M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804H125M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804H150M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 150 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804H175M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 175 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804H200M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 200 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804H125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804H150M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 150 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804H175M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 175 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804H200M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 200 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804H175M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 175 |  | 440 - 480 (460) | 3 | 65 | 124 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804H200M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 200 |  | 440 - 480 (460) | 3 | 65 | 124 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF6004H100L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBDF6004H110L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBDF6004H125L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBDF6004H150L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 150 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBDF6004H100M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004H110M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004H125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004H150M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 150 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004H175M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 175 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004H200M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 200 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004H125M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004H150M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 150 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004H175M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 175 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6004H200M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 200 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF4804L100M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804L110M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804L125M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804L150M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 150 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804L175M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 175 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804L200M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 200 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804L125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804L150M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 150 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804L175M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 175 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804L200M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 200 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804L175M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 175 |  | 440 - 480 (460) | 3 | 100 | 124 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4804L200M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 200 |  | 440 - 480 (460) | 3 | 100 | 124 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF2004N1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2004N1501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2004N1751030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2004N2001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2004N1501040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 200 | 3 | 65 | 120 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2004N1751040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 200 | 3 | 65 | 120 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2004N2001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 200 | 3 | 65 | 120 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2084N1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 110 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2084N1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2084N1501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2084N1751030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2084N2001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2084N1501040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 208 | 3 | 65 | 114 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2084N1751040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 208 | 3 | 65 | 114 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2084N2001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 208 | 3 | 65 | 114 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2404N1501040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 150 |  | 220 - 240 (230) | 3 | 65 | 104 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2404N1751040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 220 - 240 (230) | 3 | 65 | 104 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2404N2001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 220 - 240 (230) | 3 | 65 | 104 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2404N1751050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 175 |  | 220 - 240 (230) | 3 | 65 | 130 | 50 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2404N2001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 240 | 3 | 65 | 200 |  | 220 - 240 (230) | 3 | 65 | 130 | 50 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF4804N1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804N1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 110 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804N1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804N1501060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 150 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804N1751060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 175 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804N2001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 200 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804N1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804N1501075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 150 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804N1751075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 175 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804N2001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 200 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804N1751100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 175 |  | 440 - 480 (460) | 3 | 25 | 124 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804N2001100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 480 | 3 | 25 | 200 |  | 440 - 480 (460) | 3 | 25 | 124 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF6004N1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 100 |  | 550 - 600 (575) | 3 | 14 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004N1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 110 |  | 550 - 600 (575) | 3 | 14 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004N1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 125 |  | 550 - 600 (575) | 3 | 14 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004N1501060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 150 |  | 550 - 600 (575) | 3 | 14 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004N1001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 100 |  | 550 - 600 (575) | 3 | 14 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004N1101075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 110 |  | 550 - 600 (575) | 3 | 14 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004N1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 125 |  | 550 - 600 (575) | 3 | 14 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004N1501075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 150 |  | 550 - 600 (575) | 3 | 14 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004N1751075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 175 |  | 550 - 600 (575) | 3 | 14 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004N2001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 200 |  | 550 - 600 (575) | 3 | 14 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004N1251100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 125 |  | 550 - 600 (575) | 3 | 14 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004N1501100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 150 |  | 550 - 600 (575) | 3 | 14 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004N1751100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 175 |  | 550 - 600 (575) | 3 | 14 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004N2001100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4N*3* | 600 | 3 | 14 | 200 |  | 550 - 600 (575) | 3 | 14 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF2004S1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2004S1501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2004S1751030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2004S2001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2004S1501040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 200 | 3 | 100 | 120 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2004S1751040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 200 | 3 | 100 | 120 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2004S2001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 200 | 3 | 100 | 120 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2084S1101030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 110 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2084S1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2084S1501030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2084S1751030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2084S2001030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2084S1501040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 208 | 3 | 100 | 114 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2084S1751040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 208 | 3 | 100 | 114 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2084S2001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 208 | 3 | 100 | 114 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2404S1501040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 150 |  | 220 - 240 (230) | 3 | 100 | 104 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2404S1751040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 220 - 240 (230) | 3 | 100 | 104 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2404S2001040 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 220 - 240 (230) | 3 | 100 | 104 | 40 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2404S1751050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 175 |  | 220 - 240 (230) | 3 | 100 | 130 | 50 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2404S2001050 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 240 | 3 | 100 | 200 |  | 220 - 240 (230) | 3 | 100 | 130 | 50 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 50
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF4804S1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804S1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 110 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804S1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804S1501060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 150 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804S1751060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 175 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804S2001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 200 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804S1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804S1501075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 150 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804S1751075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 175 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804S2001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 200 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804S1751100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 175 |  | 440 - 480 (460) | 3 | 35 | 124 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804S2001100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 480 | 3 | 35 | 200 |  | 440 - 480 (460) | 3 | 35 | 124 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF6004S1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004S1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004S1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004S1501060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 150 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004S1001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004S1101075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 110 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004S1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004S1501075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 150 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004S1751075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 175 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004S2001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 200 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004S1251100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004S1501100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 150 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004S1751100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 175 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004S2001100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4S*3* | 600 | 3 | 18 | 200 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF4804H1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804H1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 110 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804H1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804H1501060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 150 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804H1751060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 175 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804H2001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 200 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804H1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804H1501075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 150 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804H1751075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 175 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804H2001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 200 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804H1751100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 175 |  | 440 - 480 (460) | 3 | 65 | 124 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804H2001100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 480 | 3 | 65 | 200 |  | 440 - 480 (460) | 3 | 65 | 124 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF6004H1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004H1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004H1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004H1501060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 150 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004H1001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004H1101075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 110 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004H1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004H1501075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 150 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004H1751075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 175 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004H2001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 200 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004H1251100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004H1501100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 150 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004H1751100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 175 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6004H2001100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4H*3* | 600 | 3 | 25 | 200 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF4804L1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804L1101060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 110 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804L1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804L1501060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 150 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804L1751060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 175 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804L2001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 200 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804L1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804L1501075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 150 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804L1751075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 175 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804L2001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 200 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804L1751100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 175 |  | 440 - 480 (460) | 3 | 100 | 124 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4804L2001100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT4L*3* | 480 | 3 | 100 | 200 |  | 440 - 480 (460) | 3 | 100 | 124 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF2002N125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2082N125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF4802N100M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4802N125M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4802N125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF6002N100L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 100 |  | 550 - 600 (575) | 3 | 14 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBDF6002N125L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 125 |  | 550 - 600 (575) | 3 | 14 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBDF6002N100M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 100 |  | 550 - 600 (575) | 3 | 14 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6002N125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 125 |  | 550 - 600 (575) | 3 | 14 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6002N125M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 125 |  | 550 - 600 (575) | 3 | 14 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF2002S125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF2082S125M030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324FXM | 240 | 3 | 10 | 65-135
ABBDF4802S100M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4802S125M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4802S125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF6002S100L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBDF6002S125L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBDF6002S100M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6002S125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6002S125M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF4802H100M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4802H125M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4802H125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF6002H100L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBDF6002H125L060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXL | 600 | 3 | 10 | 35-70
ABBDF6002H100M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6002H125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF6002H125M100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 600 | 3 | 10 | 65-135
ABBDF4802L100M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4802L125M060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF4802L125M075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324FXM | 480 | 3 | 10 | 65-135
ABBDF2002N1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 200 | 3 | 65 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2082N1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 240 | 3 | 65 | 125 |  | 208 | 3 | 65 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF4802N1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 100 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4802N1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4802N1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 480 | 3 | 25 | 125 |  | 440 - 480 (460) | 3 | 25 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF6002N1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 100 |  | 550 - 600 (575) | 3 | 14 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6002N1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 125 |  | 550 - 600 (575) | 3 | 14 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6002N1001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 100 |  | 550 - 600 (575) | 3 | 14 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6002N1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 125 |  | 550 - 600 (575) | 3 | 14 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6002N1251100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2N*3* | 600 | 3 | 14 | 125 |  | 550 - 600 (575) | 3 | 14 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF2002S1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 200 | 3 | 100 | 92 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF2082S1251030 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 240 | 3 | 100 | 125 |  | 208 | 3 | 100 | 88 | 30 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 240 | 3 | 10 | 135 | 40
[10 empty] | OLR | ABB | CR324F | 240 | 3 | 10 | 135
ABBDF4802S1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 100 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4802S1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4802S1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 480 | 3 | 35 | 125 |  | 440 - 480 (460) | 3 | 35 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF6002S1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6002S1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6002S1001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 100 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6002S1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6002S1251100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2S*3* | 600 | 3 | 18 | 125 |  | 550 - 600 (575) | 3 | 18 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF4802H1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 100 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4802H1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4802H1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 480 | 3 | 65 | 125 |  | 440 - 480 (460) | 3 | 65 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF6002H1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6002H1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 62 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6002H1001075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 100 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6002H1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 77 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF6002H1251100 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2H*3* | 600 | 3 | 25 | 125 |  | 550 - 600 (575) | 3 | 25 | 99 | 100 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 600 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 600 | 3 | 10 | 135
ABBDF4802L1001060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 100 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4802L1251060 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 77 | 60 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
ABBDF4802L1251075 | E172253 | 2019-07-20 | Vol:2, Sec:4 | [5 empty] | D | ICB | ABB | XT2L*3* | 480 | 3 | 100 | 125 |  | 440 - 480 (460) | 3 | 100 | 96 | 75 | 5288.35 | 1,3,5 |  | Size-4
[10 empty] | MC | ABB | CR305F0 | 480 | 3 | 10 | 135 | 100
[10 empty] | OLR | ABB | CR324F | 480 | 3 | 10 | 135
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application.