## Type A
Issued: 2017-01-31
Revised: 2022-07-27
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | Conditions of Use
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating
LSIS1601 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 7.5 | 2 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-6a | 240 | 3 | 5 | 9.6
LSIS1601.01 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1601.02 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1601.03 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1601.04 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1601.05 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.63 - 1
LSIS1601.06 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1 - 1.6
LSIS1601.07 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1601.08 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 2.5 - 4
LSIS1601.09 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 4 - 6
LSIS1601.10 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 5 - 8
LSIS1601.11 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 6 - 9
LSIS1601.12 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 7 - 10
LSIS1602 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 7.5 | 2 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-9a | 240 | 3 | 5 | 9.6
LSIS1602.01 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1602.02 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1602.03 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1602.04 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1602.05 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.63 - 1
LSIS1602.06 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1 - 1.6
LSIS1602.07 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1602.08 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 2.5 - 4
LSIS1602.09 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 4 - 6
LSIS1602.10 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 5 - 8
LSIS1602.11 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 6 - 9
LSIS1602.12 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 7 - 10
LSIS1603 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 10.6 | 3 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-12a | 240 | 3 | 5 | 15.2
LSIS1603.01 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1603.02 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1603.03 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1603.04 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1603.05 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.63 - 1
LSIS1603.06 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1 - 1.6
LSIS1603.07 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1603.08 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 2.5 - 4
LSIS1603.09 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 4 - 6
LSIS1603.10 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 5 - 8
LSIS1603.11 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 6 - 9
LSIS1603.12 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 7 - 10
LSIS1603.13 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 9 - 13
LSIS1603.14 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 12 - 18
LSIS1604 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 18 | - | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-18a | 240 | 3 | 5 | 22
LSIS1604.01 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1604.02 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1604.03 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1604.04 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1604.05 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.63 - 1
LSIS1604.06 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1 - 1.6
LSIS1604.07 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1604.08 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 2.5 - 4
LSIS1604.09 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 4 - 6
LSIS1604.10 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 5 - 8
LSIS1604.11 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 6 - 9
LSIS1604.12 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 7 - 10
LSIS1604.13 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 9 - 13
LSIS1604.14 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 12 - 18
LSIS1605 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 7.5 | 2 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-9b | 240 | 3 | 5 | 9.6
LSIS1605.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 1 | 0.1 - 0.16
LSIS1605.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 1 | 0.16 - 0.25
LSIS1605.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 1 | 0.25 - 0.4
LSIS1605.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 1 | 0.4 - 0.63
LSIS1605.05 |  | OLR | LSIS | MT-32 | 240 | 3 | 1 | 0.63 - 1
LSIS1605.06 |  | OLR | LSIS | MT-32 | 240 | 3 | 1 | 1 - 1.6
LSIS1605.07 |  | OLR | LSIS | MT-32 | 240 | 3 | 1 | 1.6 - 2.5
LSIS1605.08 |  | OLR | LSIS | MT-32 | 240 | 3 | 1 | 2.5 - 4
LSIS1605.09 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 4 - 6
LSIS1605.10 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 5 - 8
LSIS1605.11 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 6 - 9
LSIS1605.12 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 7 - 10
LSIS1606 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 10.6 | 3 | 1712 | 1 , 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-12b | 240 | 3 | 5 | 15.2
LSIS1606.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1606.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1606.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1606.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1606.05 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.63 - 1
LSIS1606.06 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1 - 1.6
LSIS1606.07 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1606.08 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 2.5 - 4
LSIS1606.09 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 4 - 6
LSIS1606.10 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 5 - 8
LSIS1606.11 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 6 - 9
LSIS1606.12 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 7 - 10
LSIS1606.13 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 9 - 13
LSIS1606.14 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 12 - 18
LSIS1607 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 22 | - | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-18b | 240 | 3 | 5 | 22
LSIS1607.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1607.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1607.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1607.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1607.05 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.63 - 1
LSIS1607.06 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1 - 1.6
LSIS1607.07 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1607.08 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 2.5 - 4
LSIS1607.09 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 4 - 6
LSIS1607.10 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 5 - 8
LSIS1607.11 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 6 - 9
LSIS1607.12 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 7 - 10
LSIS1607.13 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 9 - 13
LSIS1607.14 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 12 - 18
LSIS1607.15 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 16 - 22
LSIS1608 | A [ version C1(a)] | FDS | ABB | OS60GJ12P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 24.2 | 7.5 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-22b | 240 | 3 | 5 | 28
LSIS1608.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 12 - 18
LSIS1608.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 16 - 22
LSIS1608.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 18 - 25
LSIS1608.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 22 - 32
LSIS1609 | A [ version C1(a)] | FDS | ABB | OS60GJ12P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 24.2 | 7.5 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-32a | 240 | 3 | 5 | 28
LSIS1609.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 12 - 18
LSIS1609.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 16 - 22
LSIS1609.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 18 - 25
LSIS1609.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 22 - 32
LSIS1610 | A [ version C1(a)] | FDS | ABB | OS100GJ03P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 40 | - | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-40a | 240 | 3 | 5 | 42
LSIS1610.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 22 - 32
LSIS1610.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 28 - 40
LSIS1611 | A [ version C1(a)] | FDS | ABB | OS100GJ03P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 59.4 | 20 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-50a | 240 | 3 | 5 | 68
LSIS1611.01 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 24 - 36
LSIS1611.02 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 28 - 40
LSIS1611.03 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 34 - 50
LSIS1611.04 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 45 - 65
LSIS1612 | A [ version C1(a)] | FDS | ABB | OS200J03P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 65 | - | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-65a | 240 | 3 | 5 | 80
LSIS1612.01 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 34 - 50
LSIS1612.02 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 45 - 65
LSIS1613 | A [ version C1(a)] | FDS | ABB | OS200J03P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 74.8 | 25 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-75a | 240 | 3 | 5 | 80
LSIS1613.01 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 34 - 50
LSIS1613.02 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 45 - 65
LSIS1613.03 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 54 - 75
LSIS1613.04 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 63 - 85
LSIS1613.05 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 70 - 95
LSIS1614 | A [ version C1(a)] | FDS | ABB | OS200J03P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 88 | 30 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-85a | 240 | 3 | 5 | 104
LSIS1614.01 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 34 - 50
LSIS1614.02 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 45 - 65
LSIS1614.03 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 54 - 75
LSIS1614.04 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 63 - 85
LSIS1614.05 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 70 - 95
LSIS1614.06 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 80 - 100
LSIS1615 | A [ version C1(a)] | FDS | ABB | OS200J03P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 88 | 30 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-100a | 240 | 3 | 5 | 104
LSIS1615.01 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 34 - 50
LSIS1615.02 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 45 - 65
LSIS1615.03 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 54 - 75
LSIS1615.04 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 63 - 85
LSIS1615.05 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 70 - 95
LSIS1615.06 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 80 - 100
LSIS1616 | A [ version C1(a)] | FDS | ABB | OS200J03P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 104 | - | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-130a | 240 | 3 | 5 | 104
LSIS1616.01 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 34 - 50
LSIS1616.02 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 45 - 65
LSIS1616.03 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 54 - 75
LSIS1616.04 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 63 - 85
LSIS1616.05 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 80 - 105
LSIS1617 | A [ version C1(a)] | FDS | ABB | OS200J03P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 114 | 40 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-150a | 240 | 3 | 10 | 130
LSIS1617.01 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 34 - 50
LSIS1617.02 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 45 - 65
LSIS1617.03 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 54 - 75
LSIS1617.04 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 63 - 85
LSIS1617.05 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 80 - 105
LSIS1617.06 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 95 - 130
LSIS1618 | A [ version C1(a)] | FDS | ABB | OS400J03P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 154 | - | 11977 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-185a | 240 | 3 | 10 | 154
LSIS1618.01 |  | OLR | LSIS | MT-225 | 240 | 3 | 5 | 65 ~ 100
LSIS1618.02 |  | OLR | LSIS | MT-225 | 240 | 3 | 5 | 85 ~ 125
LSIS1618.03 |  | OLR | LSIS | MT-225 | 240 | 3 | 10 | 100 ~ 160
LSIS1619 | A [ version C1(a)] | FDS | ABB | OS400J03P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 169 | 60 | 11977 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-225a | 240 | 3 | 10 | 192
LSIS1619.01 |  | OLR | LSIS | MT-225 | 240 | 3 | 5 | 65 ~ 100
LSIS1619.02 |  | OLR | LSIS | MT-225 | 240 | 3 | 5 | 85 ~ 125
LSIS1619.03 |  | OLR | LSIS | MT-225 | 240 | 3 | 10 | 100 ~ 160
LSIS1619.04 |  | OLR | LSIS | MT-225 | 240 | 3 | 10 | 120 ~ 185
LSIS1619.05 |  | OLR | LSIS | MT-225 | 240 | 3 | 10 | 160 ~ 240
LSIS1620 | A [ version C1(a)] | FDS | ABB | OS400J03P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 211 | 75 | 11977 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-265a | 240 | 3 | 10 | 248
LSIS1620.01 |  | OLR | LSIS | MT-400 | 240 | 3 | 5 | 85 ~ 125
LSIS1620.02 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 100 ~ 160
LSIS1620.03 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 120 ~ 185
LSIS1620.04 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 160 ~ 240
LSIS1621 | A [ version C1(a)] | FDS | ABB | OS600J03P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 273 | 100 | 11977 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-330a | 240 | 3 | 10 | 312
LSIS1621.01 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 160 ~ 240
LSIS1621.02 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 200 ~ 330
LSIS1622 | A [ version C1(a)] | FDS | ABB | OS600J03P | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 343 | 125 | 27339 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-400a | 240 | 3 | 10 | 360
LSIS1622.01 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 160 ~ 240
LSIS1622.02 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 200 ~ 330
LSIS1622.03 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 260 ~ 400
LSIS1 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 9.6 | 3 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-6a | 240 | 3 | 5 | 9.6
LSIS1.01 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1.02 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1.03 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1.04 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1.05 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.63 - 1
LSIS1.06 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1 - 1.6
LSIS1.07 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1.08 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 2.5 - 4
LSIS1.09 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 4 - 6
LSIS1.10 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 5 - 8
LSIS1.11 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 6 - 9
LSIS1.12 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 7 - 10
LSIS2 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 9.6 | 3 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-9a | 240 | 3 | 5 | 9.6
LSIS2.01 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.1 - 0.16
LSIS2.02 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.16 - 0.25
LSIS2.03 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.25 - 0.4
LSIS2.04 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.4 - 0.63
LSIS2.05 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.63 - 1
LSIS2.06 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1 - 1.6
LSIS2.07 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1.6 - 2.5
LSIS2.08 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 2.5 - 4
LSIS2.09 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 4 - 6
LSIS2.10 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 5 - 8
LSIS2.11 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 6 - 9
LSIS2.12 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 7 - 10
LSIS3 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 15.2 | 5 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-12a | 240 | 3 | 5 | 15.2
LSIS3.01 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.1 - 0.16
LSIS3.02 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.16 - 0.25
LSIS3.03 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.25 - 0.4
LSIS3.04 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.4 - 0.63
LSIS3.05 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.63 - 1
LSIS3.06 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1 - 1.6
LSIS3.07 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1.6 - 2.5
LSIS3.08 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 2.5 - 4
LSIS3.09 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 4 - 6
LSIS3.10 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 5 - 8
LSIS3.11 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 6 - 9
LSIS3.12 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 7 - 10
LSIS3.13 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 9 - 13
LSIS3.14 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 12 - 18
LSIS4 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 18 | 7.5 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-18a | 240 | 3 | 5 | 22
LSIS4.01 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.1 - 0.16
LSIS4.02 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.16 - 0.25
LSIS4.03 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.25 - 0.4
LSIS4.04 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.4 - 0.63
LSIS4.05 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.63 - 1
LSIS4.06 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1 - 1.6
LSIS4.07 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1.6 - 2.5
LSIS4.08 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 2.5 - 4
LSIS4.09 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 4 - 6
LSIS4.10 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 5 - 8
LSIS4.11 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 6 - 9
LSIS4.12 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 7 - 10
LSIS4.13 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 9 - 13
LSIS4.14 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 12 - 18
LSIS5 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 9.6 | 3 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-9b | 240 | 3 | 5 | 9.6
LSIS5.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.1 - 0.16
LSIS5.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.16 - 0.25
LSIS5.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.25 - 0.4
LSIS5.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.4 - 0.63
LSIS5.05 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.63 - 1
LSIS5.06 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1 - 1.6
LSIS5.07 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1.6 - 2.5
LSIS5.08 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 2.5 - 4
LSIS5.09 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 4 - 6
LSIS5.10 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 5 - 8
LSIS5.11 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 6 - 9
LSIS5.12 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 7 - 10
LSIS6 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 15.2 | 5 | 1712 | 1 , 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-12b | 240 | 3 | 5 | 15.2
LSIS6.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.1 - 0.16
LSIS6.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.16 - 0.25
LSIS6.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.25 - 0.4
LSIS6.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.4 - 0.63
LSIS6.05 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.63 - 1
LSIS6.06 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1 - 1.6
LSIS6.07 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1.6 - 2.5
LSIS6.08 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 2.5 - 4
LSIS6.09 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 4 - 6
LSIS6.10 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 5 - 8
LSIS6.11 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 6 - 9
LSIS6.12 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 7 - 10
LSIS6.13 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 9 - 13
LSIS6.14 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 12 - 18
LSIS7 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 22 | 7.5 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-18b | 240 | 3 | 5 | 22
LSIS7.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.1 - 0.16
LSIS7.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.16 - 0.25
LSIS7.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.25 - 0.4
LSIS7.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.4 - 0.63
LSIS7.05 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.63 - 1
LSIS7.06 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1 - 1.6
LSIS7.07 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1.6 - 2.5
LSIS7.08 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 2.5 - 4
LSIS7.09 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 4 - 6
LSIS7.10 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 5 - 8
LSIS7.11 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 6 - 9
LSIS7.12 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 7 - 10
LSIS7.13 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 9 - 13
LSIS7.14 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 12 - 18
LSIS7.15 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 16 - 22
LSIS8 | A [ version C1(a)] | FDS | ABB | OS60GJ12P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 28 | 10 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-22b | 240 | 3 | 5 | 28
LSIS8.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 12 - 18
LSIS8.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 16 - 22
LSIS8.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 18 - 25
LSIS8.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 22 - 32
LSIS9 | A [ version C1(a)] | FDS | ABB | OS60GJ12P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 28 | 10 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-32a | 240 | 3 | 5 | 28
LSIS9.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 12 - 18
LSIS9.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 16 - 22
LSIS9.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 18 - 25
LSIS9.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 22 - 32
LSIS10 | A [ version C1(a)] | FDS | ABB | OS100GJ03P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 40 | 15 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-40a | 240 | 3 | 5 | 42
LSIS10.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 22 - 32
LSIS10.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 28 - 40
LSIS11 | A [ version C1(a)] | FDS | ABB | OS100GJ03P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 65 | 25 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-50a | 240 | 3 | 5 | 68
LSIS11.01 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 24 - 36
LSIS11.02 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 28 - 40
LSIS11.03 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 34 - 50
LSIS11.04 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 45 - 65
LSIS12 | A [ version C1(a)] | FDS | ABB | OS200J03P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 65 | 30 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-65a | 240 | 3 | 5 | 80
LSIS12.01 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 34 - 50
LSIS12.02 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 45 - 65
LSIS13 | A [ version C1(a)] | FDS | ABB | OS200J03P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 80 | 30 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-75a | 240 | 3 | 5 | 80
LSIS13.01 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 34 - 50
LSIS13.02 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 45 - 65
LSIS13.03 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 54 - 75
LSIS13.04 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 63 - 85
LSIS13.05 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 70 - 95
LSIS14 | A [ version C1(a)] | FDS | ABB | OS200J03P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 100 | 40 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-85a | 240 | 3 | 5 | 104
LSIS14.01 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 34 - 50
LSIS14.02 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 45 - 65
LSIS14.03 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 54 - 75
LSIS14.04 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 63 - 85
LSIS14.05 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 70 - 95
LSIS14.06 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 80 - 100
LSIS15 | A [ version C1(a)] | FDS | ABB | OS200J03P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 100 | 40 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-100a | 240 | 3 | 5 | 104
LSIS15.01 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 34 - 50
LSIS15.02 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 45 - 65
LSIS15.03 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 54 - 75
LSIS15.04 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 63 - 85
LSIS15.05 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 70 - 95
LSIS15.06 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 80 - 100
LSIS16 | A [ version C1(a)] | FDS | ABB | OS200J03P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 104 | 40 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-130a | 240 | 3 | 5 | 104
LSIS16.01 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 34 - 50
LSIS16.02 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 45 - 65
LSIS16.03 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 54 - 75
LSIS16.04 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 63 - 85
LSIS16.05 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 80 - 105
LSIS17 | A [ version C1(a)] | FDS | ABB | OS200J03P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 130 | 50 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-150a | 240 | 3 | 10 | 130
LSIS17.01 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 34 - 50
LSIS17.02 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 45 - 65
LSIS17.03 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 54 - 75
LSIS17.04 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 63 - 85
LSIS17.05 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 80 - 105
LSIS17.06 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 95 - 130
LSIS18 | A [ version C1(a)] | FDS | ABB | OS400J03P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 154 | 60 | 11977 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-185a | 240 | 3 | 10 | 154
LSIS18.01 |  | OLR | LSIS | MT-225 | 240 | 3 | 5 | 65 ~ 100
LSIS18.02 |  | OLR | LSIS | MT-225 | 240 | 3 | 5 | 85 ~ 125
LSIS18.03 |  | OLR | LSIS | MT-225 | 240 | 3 | 10 | 100 ~ 160
LSIS19 | A [ version C1(a)] | FDS | ABB | OS400J03P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 192 | 75 | 11977 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-225a | 240 | 3 | 10 | 192
LSIS19.01 |  | OLR | LSIS | MT-225 | 240 | 3 | 5 | 65 ~ 100
LSIS19.02 |  | OLR | LSIS | MT-225 | 240 | 3 | 5 | 85 ~ 125
LSIS19.03 |  | OLR | LSIS | MT-225 | 240 | 3 | 10 | 100 ~ 160
LSIS19.04 |  | OLR | LSIS | MT-225 | 240 | 3 | 10 | 120 ~ 185
LSIS19.05 |  | OLR | LSIS | MT-225 | 240 | 3 | 10 | 160 ~ 240
LSIS20 | A [ version C1(a)] | FDS | ABB | OS400J03P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 240 | 100 | 11977 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-265a | 240 | 3 | 10 | 248
LSIS20.01 |  | OLR | LSIS | MT-400 | 240 | 3 | 5 | 85 ~ 125
LSIS20.02 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 100 ~ 160
LSIS20.03 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 120 ~ 185
LSIS20.04 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 160 ~ 240
LSIS21 | A [ version C1(a)] | FDS | ABB | OS600J03P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 312 | 125 | 11977 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-330a | 240 | 3 | 10 | 312
LSIS21.01 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 160 ~ 240
LSIS21.02 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 200 ~ 330
LSIS22 | A [ version C1(a)] | FDS | ABB | OS600J03P | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 360 | 150 | 27339 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-400a | 240 | 3 | 10 | 360
LSIS22.01 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 160 ~ 240
LSIS22.02 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 200 ~ 330
LSIS22.03 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 260 ~ 400
LSIS23 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 7.6 | 5 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-6a | 480 | 3 | 5 | 7.6
LSIS23.01 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.1 - 0.16
LSIS23.02 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.16 - 0.25
LSIS23.03 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.25 - 0.4
LSIS23.04 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.4 - 0.63
LSIS23.05 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.63 - 1
LSIS23.06 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 1 - 1.6
LSIS23.07 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 1.6 - 2.5
LSIS23.08 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 2.5 - 4
LSIS23.09 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 4 - 6
LSIS23.10 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 5 - 8
LSIS23.11 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 6 - 9
LSIS23.12 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 7 - 10
LSIS24 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 7.6 | 5 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-9a | 480 | 3 | 5 | 7.6
LSIS24.01 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.1 - 0.16
LSIS24.02 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.16 - 0.25
LSIS24.03 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.25 - 0.4
LSIS24.04 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.4 - 0.63
LSIS24.05 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.63 - 1
LSIS24.06 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 1 - 1.6
LSIS24.07 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 1.6 - 2.5
LSIS24.08 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 2.5 - 4
LSIS24.09 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 4 - 6
LSIS24.10 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 5 - 8
LSIS24.11 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 6 - 9
LSIS24.12 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 7 - 10
LSIS25 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 11 | 7.5 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-12a | 480 | 3 | 5 | 11
LSIS25.01 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.1 - 0.16
LSIS25.02 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.16 - 0.25
LSIS25.03 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.25 - 0.4
LSIS25.04 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.4 - 0.63
LSIS25.05 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.63 - 1
LSIS25.06 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 1 - 1.6
LSIS25.07 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 1.6 - 2.5
LSIS25.08 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 2.5 - 4
LSIS25.09 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 4 - 6
LSIS25.10 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 5 - 8
LSIS25.11 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 6 - 9
LSIS25.12 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 7 - 10
LSIS25.13 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 9 - 13
LSIS26 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 14 | 10 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-18a | 480 | 3 | 5 | 14
LSIS26.01 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.1 - 0.16
LSIS26.02 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.16 - 0.25
LSIS26.03 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.25 - 0.4
LSIS26.04 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.4 - 0.63
LSIS26.05 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.63 - 1
LSIS26.06 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 1 - 1.6
LSIS26.07 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 1.6 - 2.5
LSIS26.08 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 2.5 - 4
LSIS26.09 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 4 - 6
LSIS26.10 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 5 - 8
LSIS26.11 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 6 - 9
LSIS26.12 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 7 - 10
LSIS26.13 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 9 - 13
LSIS26.14 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 12 - 18
LSIS27 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 7.6 | 5 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-9b | 480 | 3 | 5 | 7.6
LSIS27.01 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.1 - 0.16
LSIS27.02 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.16 - 0.25
LSIS27.03 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.25 - 0.4
LSIS27.04 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.4 - 0.63
LSIS27.05 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.63 - 1
LSIS27.06 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 1 - 1.6
LSIS27.07 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 1.6 - 2.5
LSIS27.08 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 2.5 - 4
LSIS27.09 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 4 - 6
LSIS27.10 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 5 - 8
LSIS27.11 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 6 - 9
LSIS27.12 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 7 - 10
LSIS28 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 11 | 7.5 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-12b | 480 | 3 | 5 | 11
LSIS28.01 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.1 - 0.16
LSIS28.02 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.16 - 0.25
LSIS28.03 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.25 - 0.4
LSIS28.04 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.4 - 0.63
LSIS28.05 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.63 - 1
LSIS28.06 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 1 - 1.6
LSIS28.07 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 1.6 - 2.5
LSIS28.08 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 2.5 - 4
LSIS28.09 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 4 - 6
LSIS28.10 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 5 - 8
LSIS28.11 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 6 - 9
LSIS28.12 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 7 - 10
LSIS28.13 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 9 - 13
LSIS29 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 14 | 10 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-18b | 480 | 3 | 5 | 14
LSIS29.01 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.1 - 0.16
LSIS29.02 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.16 - 0.25
LSIS29.03 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.25 - 0.4
LSIS29.04 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.4 - 0.63
LSIS29.05 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.63 - 1
LSIS29.06 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 1 - 1.6
LSIS29.07 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 1.6 - 2.5
LSIS29.08 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 2.5 - 4
LSIS29.09 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 4 - 6
LSIS29.10 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 5 - 8
LSIS29.11 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 6 - 9
LSIS29.12 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 7 - 10
LSIS29.13 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 9 - 13
LSIS29.14 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 12 - 18
LSIS30 | A [ version C1(a)] | FDS | ABB | OS60GJ12P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 21 | 15 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-22b | 480 | 3 | 5 | 21
LSIS30.01 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 12 - 18
LSIS30.02 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 16 - 22
LSIS30.03 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 18 - 25
LSIS31 | A [ version C1(a)] | FDS | ABB | OS60GJ12P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 27 | 20 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-32a | 480 | 3 | 5 | 27
LSIS31.01 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 12 - 18
LSIS31.02 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 16 - 22
LSIS31.03 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 18 - 25
LSIS31.04 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 22 - 32
LSIS32 | A [ version C1(a)] | FDS | ABB | OS100GJ03P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 40 | 30 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-40a | 480 | 3 | 5 | 40
LSIS32.01 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 22 - 32
LSIS32.02 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 28 - 40
LSIS33 | A [ version C1(a)] | FDS | ABB | OS100GJ03P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 52 | 40 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-50a | 480 | 3 | 5 | 52
LSIS33.01 |  | OLR | LSIS | MT-63 | 480 | 3 | 5 | 34 - 50
LSIS33.02 |  | OLR | LSIS | MT-63 | 480 | 3 | 5 | 45 - 65
LSIS34 | A [ version C1(a)] | FDS | ABB | OS200J03P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 65 | 50 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-65a | 480 | 3 | 5 | 65
LSIS34.01 |  | OLR | LSIS | MT-63 | 480 | 3 | 5 | 34 - 50
LSIS34.02 |  | OLR | LSIS | MT-63 | 480 | 3 | 5 | 45 - 65
LSIS35 | A [ version C1(a)] | FDS | ABB | OS200J03P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 65 | 50 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-75a | 480 | 3 | 5 | 65
LSIS35.01 |  | OLR | LSIS | MT-95 | 480 | 3 | 5 | 34 - 50
LSIS35.02 |  | OLR | LSIS | MT-95 | 480 | 3 | 5 | 45 - 65
LSIS35.03 |  | OLR | LSIS | MT-95 | 480 | 3 | 10 | 54 - 75
LSIS36 | A [ version C1(a)] | FDS | ABB | OS200J03P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 77 | 60 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-85a | 480 | 3 | 10 | 77
LSIS36.01 |  | OLR | LSIS | MT-95 | 480 | 3 | 5 | 34 - 50
LSIS36.02 |  | OLR | LSIS | MT-95 | 480 | 3 | 5 | 45 - 65
LSIS36.03 |  | OLR | LSIS | MT-95 | 480 | 3 | 10 | 54 - 75
LSIS36.04 |  | OLR | LSIS | MT-95 | 480 | 3 | 10 | 63 - 85
LSIS37 | A [ version C1(a)] | FDS | ABB | OS200J03P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 96 | 75 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-100a | 480 | 3 | 10 | 96
LSIS37.01 |  | OLR | LSIS | MT-95 | 480 | 3 | 5 | 34 - 50
LSIS37.02 |  | OLR | LSIS | MT-95 | 480 | 3 | 5 | 45 - 65
LSIS37.03 |  | OLR | LSIS | MT-95 | 480 | 3 | 10 | 54 - 75
LSIS37.04 |  | OLR | LSIS | MT-95 | 480 | 3 | 10 | 63 - 85
LSIS37.05 |  | OLR | LSIS | MT-95 | 480 | 3 | 10 | 70 - 95
LSIS37.06 |  | OLR | LSIS | MT-95 | 480 | 3 | 10 | 80 - 100
LSIS38 | A [ version C1(a)] | FDS | ABB | OS200J03P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 96 | 75 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-130a | 480 | 3 | 10 | 96
LSIS38.01 |  | OLR | LSIS | MT-150 | 480 | 3 | 5 | 34 - 50
LSIS38.02 |  | OLR | LSIS | MT-150 | 480 | 3 | 5 | 45 - 65
LSIS38.03 |  | OLR | LSIS | MT-150 | 480 | 3 | 10 | 54 - 75
LSIS38.04 |  | OLR | LSIS | MT-150 | 480 | 3 | 10 | 63 - 85
LSIS38.05 |  | OLR | LSIS | MT-150 | 480 | 3 | 10 | 80 - 105
LSIS39 | A [ version C1(a)] | FDS | ABB | OS200J03P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 124 | 100 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-150a | 480 | 3 | 10 | 124
LSIS39.01 |  | OLR | LSIS | MT-150 | 480 | 3 | 5 | 34 - 50
LSIS39.02 |  | OLR | LSIS | MT-150 | 480 | 3 | 5 | 45 - 65
LSIS39.03 |  | OLR | LSIS | MT-150 | 480 | 3 | 10 | 54 - 75
LSIS39.04 |  | OLR | LSIS | MT-150 | 480 | 3 | 10 | 63 - 85
LSIS39.05 |  | OLR | LSIS | MT-150 | 480 | 3 | 10 | 80 - 105
LSIS39.06 |  | OLR | LSIS | MT-150 | 480 | 3 | 10 | 95 - 130
LSIS40 | A [ version C1(a)] | FDS | ABB | OS400J03P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 156 | 125 | 11977 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-185a | 480 | 3 | 10 | 156
LSIS40.01 |  | OLR | LSIS | MT-225 | 480 | 3 | 5 | 65 ~ 100
LSIS40.02 |  | OLR | LSIS | MT-225 | 480 | 3 | 5 | 85 ~ 125
LSIS40.03 |  | OLR | LSIS | MT-225 | 480 | 3 | 10 | 100 ~ 160
LSIS41 | A [ version C1(a)] | FDS | ABB | OS400J03P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 180 | 150 | 11977 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-225a | 480 | 3 | 10 | 180
LSIS41.01 |  | OLR | LSIS | MT-225 | 480 | 3 | 5 | 65 ~ 100
LSIS41.02 |  | OLR | LSIS | MT-225 | 480 | 3 | 5 | 85 ~ 125
LSIS41.03 |  | OLR | LSIS | MT-225 | 480 | 3 | 10 | 100 ~ 160
LSIS41.04 |  | OLR | LSIS | MT-225 | 480 | 3 | 10 | 120 ~ 185
LSIS42 | A [ version C1(a)] | FDS | ABB | OS400J03P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 240 | 200 | 11977 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-265a | 480 | 3 | 10 | 240
LSIS42.01 |  | OLR | LSIS | MT-400 | 480 | 3 | 5 | 85 ~ 125
LSIS42.02 |  | OLR | LSIS | MT-400 | 480 | 3 | 10 | 100 ~ 160
LSIS42.03 |  | OLR | LSIS | MT-400 | 480 | 3 | 10 | 120 ~ 185
LSIS42.04 |  | OLR | LSIS | MT-400 | 480 | 3 | 10 | 160 ~ 240
LSIS43 | A [ version C1(a)] | FDS | ABB | OS600J03P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 302 | 250 | 11977 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-330a | 480 | 3 | 10 | 302
LSIS43.01 |  | OLR | LSIS | MT-400 | 480 | 3 | 10 | 160 ~ 240
LSIS43.02 |  | OLR | LSIS | MT-400 | 480 | 3 | 10 | 200 ~ 330
LSIS44 | A [ version C1(a)] | FDS | ABB | OS600J03P | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 361 | 300 | 27339 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-400a | 480 | 3 | 10 | 361
LSIS44.01 |  | OLR | LSIS | MT-400 | 480 | 3 | 10 | 160 ~ 240
LSIS44.02 |  | OLR | LSIS | MT-400 | 480 | 3 | 10 | 200 ~ 330
LSIS44.03 |  | OLR | LSIS | MT-400 | 480 | 3 | 10 | 260 ~ 400
LSIS45 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 9 | 7.5 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 200 | -
|  | MC | LSIS | MC-6a | 600 | 3 | 5 | 9
LSIS45.01 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.1 - 0.16
LSIS45.02 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.16 - 0.25
LSIS45.03 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.25 - 0.4
LSIS45.04 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.4 - 0.63
LSIS45.05 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.63 - 1
LSIS45.06 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1 - 1.6
LSIS45.07 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1.6 - 2.5
LSIS45.08 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 2.5 - 4
LSIS45.09 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 4 - 6
LSIS45.10 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 5 - 8
LSIS45.11 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 6 - 9
LSIS46 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 9 | 7.5 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 200 | -
|  | MC | LSIS | MC-9a | 600 | 3 | 5 | 9
LSIS46.01 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.1 - 0.16
LSIS46.02 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.16 - 0.25
LSIS46.03 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.25 - 0.4
LSIS46.04 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.4 - 0.63
LSIS46.05 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.63 - 1
LSIS46.06 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1 - 1.6
LSIS46.07 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1.6 - 2.5
LSIS46.08 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 2.5 - 4
LSIS46.09 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 4 - 6
LSIS46.10 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 5 - 8
LSIS46.11 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 6 - 9
LSIS47 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 11 | 10 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 200 | -
|  | MC | LSIS | MC-12a | 600 | 3 | 5 | 11
LSIS47.01 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.1 - 0.16
LSIS47.02 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.16 - 0.25
LSIS47.03 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.25 - 0.4
LSIS47.04 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.4 - 0.63
LSIS47.05 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.63 - 1
LSIS47.06 |  | OLR | LSIS | MT-12 | 600 | 3 | 1 | 1 - 1.6
LSIS47.07 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1.6 - 2.5
LSIS47.08 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 2.5 - 4
LSIS47.09 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 4 - 6
LSIS47.10 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 5 - 8
LSIS47.11 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 6 - 9
LSIS47.12 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 7 - 10
LSIS47.13 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 9 - 13
LSIS48 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 17 | 15 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 200 | -
|  | MC | LSIS | MC-18a | 600 | 3 | 5 | 17
LSIS48.01 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.1 - 0.16
LSIS48.02 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.16 - 0.25
LSIS48.03 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.25 - 0.4
LSIS48.04 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.4 - 0.63
LSIS48.05 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.63 - 1
LSIS48.06 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1 - 1.6
LSIS48.07 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1.6 - 2.5
LSIS48.08 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 2.5 - 4
LSIS48.09 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 4 - 6
LSIS48.10 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 5 - 8
LSIS48.11 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 6 - 9
LSIS48.12 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 7 - 10
LSIS48.13 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 9 - 13
LSIS48.14 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 12 - 18
LSIS49 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 9 | 7.5 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 200 | -
|  | MC | LSIS | MC-9b | 600 | 3 | 5 | 9
LSIS49.01 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.1 - 0.16
LSIS49.02 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.16 - 0.25
LSIS49.03 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.25 - 0.4
LSIS49.04 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.4 - 0.63
LSIS49.05 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.63 - 1
LSIS49.06 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 1 - 1.6
LSIS49.07 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 1.6 - 2.5
LSIS49.08 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 2.5 - 4
LSIS49.09 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 4 - 6
LSIS49.10 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 5 - 8
LSIS49.11 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 6 - 9
LSIS50 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 11 | 10 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 200 | -
|  | MC | LSIS | MC-12b | 600 | 3 | 5 | 11
LSIS50.01 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.1 - 0.16
LSIS50.02 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.16 - 0.25
LSIS50.03 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.25 - 0.4
LSIS50.04 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.4 - 0.63
LSIS50.05 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.63 - 1
LSIS50.06 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 1 - 1.6
LSIS50.07 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 1.6 - 2.5
LSIS50.08 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 2.5 - 4
LSIS50.09 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 4 - 6
LSIS50.10 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 5 - 8
LSIS50.11 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 6 - 9
LSIS50.12 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 7 - 10
LSIS50.13 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 9 - 13
LSIS51 | A [ version C1(a)] | FDS | ABB | OS30FAJ12P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 17 | 15 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 200 | -
|  | MC | LSIS | MC-18b | 600 | 3 | 5 | 17
LSIS51.01 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.1 - 0.16
LSIS51.02 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.16 - 0.25
LSIS51.03 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.25 - 0.4
LSIS51.04 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.4 - 0.63
LSIS51.05 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.63 - 1
LSIS51.06 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 1 - 1.6
LSIS51.07 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 1.6 - 2.5
LSIS51.08 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 2.5 - 4
LSIS51.09 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 4 - 6
LSIS51.10 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 5 - 8
LSIS51.11 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 6 - 9
LSIS51.12 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 7 - 10
LSIS51.13 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 9 - 13
LSIS51.14 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 12 - 18
LSIS52 | A [ version C1(a)] | FDS | ABB | OS60GJ12P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 22 | 20 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 200 | -
|  | MC | LSIS | MC-22b | 600 | 3 | 5 | 22
LSIS52.01 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 12 - 18
LSIS52.02 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 16 - 22
LSIS53 | A [ version C1(a)] | FDS | ABB | OS60GJ12P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 27 | 25 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 200 | -
|  | MC | LSIS | MC-32a | 600 | 3 | 5 | 27
LSIS53.01 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 12 - 18
LSIS53.02 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 16 - 22
LSIS53.03 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 18 - 25
LSIS53.04 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 22 - 32
LSIS54.01 | A [ version C1(a)] | FDS | ABB | OS100GJ03P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 32 | 30 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 200 | -
|  | MC | LSIS | MC-40a | 600 | 3 | 5 | 32
LSIS54.01 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 22 - 32
LSIS55 | A [ version C1(a)] | FDS | ABB | OS100GJ03P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 52 | 50 | 1712 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 200 | -
|  | MC | LSIS | MC-50a | 600 | 3 | 5 | 52
LSIS55.01 |  | OLR | LSIS | MT-63 | 600 | 3 | 5 | 24 - 36
LSIS55.02 |  | OLR | LSIS | MT-63 | 600 | 3 | 5 | 28 - 40
LSIS55.03 |  | OLR | LSIS | MT-63 | 600 | 3 | 5 | 34 - 50
LSIS55.04 |  | OLR | LSIS | MT-63 | 600 | 3 | 5 | 45 - 65
LSIS56 | A [ version C1(a)] | FDS | ABB | OS200J03P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 62 | 60 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 200 | -
|  | MC | LSIS | MC-65a | 600 | 3 | 10 | 62
LSIS56.01 |  | OLR | LSIS | MT-63 | 600 | 3 | 5 | 34 - 50
LSIS56.02 |  | OLR | LSIS | MT-63 | 600 | 3 | 10 | 45 - 65
LSIS57 | A [ version C1(a)] | FDS | ABB | OS200J03P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 62 | 60 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 200 | -
|  | MC | LSIS | MC-75a | 600 | 3 | 10 | 62
LSIS57.01 |  | OLR | LSIS | MT-95 | 600 | 3 | 5 | 34 - 50
LSIS57.02 |  | OLR | LSIS | MT-95 | 600 | 3 | 10 | 45 - 65
LSIS57.03 |  | OLR | LSIS | MT-95 | 600 | 3 | 10 | 54 - 75
LSIS58 | A [ version C1(a)] | FDS | ABB | OS200J03P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 77 | 75 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 200 | -
|  | MC | LSIS | MC-85a | 600 | 3 | 10 | 77
LSIS58.01 |  | OLR | LSIS | MT-95 | 600 | 3 | 5 | 34 - 50
LSIS58.02 |  | OLR | LSIS | MT-95 | 600 | 3 | 10 | 45 - 65
LSIS58.03 |  | OLR | LSIS | MT-95 | 600 | 3 | 10 | 54 - 75
LSIS58.04 |  | OLR | LSIS | MT-95 | 600 | 3 | 10 | 63 - 85
LSIS59 | A [ version C1(a)] | FDS | ABB | OS200J03P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 77 | 75 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 200 | -
|  | MC | LSIS | MC-100a | 600 | 3 | 10 | 77
LSIS59.01 |  | OLR | LSIS | MT-95 | 600 | 3 | 5 | 34 - 50
LSIS59.02 |  | OLR | LSIS | MT-95 | 600 | 3 | 10 | 45 - 65
LSIS59.03 |  | OLR | LSIS | MT-95 | 600 | 3 | 10 | 54 - 75
LSIS59.04 |  | OLR | LSIS | MT-95 | 600 | 3 | 10 | 63 - 85
LSIS60 | A [ version C1(a)] | FDS | ABB | OS200J03P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 77 | 75 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 200 | -
|  | MC | LSIS | MC-130a | 600 | 3 | 10 | 77
LSIS60.01 |  | OLR | LSIS | MT-150 | 600 | 3 | 5 | 34 - 50
LSIS60.02 |  | OLR | LSIS | MT-150 | 600 | 3 | 10 | 45 - 65
LSIS60.03 |  | OLR | LSIS | MT-150 | 600 | 3 | 10 | 54 - 75
LSIS60.04 |  | OLR | LSIS | MT-150 | 600 | 3 | 10 | 63 - 85
LSIS61 | A [ version C1(a)] | FDS | ABB | OS200J03P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 77 | 75 | 4312 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 200 | -
|  | MC | LSIS | MC-150a | 600 | 3 | 10 | 77
LSIS61.01 |  | OLR | LSIS | MT-150 | 600 | 3 | 5 | 34 - 50
LSIS61.02 |  | OLR | LSIS | MT-150 | 600 | 3 | 10 | 45 - 65
LSIS61.03 |  | OLR | LSIS | MT-150 | 600 | 3 | 10 | 54 - 75
LSIS61.04 |  | OLR | LSIS | MT-150 | 600 | 3 | 10 | 63 - 85
LSIS62 | A [ version C1(a)] | FDS | ABB | OS400J03P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 125 | 125 | 11977 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-185a | 600 | 3 | 10 | 125
LSIS62.01 |  | OLR | LSIS | MT-225 | 600 | 3 | 5 | 65 ~ 100
LSIS62.02 |  | OLR | LSIS | MT-225 | 600 | 3 | 5 | 85 ~ 125
LSIS63 | A [ version C1(a)] | FDS | ABB | OS400J03P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 144 | 150 | 11977 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-225a | 600 | 3 | 10 | 144
LSIS63.01 |  | OLR | LSIS | MT-225 | 600 | 3 | 5 | 65 ~ 100
LSIS63.02 |  | OLR | LSIS | MT-225 | 600 | 3 | 5 | 85 ~ 125
LSIS63.03 |  | OLR | LSIS | MT-225 | 600 | 3 | 10 | 100 ~ 160
LSIS64 | A [ version C1(a)] | FDS | ABB | OS400J03P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 192 | 200 | 11977 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-265a | 600 | 3 | 10 | 192
LSIS64.01 |  | OLR | LSIS | MT-400 | 600 | 3 | 5 | 85 ~ 125
LSIS64.02 |  | OLR | LSIS | MT-400 | 600 | 3 | 10 | 100 ~ 160
LSIS64.03 |  | OLR | LSIS | MT-400 | 600 | 3 | 10 | 120 ~ 185
LSIS64.04 |  | OLR | LSIS | MT-400 | 600 | 3 | 10 | 160 ~ 240
LSIS65 | A [ version C1(a)] | FDS | ABB | OS400J03P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 242 | 250 | 11977 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-330a | 600 | 3 | 10 | 242
LSIS65.01 |  | OLR | LSIS | MT-400 | 600 | 3 | 5 | 85 ~ 125
LSIS65.02 |  | OLR | LSIS | MT-400 | 600 | 3 | 10 | 100 ~ 160
LSIS65.03 |  | OLR | LSIS | MT-400 | 600 | 3 | 10 | 120 ~ 185
LSIS65.04 |  | OLR | LSIS | MT-400 | 600 | 3 | 10 | 160 ~ 240
LSIS65.05 |  | OLR | LSIS | MT-400 | 600 | 3 | 10 | 200 ~ 330
LSIS66 | A [ version C1(a)] | FDS | ABB | OS600J03P | 600 | 3 | 200 | - |  | 600 | 3 | 100 | 289 | 300 | 27339 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-400a | 600 | 3 | 10 | 289
LSIS66.01 |  | OLR | LSIS | MT-400 | 600 | 3 | 10 | 160 ~ 240
LSIS66.02 |  | OLR | LSIS | MT-400 | 600 | 3 | 10 | 200 ~ 330
LSIS1623 | A [ version C1(a)] | FDS | SOCOMEC | 38613004 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 7.5 | 2 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-6a | 240 | 3 | 5 | 9.6
LSIS1623.01 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1623.02 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1623.03 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1623.04 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1623.05 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.63 - 1
LSIS1623.06 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1 - 1.6
LSIS1623.07 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1623.08 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 2.5 - 4
LSIS1623.09 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 4 - 6
LSIS1623.10 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 5 - 8
LSIS1623.11 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 6 - 9
LSIS1623.12 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 7 - 10
LSIS1624 | A [ version C1(a)] | FDS | SOCOMEC | 38613004 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 7.5 | 2 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-9a | 240 | 3 | 5 | 9.6
LSIS1624.01 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1624.02 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1624.03 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1624.04 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1624.05 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.63 - 1
LSIS1624.06 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1 - 1.6
LSIS1624.07 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1624.08 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 2.5 - 4
LSIS1624.09 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 4 - 6
LSIS1624.10 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 5 - 8
LSIS1624.11 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 6 - 9
LSIS1624.12 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 7 - 10
LSIS1625 | A [ version C1(a)] | FDS | SOCOMEC | 38613004 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 10.6 | 3 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-12a | 240 | 3 | 5 | 15.2
LSIS1625.01 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1625.02 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1625.03 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1625.04 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1625.05 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.63 - 1
LSIS1625.06 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1 - 1.6
LSIS1625.07 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1625.08 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 2.5 - 4
LSIS1625.09 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 4 - 6
LSIS1625.10 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 5 - 8
LSIS1625.11 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 6 - 9
LSIS1625.12 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 7 - 10
LSIS1625.13 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 9 - 13
LSIS1625.14 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 12 - 18
LSIS1626 | A [ version C1(a)] | FDS | SOCOMEC | 38613004 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 18 | - | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-18a | 240 | 3 | 5 | 22
LSIS1626.01 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1626.02 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1626.03 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1626.04 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1626.05 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.63 - 1
LSIS1626.06 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1 - 1.6
LSIS1626.07 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1626.08 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 2.5 - 4
LSIS1626.09 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 4 - 6
LSIS1626.10 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 5 - 8
LSIS1626.11 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 6 - 9
LSIS1626.12 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 7 - 10
LSIS1626.13 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 9 - 13
LSIS1626.14 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 12 - 18
LSIS1627 | A [ version C1(a)] | FDS | SOCOMEC | 38613006 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 7.5 | 2 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-9b | 240 | 3 | 5 | 9.6
LSIS1627.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1627.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1627.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1627.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1627.05 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.63 - 1
LSIS1627.06 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1 - 1.6
LSIS1627.07 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1627.08 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 2.5 - 4
LSIS1627.09 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 4 - 6
LSIS1627.10 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 5 - 8
LSIS1627.11 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 6 - 9
LSIS1627.12 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 7 - 10
LSIS1628 | A [ version C1(a)] | FDS | SOCOMEC | 38613006 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 10.6 | 3 | 1493 | 1 , 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-12b | 240 | 3 | 5 | 15.2
LSIS1628.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1628.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1628.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1628.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1628.05 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.63 - 1
LSIS1628.06 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1 - 1.6
LSIS1628.07 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1628.08 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 2.5 - 4
LSIS1628.09 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 4 - 6
LSIS1628.10 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 5 - 8
LSIS1628.11 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 6 - 9
LSIS1628.12 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 7 - 10
LSIS1628.13 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 9 - 13
LSIS1628.14 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 12 - 18
LSIS1629 | A [ version C1(a)] | FDS | SOCOMEC | 38613006 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 22 | - | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-18b | 240 | 3 | 5 | 22
LSIS1629.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1629.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1629.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1629.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1629.05 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.63 - 1
LSIS1629.06 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1 - 1.6
LSIS1629.07 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1629.08 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 2.5 - 4
LSIS1629.09 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 4 - 6
LSIS1629.10 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 5 - 8
LSIS1629.11 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 6 - 9
LSIS1629.12 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 7 - 10
LSIS1629.13 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 9 - 13
LSIS1629.14 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 12 - 18
LSIS1629.15 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 16 - 22
LSIS1630 | A [ version C1(a)] | FDS | SOCOMEC | 38613006 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 24.2 | 7.5 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-22b | 240 | 3 | 5 | 28
LSIS1630.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 12 - 18
LSIS1630.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 16 - 22
LSIS1630.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 18 - 25
LSIS1630.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 22 - 32
LSIS1631 | A [ version C1(a)] | FDS | SOCOMEC | 38613010 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 24.2 | 7.5 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-32a | 240 | 3 | 5 | 28
LSIS1631.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 12 - 18
LSIS1631.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 16 - 22
LSIS1631.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 18 - 25
LSIS1631.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 22 - 32
LSIS1631 | A [ version C1(a)] | FDS | SOCOMEC | 38613010 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 40 | - | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-40a | 240 | 3 | 5 | 42
LSIS1631.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 22 - 32
LSIS1631.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 28 - 40
LSIS1632 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 59.4 | 20 | 2667 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-50a | 240 | 3 | 5 | 68
LSIS1632.01 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 24 - 36
LSIS1632.02 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 28 - 40
LSIS1632.03 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 34 - 50
LSIS1632.04 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 45 - 65
LSIS1633 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 65 | - | 2667 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-65a | 240 | 3 | 5 | 80
LSIS1633.01 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 34 - 50
LSIS1633.02 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 45 - 65
LSIS1634 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 74.8 | 25 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-75a | 240 | 3 | 5 | 80
LSIS1634.01 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 34 - 50
LSIS1634.02 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 45 - 65
LSIS1634.03 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 54 - 75
LSIS1634.04 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 63 - 85
LSIS1634.05 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 70 - 95
LSIS1635 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 88 | 30 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-85a | 240 | 3 | 5 | 104
LSIS1635.01 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 34 - 50
LSIS1635.02 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 45 - 65
LSIS1635.03 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 54 - 75
LSIS1635.04 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 63 - 85
LSIS1635.05 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 70 - 95
LSIS1635.06 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 80 - 100
LSIS1637 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 88 | 30 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-100a | 240 | 3 | 5 | 104
LSIS1637.01 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 34 - 50
LSIS1637.02 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 45 - 65
LSIS1637.03 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 54 - 75
LSIS1637.04 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 63 - 85
LSIS1637.05 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 70 - 95
LSIS1637.06 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 80 - 100
LSIS1638 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 104 | - | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-130a | 240 | 3 | 5 | 104
LSIS1638.01 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 34 - 50
LSIS1638.02 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 45 - 65
LSIS1638.03 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 54 - 75
LSIS1638.04 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 63 - 85
LSIS1638.05 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 80 - 105
LSIS1639 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 114 | 40 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-150a | 240 | 3 | 10 | 130
LSIS1639.01 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 34 - 50
LSIS1639.02 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 45 - 65
LSIS1639.03 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 54 - 75
LSIS1639.04 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 63 - 85
LSIS1639.05 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 80 - 105
LSIS1639.06 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 95 - 130
LSIS1640 | A [ version C1(a)] | FDS | SOCOMEC | 38513038 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 154 | - | 9764 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-185a | 240 | 3 | 10 | 154
LSIS1640.01 |  | OLR | LSIS | MT-225 | 240 | 3 | 5 | 65 ~ 100
LSIS1640.02 |  | OLR | LSIS | MT-225 | 240 | 3 | 5 | 85 ~ 125
LSIS1640.03 |  | OLR | LSIS | MT-225 | 240 | 3 | 10 | 100 ~ 160
LSIS1641 | A [ version C1(a)] | FDS | SOCOMEC | 38513038 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 169 | 60 | 9764 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-225a | 240 | 3 | 10 | 192
LSIS1641.01 |  | OLR | LSIS | MT-225 | 240 | 3 | 5 | 65 ~ 100
LSIS1641.02 |  | OLR | LSIS | MT-225 | 240 | 3 | 5 | 85 ~ 125
LSIS1641.03 |  | OLR | LSIS | MT-225 | 240 | 3 | 10 | 100 ~ 160
LSIS1641.04 |  | OLR | LSIS | MT-225 | 240 | 3 | 10 | 120 ~ 185
LSIS1641.05 |  | OLR | LSIS | MT-225 | 240 | 3 | 10 | 160 ~ 240
LSIS1642 | A [ version C1(a)] | FDS | SOCOMEC | 38503060 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 211 | 75 | 27339 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-265a | 240 | 3 | 10 | 248
LSIS1642.01 |  | OLR | LSIS | MT-400 | 240 | 3 | 5 | 85 ~ 125
LSIS1642.02 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 100 ~ 160
LSIS1642.03 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 120 ~ 185
LSIS1642.04 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 160 ~ 240
LSIS1643 | A [ version C1(a)] | FDS | SOCOMEC | 38503060 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 273 | 100 | 27339 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-330a | 240 | 3 | 10 | 312
LSIS1643.01 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 160 ~ 240
LSIS1643.02 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 200 ~ 330
LSIS1644 | A [ version C1(a)] | FDS | SOCOMEC | 38503060 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 343 | 125 | 27339 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-400a | 240 | 3 | 10 | 360
LSIS1644.01 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 160 ~ 240
LSIS1644.02 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 200 ~ 330
LSIS1644.03 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 260 ~ 400
LSIS1645 | A [ version C1(a)] | FDS | SOCOMEC | 38503060 | 240 | 3 | 200 | - |  | 208 | 3 | 200 | 396 | 150 | 27339 | 1,3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-500a | 240 | 3 | 10 | 480
LSIS1645.01 |  | OLR | LSIS | MT-800 | 240 | 3 | 10 | 200~300
LSIS1645.02 |  | OLR | LSIS | MT-800 | 240 | 3 | 10 | 260~400
LSIS1645.03 |  | OLR | LSIS | MT-800 | 240 | 3 | 10 | 400~600
LSIS1646 | A [ version C1(a)] | FDS | SOCOMEC | 38503080 | 240 | 3 | 200 |  |  | 208 | 3 | 200 | 528 | 200 | 27339 | 1,3
|  | F | Any | Class L Time Delay Fuse |  |  | 200
|  | MC | LSIS | MC-630a | 240 | 3 | 18 | 604
LSIS1646.01 |  | OLR | LSIS | MT-800 | 240 | 3 | 10 | 200~300
LSIS1646.02 |  | OLR | LSIS | MT-800 | 240 | 3 | 10 | 260~400
LSIS1646.03 |  | OLR | LSIS | MT-800 | 240 | 3 | 18 | 400~600
LSIS1646.04 |  | OLR | LSIS | MT-800 | 240 | 3 | 18 | 520~800
LSIS1647 | A [ version C1(a)] | FDS | SOCOMEC | 38503080 | 240 | 3 | 200 |  |  | 208 | 3 | 200 | 528 | 200 | 27339 | 1,3
|  | F | Any | Class L Time Delay Fuse |  |  | 200
|  | MC | LSIS | MC-800a | 240 | 3 | 18 | 722
LSIS1647.01 |  | OLR | LSIS | MT-800 | 240 | 3 | 10 | 200~300
LSIS1647.02 |  | OLR | LSIS | MT-800 | 240 | 3 | 10 | 260~400
LSIS1647.03 |  | OLR | LSIS | MT-800 | 240 | 3 | 18 | 400~600
LSIS1647.04 |  | OLR | LSIS | MT-800 | 240 | 3 | 18 | 520~800
LSIS1501 | A [ version C1(a)] | FDS | SOCOMEC | 38613004 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 9.6 | 3 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-6a | 240 | 3 | 5 | 9.6
LSIS1501.01 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1501.02 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1501.03 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1501.04 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1501.05 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.63 - 1
LSIS1501.06 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1 - 1.6
LSIS1501.07 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1501.08 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 2.5 - 4
LSIS1501.09 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 4 - 6
LSIS1501.10 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 5 - 8
LSIS1501.11 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 6 - 9
LSIS1501.12 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 7 - 10
LSIS1502 | A [ version C1(a)] | FDS | SOCOMEC | 38613004 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 9.6 | 3 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-9a | 240 | 3 | 5 | 9.6
LSIS1502.01 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1502.02 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1502.03 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1502.04 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1502.05 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.63 - 1
LSIS1502.06 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1 - 1.6
LSIS1502.07 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1502.08 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 2.5 - 4
LSIS1502.09 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 4 - 6
LSIS1502.10 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 5 - 8
LSIS1502.11 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 6 - 9
LSIS1502.12 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 7 - 10
LSIS1503 | A [ version C1(a)] | FDS | SOCOMEC | 38613004 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 15.2 | 5 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-12a | 240 | 3 | 5 | 15.2
LSIS1503.01 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1503.02 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1503.03 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1503.04 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1503.05 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.63 - 1
LSIS1503.06 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1 - 1.6
LSIS1503.07 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1503.08 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 2.5 - 4
LSIS1503.09 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 4 - 6
LSIS1503.10 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 5 - 8
LSIS1503.11 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 6 - 9
LSIS1503.12 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 7 - 10
LSIS1503.13 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 9 - 13
LSIS1503.14 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 12 - 18
LSIS1504 | A [ version C1(a)] | FDS | SOCOMEC | 38613004 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 18 | 7.5 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-18a | 240 | 3 | 5 | 22
LSIS1504.01 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1504.02 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1504.03 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1504.04 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1504.05 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 0.63 - 1
LSIS1504.06 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1 - 1.6
LSIS1504.07 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1504.08 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 2.5 - 4
LSIS1504.09 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 4 - 6
LSIS1504.10 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 5 - 8
LSIS1504.11 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 6 - 9
LSIS1504.12 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 7 - 10
LSIS1504.13 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 9 - 13
LSIS1504.14 |  | OLR | LSIS | MT-12 | 240 | 3 | 5 | 12 - 18
LSIS1505 | A [ version C1(a)] | FDS | SOCOMEC | 38613006 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 9.6 | 3 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-9b | 240 | 3 | 5 | 9.6
LSIS1505.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1505.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1505.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1505.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1505.05 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.63 - 1
LSIS1505.06 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1 - 1.6
LSIS1505.07 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1505.08 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 2.5 - 4
LSIS1505.09 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 4 - 6
LSIS1505.10 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 5 - 8
LSIS1505.11 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 6 - 9
LSIS1505.12 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 7 - 10
LSIS1506 | A [ version C1(a)] | FDS | SOCOMEC | 38613006 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 15.2 | 5 | 1493 | 1 , 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-12b | 240 | 3 | 5 | 15.2
LSIS1506.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1506.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1506.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1506.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1506.05 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.63 - 1
LSIS1506.06 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1 - 1.6
LSIS1506.07 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1506.08 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 2.5 - 4
LSIS1506.09 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 4 - 6
LSIS1506.10 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 5 - 8
LSIS1506.11 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 6 - 9
LSIS1506.12 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 7 - 10
LSIS1506.13 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 9 - 13
LSIS1506.14 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 12 - 18
LSIS1507 | A [ version C1(a)] | FDS | SOCOMEC | 38613006 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 22 | 7.5 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-18b | 240 | 3 | 5 | 22
LSIS1507.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.1 - 0.16
LSIS1507.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.16 - 0.25
LSIS1507.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.25 - 0.4
LSIS1507.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.4 - 0.63
LSIS1507.05 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 0.63 - 1
LSIS1507.06 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1 - 1.6
LSIS1507.07 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 1.6 - 2.5
LSIS1507.08 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 2.5 - 4
LSIS1507.09 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 4 - 6
LSIS1507.10 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 5 - 8
LSIS1507.11 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 6 - 9
LSIS1507.12 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 7 - 10
LSIS1507.13 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 9 - 13
LSIS1507.14 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 12 - 18
LSIS1507.15 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 16 - 22
LSIS1508 | A [ version C1(a)] | FDS | SOCOMEC | 38613006 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 28 | 10 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-22b | 240 | 3 | 5 | 28
LSIS1508.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 12 - 18
LSIS1508.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 16 - 22
LSIS1508.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 18 - 25
LSIS1508.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 22 - 32
LSIS1509 | A [ version C1(a)] | FDS | SOCOMEC | 38613010 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 28 | 10 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-32a | 240 | 3 | 5 | 28
LSIS1509.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 12 - 18
LSIS1509.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 16 - 22
LSIS1509.03 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 18 - 25
LSIS1509.04 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 22 - 32
LSIS1510 | A [ version C1(a)] | FDS | SOCOMEC | 38613010 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 40 | 15 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-40a | 240 | 3 | 5 | 42
LSIS1510.01 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 22 - 32
LSIS1510.02 |  | OLR | LSIS | MT-32 | 240 | 3 | 5 | 28 - 40
LSIS1511 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 65 | 25 | 2667 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-50a | 240 | 3 | 5 | 68
LSIS1511.01 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 24 - 36
LSIS1511.02 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 28 - 40
LSIS1511.03 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 34 - 50
LSIS1511.04 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 45 - 65
LSIS1512 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 65 | 30 | 2667 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-65a | 240 | 3 | 5 | 80
LSIS1512.01 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 34 - 50
LSIS1512.02 |  | OLR | LSIS | MT-63 | 240 | 3 | 5 | 45 - 65
LSIS1513 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 80 | 30 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-75a | 240 | 3 | 5 | 80
LSIS1513.01 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 34 - 50
LSIS1513.02 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 45 - 65
LSIS1513.03 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 54 - 75
LSIS1513.04 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 63 - 85
LSIS1513.05 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 70 - 95
LSIS1514 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 100 | 40 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-85a | 240 | 3 | 5 | 104
LSIS1514.01 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 34 - 50
LSIS1514.02 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 45 - 65
LSIS1514.03 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 54 - 75
LSIS1514.04 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 63 - 85
LSIS1514.05 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 70 - 95
LSIS1514.06 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 80 - 100
LSIS1515 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 100 | 40 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-100a | 240 | 3 | 5 | 104
LSIS1515.01 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 34 - 50
LSIS1515.02 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 45 - 65
LSIS1515.03 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 54 - 75
LSIS1515.04 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 63 - 85
LSIS1515.05 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 70 - 95
LSIS1515.06 |  | OLR | LSIS | MT-95 | 240 | 3 | 5 | 80 - 100
LSIS1516 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 104 | 40 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-130a | 240 | 3 | 5 | 104
LSIS1516.01 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 34 - 50
LSIS1516.02 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 45 - 65
LSIS1516.03 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 54 - 75
LSIS1516.04 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 63 - 85
LSIS1516.05 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 80 - 105
LSIS1517 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 130 | 50 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-150a | 240 | 3 | 10 | 130
LSIS1517.01 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 34 - 50
LSIS1517.02 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 45 - 65
LSIS1517.03 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 54 - 75
LSIS1517.04 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 63 - 85
LSIS1517.05 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 80 - 105
LSIS1517.06 |  | OLR | LSIS | MT-150 | 240 | 3 | 5 | 95 - 130
LSIS1518 | A [ version C1(a)] | FDS | SOCOMEC | 38513038 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 154 | 60 | 9764 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-185a | 240 | 3 | 10 | 154
LSIS1518.01 |  | OLR | LSIS | MT-225 | 240 | 3 | 5 | 65 ~ 100
LSIS1518.02 |  | OLR | LSIS | MT-225 | 240 | 3 | 5 | 85 ~ 125
LSIS1518.03 |  | OLR | LSIS | MT-225 | 240 | 3 | 10 | 100 ~ 160
LSIS1519 | A [ version C1(a)] | FDS | SOCOMEC | 38513038 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 192 | 75 | 9764 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-225a | 240 | 3 | 10 | 192
LSIS1519.01 |  | OLR | LSIS | MT-225 | 240 | 3 | 5 | 65 ~ 100
LSIS1519.02 |  | OLR | LSIS | MT-225 | 240 | 3 | 5 | 85 ~ 125
LSIS1519.03 |  | OLR | LSIS | MT-225 | 240 | 3 | 10 | 100 ~ 160
LSIS1519.04 |  | OLR | LSIS | MT-225 | 240 | 3 | 10 | 120 ~ 185
LSIS1519.05 |  | OLR | LSIS | MT-225 | 240 | 3 | 10 | 160 ~ 240
LSIS1520 | A [ version C1(a)] | FDS | SOCOMEC | 38503060 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 240 | 100 | 27339 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-265a | 240 | 3 | 10 | 248
LSIS1520.01 |  | OLR | LSIS | MT-400 | 240 | 3 | 5 | 85 ~ 125
LSIS1520.02 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 100 ~ 160
LSIS1520.03 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 120 ~ 185
LSIS1520.04 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 160 ~ 240
LSIS1521 | A [ version C1(a)] | FDS | SOCOMEC | 38503060 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 312 | 125 | 27339 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-330a | 240 | 3 | 10 | 312
LSIS1521.01 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 160 ~ 240
LSIS1521.02 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 200 ~ 330
LSIS1522 | A [ version C1(a)] | FDS | SOCOMEC | 38503060 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 360 | 150 | 27339 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-400a | 240 | 3 | 10 | 360
LSIS1522.01 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 160 ~ 240
LSIS1522.02 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 200 ~ 330
LSIS1522.03 |  | OLR | LSIS | MT-400 | 240 | 3 | 10 | 260 ~ 400
LSIS1523 | A [ version C1(a)] | FDS | SOCOMEC | 38503060 | 240 | 3 | 200 | - |  | 240 | 3 | 200 | 480 | 200 | 27339 | 1,3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-500a | 240 | 3 | 10 | 480
LSIS1523.01 |  | OLR | LSIS | MT-800 | 240 | 3 | 10 | 200~300
LSIS1523.02 |  | OLR | LSIS | MT-800 | 240 | 3 | 10 | 260~400
LSIS1523.03 |  | OLR | LSIS | MT-800 | 240 | 3 | 10 | 400~600
LSIS1524 | A [ version C1(a)] | FDS | SOCOMEC | 38503080 | 240 | 3 | 200 |  |  | 240 | 3 | 200 | 604 | 250 | 27339 | 1,3
|  | F | Any | Class L Time Delay Fuse |  |  | 200
|  | MC | LSIS | MC-630a | 240 | 3 | 18 | 604
LSIS1524.01 |  | OLR | LSIS | MT-800 | 240 | 3 | 10 | 200~300
LSIS1524.02 |  | OLR | LSIS | MT-800 | 240 | 3 | 10 | 260~400
LSIS1524.03 |  | OLR | LSIS | MT-800 | 240 | 3 | 18 | 400~600
LSIS1524.03 |  | OLR | LSIS | MT-800 | 240 | 3 | 18 | 520~800
LSIS1525 | A [ version C1(a)] | FDS | SOCOMEC | 38503080 | 240 | 3 | 200 |  |  | 240 | 3 | 200 | 722 | 300 | 27339 | 1,3
|  | F | Any | Class L Time Delay Fuse |  |  | 200
|  | MC | LSIS | MC-800a | 240 | 3 | 18 | 722
LSIS1525.01 |  | OLR | LSIS | MT-800 | 240 | 3 | 10 | 200~300
LSIS1525.02 |  | OLR | LSIS | MT-800 | 240 | 3 | 10 | 260~400
LSIS1525.03 |  | OLR | LSIS | MT-800 | 240 | 3 | 18 | 400~600
LSIS1525.03 |  | OLR | LSIS | MT-800 | 240 | 3 | 18 | 520~800
LSIS1526 | A [ version C1(a)] | FDS | SOCOMEC | 38613004 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 7.6 | 5 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-6a | 480 | 3 | 5 | 7.6
LSIS1526.01 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.1 - 0.16
LSIS1526.02 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.16 - 0.25
LSIS1526.03 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.25 - 0.4
LSIS1526.04 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.4 - 0.63
LSIS1526.05 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.63 - 1
LSIS1526.06 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 1 - 1.6
LSIS1526.07 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 1.6 - 2.5
LSIS1526.08 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 2.5 - 4
LSIS1526.09 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 4 - 6
LSIS1526.10 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 5 - 8
LSIS1526.11 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 6 - 9
LSIS1526.12 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 7 - 10
LSIS1527 | A [ version C1(a)] | FDS | SOCOMEC | 38613004 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 7.6 | 5 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-9a | 480 | 3 | 5 | 7.6
LSIS1527.01 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.1 - 0.16
LSIS1527.02 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.16 - 0.25
LSIS1527.03 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.25 - 0.4
LSIS1527.04 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.4 - 0.63
LSIS1527.05 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.63 - 1
LSIS1527.06 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 1 - 1.6
LSIS1527.07 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 1.6 - 2.5
LSIS1527.08 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 2.5 - 4
LSIS1527.09 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 4 - 6
LSIS1527.10 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 5 - 8
LSIS1527.11 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 6 - 9
LSIS1527.12 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 7 - 10
LSIS1528 | A [ version C1(a)] | FDS | SOCOMEC | 38613004 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 11 | 7.5 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-12a | 480 | 3 | 5 | 11
LSIS1528.01 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.1 - 0.16
LSIS1528.02 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.16 - 0.25
LSIS1528.03 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.25 - 0.4
LSIS1528.04 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.4 - 0.63
LSIS1528.05 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.63 - 1
LSIS1528.06 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 1 - 1.6
LSIS1528.07 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 1.6 - 2.5
LSIS1528.08 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 2.5 - 4
LSIS1528.09 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 4 - 6
LSIS1528.10 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 5 - 8
LSIS1528.11 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 6 - 9
LSIS1528.12 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 7 - 10
LSIS1528.13 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 9 - 13
LSIS1529 | A [ version C1(a)] | FDS | SOCOMEC | 38613004 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 14 | 10 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-18a | 480 | 3 | 5 | 14
LSIS1529.01 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.1 - 0.16
LSIS1529.02 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.16 - 0.25
LSIS1529.03 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.25 - 0.4
LSIS1529.04 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.4 - 0.63
LSIS1529.05 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 0.63 - 1
LSIS1529.06 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 1 - 1.6
LSIS1529.07 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 1.6 - 2.5
LSIS1529.08 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 2.5 - 4
LSIS1529.09 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 4 - 6
LSIS1529.10 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 5 - 8
LSIS1529.11 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 6 - 9
LSIS1529.12 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 7 - 10
LSIS1529.13 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 9 - 13
LSIS1529.14 |  | OLR | LSIS | MT-12 | 480 | 3 | 5 | 12 - 18
LSIS1530 | A [ version C1(a)] | FDS | SOCOMEC | 38613006 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 7.6 | 5 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-9b | 480 | 3 | 5 | 7.6
LSIS1530.01 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.1 - 0.16
LSIS1530.02 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.16 - 0.25
LSIS1530.03 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.25 - 0.4
LSIS1530.04 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.4 - 0.63
LSIS1530.05 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.63 - 1
LSIS1530.06 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 1 - 1.6
LSIS1530.07 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 1.6 - 2.5
LSIS1530.08 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 2.5 - 4
LSIS1530.09 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 4 - 6
LSIS1530.10 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 5 - 8
LSIS1530.11 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 6 - 9
LSIS1530.12 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 7 - 10
LSIS1531 | A [ version C1(a)] | FDS | SOCOMEC | 38613006 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 11 | 7.5 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-12b | 480 | 3 | 5 | 11
LSIS1531.01 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.1 - 0.16
LSIS1531.02 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.16 - 0.25
LSIS1531.03 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.25 - 0.4
LSIS1531.04 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.4 - 0.63
LSIS1531.05 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.63 - 1
LSIS1531.06 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 1 - 1.6
LSIS1531.07 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 1.6 - 2.5
LSIS1531.08 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 2.5 - 4
LSIS1531.09 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 4 - 6
LSIS1531.10 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 5 - 8
LSIS1531.11 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 6 - 9
LSIS1531.12 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 7 - 10
LSIS1531.13 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 9 - 13
LSIS1532 | A [ version C1(a)] | FDS | SOCOMEC | 38613006 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 14 | 10 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-18b | 480 | 3 | 5 | 14
LSIS1532.01 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.1 - 0.16
LSIS1532.02 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.16 - 0.25
LSIS1532.03 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.25 - 0.4
LSIS1532.04 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.4 - 0.63
LSIS1532.05 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 0.63 - 1
LSIS1532.06 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 1 - 1.6
LSIS1532.07 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 1.6 - 2.5
LSIS1532.08 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 2.5 - 4
LSIS1532.09 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 4 - 6
LSIS1532.10 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 5 - 8
LSIS1532.11 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 6 - 9
LSIS1532.12 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 7 - 10
LSIS1532.13 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 9 - 13
LSIS1532.14 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 12 - 18
LSIS1533 | A [ version C1(a)] | FDS | SOCOMEC | 38613006 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 21 | 15 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-22b | 480 | 3 | 5 | 21
LSIS1533.01 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 12 - 18
LSIS1533.02 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 16 - 22
LSIS1533.03 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 18 - 25
LSIS1534 | A [ version C1(a)] | FDS | SOCOMEC | 38613010 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 27 | 20 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-32a | 480 | 3 | 5 | 27
LSIS1534.01 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 12 - 18
LSIS1534.02 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 16 - 22
LSIS1534.03 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 18 - 25
LSIS1534.04 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 22 - 32
LSIS1535 | A [ version C1(a)] | FDS | SOCOMEC | 38613010 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 40 | 30 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-40a | 480 | 3 | 5 | 40
LSIS1535.01 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 22 - 32
LSIS1535.02 |  | OLR | LSIS | MT-32 | 480 | 3 | 5 | 28 - 40
LSIS1536 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 52 | 40 | 2667 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-50a | 480 | 3 | 5 | 52
LSIS1536.01 |  | OLR | LSIS | MT-63 | 480 | 3 | 5 | 34 - 50
LSIS1536.02 |  | OLR | LSIS | MT-63 | 480 | 3 | 5 | 45 - 65
LSIS1537 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 65 | 50 | 2667 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-65a | 480 | 3 | 5 | 65
LSIS1537.01 |  | OLR | LSIS | MT-63 | 480 | 3 | 5 | 34 - 50
LSIS1537.02 |  | OLR | LSIS | MT-63 | 480 | 3 | 5 | 45 - 65
LSIS1538 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 65 | 50 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-75a | 480 | 3 | 5 | 65
LSIS1538.01 |  | OLR | LSIS | MT-95 | 480 | 3 | 5 | 34 - 50
LSIS1538.02 |  | OLR | LSIS | MT-95 | 480 | 3 | 5 | 45 - 65
LSIS1538.03 |  | OLR | LSIS | MT-95 | 480 | 3 | 10 | 54 - 75
LSIS1539 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 77 | 60 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-85a | 480 | 3 | 10 | 77
LSIS1539.01 |  | OLR | LSIS | MT-95 | 480 | 3 | 5 | 34 - 50
LSIS1539.02 |  | OLR | LSIS | MT-95 | 480 | 3 | 5 | 45 - 65
LSIS1539.03 |  | OLR | LSIS | MT-95 | 480 | 3 | 10 | 54 - 75
LSIS1539.04 |  | OLR | LSIS | MT-95 | 480 | 3 | 10 | 63 - 85
LSIS1540 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 96 | 75 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-100a | 480 | 3 | 10 | 96
LSIS1540.01 |  | OLR | LSIS | MT-95 | 480 | 3 | 5 | 34 - 50
LSIS1540.02 |  | OLR | LSIS | MT-95 | 480 | 3 | 5 | 45 - 65
LSIS1540.03 |  | OLR | LSIS | MT-95 | 480 | 3 | 10 | 54 - 75
LSIS1540.04 |  | OLR | LSIS | MT-95 | 480 | 3 | 10 | 63 - 85
LSIS1540.05 |  | OLR | LSIS | MT-95 | 480 | 3 | 10 | 70 - 95
LSIS1540.06 |  | OLR | LSIS | MT-95 | 480 | 3 | 10 | 80 - 100
LSIS1541 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 96 | 75 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-130a | 480 | 3 | 10 | 96
LSIS1541.01 |  | OLR | LSIS | MT-150 | 480 | 3 | 5 | 34 - 50
LSIS1541.02 |  | OLR | LSIS | MT-150 | 480 | 3 | 5 | 45 - 65
LSIS1541.03 |  | OLR | LSIS | MT-150 | 480 | 3 | 10 | 54 - 75
LSIS1541.04 |  | OLR | LSIS | MT-150 | 480 | 3 | 10 | 63 - 85
LSIS1541.05 |  | OLR | LSIS | MT-150 | 480 | 3 | 10 | 80 - 105
LSIS1542 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 124 | 100 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 480 | - | 200 | -
|  | MC | LSIS | MC-150a | 480 | 3 | 10 | 124
LSIS1542.01 |  | OLR | LSIS | MT-150 | 480 | 3 | 5 | 34 - 50
LSIS1542.02 |  | OLR | LSIS | MT-150 | 480 | 3 | 5 | 45 - 65
LSIS1542.03 |  | OLR | LSIS | MT-150 | 480 | 3 | 10 | 54 - 75
LSIS1542.04 |  | OLR | LSIS | MT-150 | 480 | 3 | 10 | 63 - 85
LSIS1542.05 |  | OLR | LSIS | MT-150 | 480 | 3 | 10 | 80 - 105
LSIS1542.06 |  | OLR | LSIS | MT-150 | 480 | 3 | 10 | 95 - 130
LSIS1543 | A [ version C1(a)] | FDS | SOCOMEC | 38513038 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 156 | 125 | 9764 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-185a | 480 | 3 | 10 | 156
LSIS1543.01 |  | OLR | LSIS | MT-225 | 480 | 3 | 5 | 65 ~ 100
LSIS1543.02 |  | OLR | LSIS | MT-225 | 480 | 3 | 5 | 85 ~ 125
LSIS1543.03 |  | OLR | LSIS | MT-225 | 480 | 3 | 10 | 100 ~ 160
LSIS1544 | A [ version C1(a)] | FDS | SOCOMEC | 38513038 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 180 | 150 | 9764 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-225a | 480 | 3 | 10 | 180
LSIS1544.01 |  | OLR | LSIS | MT-225 | 480 | 3 | 5 | 65 ~ 100
LSIS1544.02 |  | OLR | LSIS | MT-225 | 480 | 3 | 5 | 85 ~ 125
LSIS1544.03 |  | OLR | LSIS | MT-225 | 480 | 3 | 10 | 100 ~ 160
LSIS1544.04 |  | OLR | LSIS | MT-225 | 480 | 3 | 10 | 120 ~ 185
LSIS1545 | A [ version C1(a)] | FDS | SOCOMEC | 38503060 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 240 | 200 | 27339 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-265a | 480 | 3 | 10 | 240
LSIS1545.01 |  | OLR | LSIS | MT-400 | 480 | 3 | 5 | 85 ~ 125
LSIS1545.02 |  | OLR | LSIS | MT-400 | 480 | 3 | 10 | 100 ~ 160
LSIS1545.03 |  | OLR | LSIS | MT-400 | 480 | 3 | 10 | 120 ~ 185
LSIS1545.04 |  | OLR | LSIS | MT-400 | 480 | 3 | 10 | 160 ~ 240
LSIS1546 | A [ version C1(a)] | FDS | SOCOMEC | 38503060 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 302 | 250 | 27339 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-330a | 480 | 3 | 10 | 302
LSIS1546.01 |  | OLR | LSIS | MT-400 | 480 | 3 | 10 | 160 ~ 240
LSIS1546.02 |  | OLR | LSIS | MT-400 | 480 | 3 | 10 | 200 ~ 330
LSIS1547 | A [ version C1(a)] | FDS | SOCOMEC | 38503060 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 361 | 300 | 27339 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-400a | 480 | 3 | 10 | 361
LSIS1547.01 |  | OLR | LSIS | MT-400 | 480 | 3 | 10 | 160 ~ 240
LSIS1547.02 |  | OLR | LSIS | MT-400 | 480 | 3 | 10 | 200 ~ 330
LSIS1547.03 |  | OLR | LSIS | MT-400 | 480 | 3 | 10 | 260 ~ 400
LSIS1548 | A [ version C1(a)] | FDS | SOCOMEC | 38503060 | 480 | 3 | 200 | - |  | 480 | 3 | 200 | 477 | 400 | 27339 | 1,3
|  | F | Any | Class J Time Delay Fuse |  |  | 200 | -
|  | MC | LSIS | MC-500a | 480 | 3 | 18 | 477
LSIS1548.01 |  | OLR | LSIS | MT-800 | 480 | 3 | 10 | 200~300
LSIS1548.02 |  | OLR | LSIS | MT-800 | 480 | 3 | 18 | 260~400
LSIS1548.03 |  | OLR | LSIS | MT-800 | 480 | 3 | 18 | 400~600
LSIS1549 | A [ version C1(a)] | FDS | SOCOMEC | 38503080 | 480 | 3 | 200 |  |  | 480 | 3 | 200 | 590 | 500 | 27339 | 1,3
|  | F | Any | Class L Time Delay Fuse |  |  | 200
|  | MC | LSIS | MC-630a | 480 | 3 | 30 | 590
LSIS1549.01 |  | OLR | LSIS | MT-800 | 480 | 3 | 10 | 200~300
LSIS1549.02 |  | OLR | LSIS | MT-800 | 480 | 3 | 18 | 260~400
LSIS1549.03 |  | OLR | LSIS | MT-800 | 480 | 3 | 30 | 400~600
LSIS1549.04 |  | OLR | LSIS | MT-800 | 480 | 3 | 30 | 520~800
LSIS1550 | A [ version C1(a)] | FDS | SOCOMEC | 38503080 | 480 | 3 | 200 |  |  | 480 | 3 | 200 | 722 | 600 | 27339 | 1,3
|  | F | Any | Class L Time Delay Fuse |  |  | 200
|  | MC | LSIS | MC-800a | 480 | 3 | 30 | 722
LSIS1550.01 |  | OLR | LSIS | MT-800 | 480 | 3 | 18 | 200~300
LSIS1550.02 |  | OLR | LSIS | MT-800 | 480 | 3 | 18 | 260~400
LSIS1550.03 |  | OLR | LSIS | MT-800 | 480 | 3 | 30 | 400~600
LSIS1550.04 |  | OLR | LSIS | MT-800 | 480 | 3 | 30 | 520~800
LSIS1551 | A [ version C1(a)] | FDS | SOCOMEC | 37103003 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 9 | 7.5 | 1493 | 1, 3
|  | F | Any | Class CC Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-6a | 600 | 3 | 5 | 9
LSIS1551.01 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.1 - 0.16
LSIS1551.02 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.16 - 0.25
LSIS1551.03 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.25 - 0.4
LSIS1551.04 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.4 - 0.63
LSIS1551.05 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.63 - 1
LSIS1551.06 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1 - 1.6
LSIS1551.07 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1.6 - 2.5
LSIS1551.08 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 2.5 - 4
LSIS1551.09 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 4 - 6
LSIS1551.10 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 5 - 8
LSIS1551.11 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 6 - 9
LSIS1552 | A [ version C1(a)] | FDS | SOCOMEC | 37103004 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 9 | 7.5 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-6a | 600 | 3 | 5 | 9
LSIS1552.01 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.1 - 0.16
LSIS1552.02 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.16 - 0.25
LSIS1552.03 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.25 - 0.4
LSIS1552.04 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.4 - 0.63
LSIS1552.05 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.63 - 1
LSIS1552.06 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1 - 1.6
LSIS1552.07 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1.6 - 2.5
LSIS1552.08 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 2.5 - 4
LSIS1552.09 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 4 - 6
LSIS1552.10 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 5 - 8
LSIS1552.11 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 6 - 9
LSIS1553 | A [ version C1(a)] | FDS | SOCOMEC | 37103003 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 9 | 7.5 | 1493 | 1, 3
|  | F | Any | Class CC Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-9a | 600 | 3 | 5 | 9
LSIS1553.01 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.1 - 0.16
LSIS1553.02 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.16 - 0.25
LSIS1553.03 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.25 - 0.4
LSIS1553.04 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.4 - 0.63
LSIS1553.05 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.63 - 1
LSIS1553.06 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1 - 1.6
LSIS1553.07 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1.6 - 2.5
LSIS1553.08 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 2.5 - 4
LSIS1553.09 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 4 - 6
LSIS1553.10 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 5 - 8
LSIS1553.11 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 6 - 9
LSIS1554 | A [ version C1(a)] | FDS | SOCOMEC | 37103004 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 9 | 7.5 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-9a | 600 | 3 | 5 | 9
LSIS1554.01 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.1 - 0.16
LSIS1554.02 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.16 - 0.25
LSIS1554.03 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.25 - 0.4
LSIS1554.04 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.4 - 0.63
LSIS1554.05 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.63 - 1
LSIS1554.06 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1 - 1.6
LSIS1554.07 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1.6 - 2.5
LSIS1554.08 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 2.5 - 4
LSIS1554.09 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 4 - 6
LSIS1554.10 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 5 - 8
LSIS1554.11 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 6 - 9
LSIS1555 | A [ version C1(a)] | FDS | SOCOMEC | 37103003 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 11 | 10 | 1493 | 1, 3
|  | F | Any | Class CC Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-12a | 600 | 3 | 5 | 11
LSIS1555.01 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.1 - 0.16
LSIS1555.02 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.16 - 0.25
LSIS1555.03 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.25 - 0.4
LSIS1555.04 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.4 - 0.63
LSIS1555.05 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.63 - 1
LSIS1555.06 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1 - 1.6
LSIS1555.07 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1.6 - 2.5
LSIS1555.08 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 2.5 - 4
LSIS1555.09 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 4 - 6
LSIS1555.10 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 5 - 8
LSIS1555.11 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 6 - 9
LSIS1555.12 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 7 - 10
LSIS1555.13 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 9 - 13
LSIS1556 | A [ version C1(a)] | FDS | SOCOMEC | 37103004 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 11 | 10 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-12a | 600 | 3 | 5 | 11
LSIS1556.01 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.1 - 0.16
LSIS1556.02 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.16 - 0.25
LSIS1556.03 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.25 - 0.4
LSIS1556.04 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.4 - 0.63
LSIS1556.05 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.63 - 1
LSIS1556.06 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1 - 1.6
LSIS1556.07 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1.6 - 2.5
LSIS1556.08 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 2.5 - 4
LSIS1556.09 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 4 - 6
LSIS1556.10 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 5 - 8
LSIS1556.11 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 6 - 9
LSIS1556.12 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 7 - 10
LSIS1556.13 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 9 - 13
LSIS1557 | A [ version C1(a)] | FDS | SOCOMEC | 37103003 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 17 | 15 | 1493 | 1, 3
|  | F | Any | Class CC Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-18a | 600 | 3 | 5 | 17
LSIS1557.01 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.1 - 0.16
LSIS1557.02 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.16 - 0.25
LSIS1557.03 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.25 - 0.4
LSIS1557.04 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.4 - 0.63
LSIS1557.05 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.63 - 1
LSIS1557.06 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1 - 1.6
LSIS1557.07 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1.6 - 2.5
LSIS1557.08 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 2.5 - 4
LSIS1557.09 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 4 - 6
LSIS1557.10 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 5 - 8
LSIS1557.11 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 6 - 9
LSIS1557.12 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 7 - 10
LSIS1557.13 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 9 - 13
LSIS1557.14 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 12 - 18
LSIS1558 | A [ version C1(a)] | FDS | SOCOMEC | 37103004 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 17 | 15 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-18a | 600 | 3 | 5 | 17
LSIS1558.01 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.1 - 0.16
LSIS1558.02 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.16 - 0.25
LSIS1558.03 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.25 - 0.4
LSIS1558.04 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.4 - 0.63
LSIS1558.05 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 0.63 - 1
LSIS1558.06 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1 - 1.6
LSIS1558.07 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 1.6 - 2.5
LSIS1558.08 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 2.5 - 4
LSIS1558.09 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 4 - 6
LSIS1558.10 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 5 - 8
LSIS1558.11 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 6 - 9
LSIS1558.12 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 7 - 10
LSIS1558.13 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 9 - 13
LSIS1558.14 |  | OLR | LSIS | MT-12 | 600 | 3 | 5 | 12 - 18
LSIS1559 | A [ version C1(a)] | FDS | SOCOMEC | 38613006 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 9 | 7.5 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-9b | 600 | 3 | 5 | 9
LSIS1559.01 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.1 - 0.16
LSIS1559.02 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.16 - 0.25
LSIS1559.03 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.25 - 0.4
LSIS1559.04 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.4 - 0.63
LSIS1559.05 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.63 - 1
LSIS1559.06 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 1 - 1.6
LSIS1559.07 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 1.6 - 2.5
LSIS1559.08 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 2.5 - 4
LSIS1559.09 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 4 - 6
LSIS1559.10 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 5 - 8
LSIS1559.11 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 6 - 9
LSIS1560 | A [ version C1(a)] | FDS | SOCOMEC | 38613006 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 11 | 10 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-12b | 600 | 3 | 5 | 11
LSIS1560.01 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.1 - 0.16
LSIS1560.02 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.16 - 0.25
LSIS1560.03 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.25 - 0.4
LSIS1560.04 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.4 - 0.63
LSIS1560.05 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.63 - 1
LSIS1560.06 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 1 - 1.6
LSIS1560.07 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 1.6 - 2.5
LSIS1560.08 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 2.5 - 4
LSIS1560.09 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 4 - 6
LSIS1560.10 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 5 - 8
LSIS1560.11 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 6 - 9
LSIS1560.12 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 7 - 10
LSIS1560.13 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 9 - 13
LSIS1561 | A [ version C1(a)] | FDS | SOCOMEC | 38613006 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 17 | 15 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-18b | 600 | 3 | 5 | 17
LSIS1561.01 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.1 - 0.16
LSIS1561.02 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.16 - 0.25
LSIS1561.03 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.25 - 0.4
LSIS1561.04 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.4 - 0.63
LSIS1561.05 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 0.63 - 1
LSIS1561.06 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 1 - 1.6
LSIS1561.07 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 1.6 - 2.5
LSIS1561.08 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 2.5 - 4
LSIS1561.09 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 4 - 6
LSIS1561.10 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 5 - 8
LSIS1561.11 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 6 - 9
LSIS1561.12 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 7 - 10
LSIS1561.13 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 9 - 13
LSIS1561.14 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 12 - 18
LSIS1562 | A [ version C1(a)] | FDS | SOCOMEC | 38613006 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 22 | 20 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-22b | 600 | 3 | 5 | 22
LSIS1562.01 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 12 - 18
LSIS1562.02 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 16 - 22
LSIS1563 | A [ version C1(a)] | FDS | SOCOMEC | 38613010 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 27 | 25 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-32a | 600 | 3 | 5 | 27
LSIS1563.01 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 12 - 18
LSIS1563.02 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 16 - 22
LSIS1563.03 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 18 - 25
LSIS1563.04 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 22 - 32
LSIS1564.01 | A [ version C1(a)] | FDS | SOCOMEC | 38613010 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 32 | 30 | 1493 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-40a | 600 | 3 | 5 | 32
LSIS1564.01 |  | OLR | LSIS | MT-32 | 600 | 3 | 5 | 22 - 32
LSIS1565 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 52 | 50 | 2667 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-50a | 600 | 3 | 5 | 52
LSIS1565.01 |  | OLR | LSIS | MT-63 | 600 | 3 | 5 | 24 - 36
LSIS1565.02 |  | OLR | LSIS | MT-63 | 600 | 3 | 5 | 28 - 40
LSIS1565.03 |  | OLR | LSIS | MT-63 | 600 | 3 | 5 | 34 - 50
LSIS1565.04 |  | OLR | LSIS | MT-63 | 600 | 3 | 5 | 45 - 65
LSIS1566 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 62 | 60 | 2667 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-65a | 600 | 3 | 10 | 62
LSIS1566.01 |  | OLR | LSIS | MT-63 | 600 | 3 | 5 | 34 - 50
LSIS1566.02 |  | OLR | LSIS | MT-63 | 600 | 3 | 10 | 45 - 65
LSIS1567 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 62 | 60 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-75a | 600 | 3 | 10 | 62
LSIS1567.01 |  | OLR | LSIS | MT-95 | 600 | 3 | 5 | 34 - 50
LSIS1567.02 |  | OLR | LSIS | MT-95 | 600 | 3 | 10 | 45 - 65
LSIS1567.03 |  | OLR | LSIS | MT-95 | 600 | 3 | 10 | 54 - 75
LSIS1568 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 77 | 75 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-85a | 600 | 3 | 10 | 77
LSIS1568.01 |  | OLR | LSIS | MT-95 | 600 | 3 | 5 | 34 - 50
LSIS1568.02 |  | OLR | LSIS | MT-95 | 600 | 3 | 10 | 45 - 65
LSIS1568.03 |  | OLR | LSIS | MT-95 | 600 | 3 | 10 | 54 - 75
LSIS1568.04 |  | OLR | LSIS | MT-95 | 600 | 3 | 10 | 63 - 85
LSIS1569 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 77 | 75 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-100a | 600 | 3 | 10 | 77
LSIS1569.01 |  | OLR | LSIS | MT-95 | 600 | 3 | 5 | 34 - 50
LSIS1569.02 |  | OLR | LSIS | MT-95 | 600 | 3 | 10 | 45 - 65
LSIS1569.03 |  | OLR | LSIS | MT-95 | 600 | 3 | 10 | 54 - 75
LSIS1569.04 |  | OLR | LSIS | MT-95 | 600 | 3 | 10 | 63 - 85
LSIS1570 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 77 | 75 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-130a | 600 | 3 | 10 | 77
LSIS1570.01 |  | OLR | LSIS | MT-150 | 600 | 3 | 5 | 34 - 50
LSIS1570.02 |  | OLR | LSIS | MT-150 | 600 | 3 | 10 | 45 - 65
LSIS1570.03 |  | OLR | LSIS | MT-150 | 600 | 3 | 10 | 54 - 75
LSIS1570.04 |  | OLR | LSIS | MT-150 | 600 | 3 | 10 | 63 - 85
LSIS1571 | A [ version C1(a)] | FDS | SOCOMEC | 38613020 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 77 | 75 | 3018 | 1, 3
|  | F | Any | Class J Time Delay Fuse | 600 | - | 100 | -
|  | MC | LSIS | MC-150a | 600 | 3 | 10 | 77
LSIS1571.01 |  | OLR | LSIS | MT-150 | 600 | 3 | 5 | 34 - 50
LSIS1571.02 |  | OLR | LSIS | MT-150 | 600 | 3 | 10 | 45 - 65
LSIS1571.03 |  | OLR | LSIS | MT-150 | 600 | 3 | 10 | 54 - 75
LSIS1571.04 |  | OLR | LSIS | MT-150 | 600 | 3 | 10 | 63 - 85
LSIS1572 | A [ version C1(a)] | FDS | SOCOMEC | 38513038 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 125 | 125 | 9764 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 100 | -
|  | MC | LSIS | MC-185a | 600 | 3 | 10 | 125
LSIS1572.01 |  | OLR | LSIS | MT-225 | 600 | 3 | 5 | 65 ~ 100
LSIS1572.02 |  | OLR | LSIS | MT-225 | 600 | 3 | 5 | 85 ~ 125
LSIS1573 | A [ version C1(a)] | FDS | SOCOMEC | 38513038 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 144 | 150 | 9764 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 100 | -
|  | MC | LSIS | MC-225a | 600 | 3 | 10 | 144
LSIS1573.01 |  | OLR | LSIS | MT-225 | 600 | 3 | 5 | 65 ~ 100
LSIS1573.02 |  | OLR | LSIS | MT-225 | 600 | 3 | 5 | 85 ~ 125
LSIS1573.03 |  | OLR | LSIS | MT-225 | 600 | 3 | 10 | 100 ~ 160
LSIS1574 | A [ version C1(a)] | FDS | SOCOMEC | 38503060 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 192 | 200 | 27339 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 100 | -
|  | MC | LSIS | MC-265a | 600 | 3 | 10 | 192
LSIS1574.01 |  | OLR | LSIS | MT-400 | 600 | 3 | 5 | 85 ~ 125
LSIS1574.02 |  | OLR | LSIS | MT-400 | 600 | 3 | 10 | 100 ~ 160
LSIS1574.03 |  | OLR | LSIS | MT-400 | 600 | 3 | 10 | 120 ~ 185
LSIS1574.04 |  | OLR | LSIS | MT-400 | 600 | 3 | 10 | 160 ~ 240
LSIS1575 | A [ version C1(a)] | FDS | SOCOMEC | 38503060 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 242 | 250 | 27339 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 100 | -
|  | MC | LSIS | MC-330a | 600 | 3 | 10 | 242
LSIS1575.01 |  | OLR | LSIS | MT-400 | 600 | 3 | 5 | 85 ~ 125
LSIS1575.02 |  | OLR | LSIS | MT-400 | 600 | 3 | 10 | 100 ~ 160
LSIS1575.03 |  | OLR | LSIS | MT-400 | 600 | 3 | 10 | 120 ~ 185
LSIS1575.04 |  | OLR | LSIS | MT-400 | 600 | 3 | 10 | 160 ~ 240
LSIS1575.05 |  | OLR | LSIS | MT-400 | 600 | 3 | 10 | 200 ~ 330
LSIS1576 | A [ version C1(a)] | FDS | SOCOMEC | 38503060 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 289 | 300 | 27339 | 1, 3
|  | F | Any | Class J Time Delay Fuse |  |  | 100 | -
|  | MC | LSIS | MC-400a | 600 | 3 | 10 | 289
LSIS1576.01 |  | OLR | LSIS | MT-400 | 600 | 3 | 10 | 160 ~ 240
LSIS1576.02 |  | OLR | LSIS | MT-400 | 600 | 3 | 10 | 200 ~ 330
LSIS1577 | A [ version C1(a)] | FDS | SOCOMEC | 38503060 | 600 | 3 | 100 | - |  | 600 | 3 | 100 | 382 | 400 | 27339 | 1,3
|  | F | Any | Class J Time Delay Fuse |  |  | 100 | -
|  | MC | LSIS | MC-500a | 600 | 3 | 18 | 382
LSIS1577.01 |  | OLR | LSIS | MT-800 | 600 | 3 | 18 | 200~300
LSIS1577.02 |  | OLR | LSIS | MT-800 | 600 | 3 | 18 | 260~400
LSIS1578 | A [ version C1(a)] | FDS | SOCOMEC | 38503080 | 600 | 3 | 100 |  |  | 600 | 3 | 100 | 472 | 500 | 27339 | 1,3
|  | F | Any | Class L Time Delay Fuse |  |  | 100
|  | MC | LSIS | MC-630a | 600 | 3 | 30 | 472
LSIS1578.01 |  | OLR | LSIS | MT-800 | 600 | 3 | 18 | 200~300
LSIS1578.02 |  | OLR | LSIS | MT-800 | 600 | 3 | 30 | 260~400
LSIS1578.03 |  | OLR | LSIS | MT-800 | 600 | 3 | 30 | 400~600
LSIS1579 | A [ version C1(a)] | FDS | SOCOMEC | 38503080 | 600 | 3 | 100 |  |  | 600 | 3 | 100 | 566 | 600 | 27339 | 1,3
|  | F | Any | Class L Time Delay Fuse |  |  | 100
|  | MC | LSIS | MC-800a | 600 | 3 | 30 | 566
LSIS1579.01 |  | OLR | LSIS | MT-800 | 600 | 3 | 18 | 200~300
LSIS1579.02 |  | OLR | LSIS | MT-800 | 600 | 3 | 30 | 260~400
LSIS1579.03 |  | OLR | LSIS | MT-800 | 600 | 3 | 30 | 400~600
LSIS1579.04 |  | OLR | LSIS | MT-800 | 600 | 3 | 30 | 520~800
Notes:
[1] Horsepower ratings shown are for reference only, final selection of Combination Motor Controller depends on the actual motor full load current and service factor
[2] Full load current values from NEC Table 430.250 or represent the maximum current rating of the combination motor controller
Conditions of Acceptability:
| 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
| 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
| 3 | Unless otherwise specified, all connections between components are made using insulated wire
having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
| 4 | The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application
(Type E Combination Motor Controllers).

## Type C
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | [B9] Conditions of Use
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating
LSIS101 | C [ version C2(b)] | CB | LSIS | UTE100E | 240 | 3 | 50 | 15 | 3 | 240 | 3 | 50 | 9.6 | 3 | 1418.3906 | 1
|  | MC | LSIS | MC-6a |  |  | 5 | 9.6 | -
LSIS101.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS101.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS101.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS101.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS101.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS101.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS101.07 |  | OLR | LSIS | MT-12 |  |  | 1 | 1.6 - 2.5 | -
LSIS101.08 |  | OLR | LSIS | MT-12 |  |  | 1 | 2.5 - 4 | -
LSIS101.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS101.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS101.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS101.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS102 | C [ version C2(b)] | CB | LSIS | UTE100N | 240 | 3 | 65 | 15 | 3 | 240 | 3 | 65 | 9.6 | 3 | 1418.3906 | 1
|  | MC | LSIS | MC-6a |  |  | 5 | 9.6 | -
LSIS102.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS102.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS102.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS102.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS102.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS102.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS102.07 |  | OLR | LSIS | MT-12 |  |  | 1 | 1.6 - 2.5 | -
LSIS102.08 |  | OLR | LSIS | MT-12 |  |  | 1 | 2.5 - 4 | -
LSIS102.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS102.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS102.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS102.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS103 | C [ version C2(b)] | CB | LSIS | UTE100E | 240 | 3 | 50 | 20 | 3 | 240 | 3 | 50 | 9.6 | 3 | 1418.3906 | 1
|  | MC | LSIS | MC-9a |  |  | 5 | 9.6 | -
LSIS103.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS103.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS103.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS103.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS103.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS103.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS103.07 |  | OLR | LSIS | MT-12 |  |  | 1 | 1.6 - 2.5 | -
LSIS103.08 |  | OLR | LSIS | MT-12 |  |  | 1 | 2.5 - 4 | -
LSIS103.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS103.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS103.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS103.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS104 | C [ version C2(b)] | CB | LSIS | UTE100N | 240 | 3 | 65 | 20 | 3 | 240 | 3 | 65 | 9.6 | 3 | 1418.3906 | 1
|  | MC | LSIS | MC-9a |  |  | 5 | 9.6 | -
LSIS104.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS104.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS104.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS104.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS104.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS104.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS104.07 |  | OLR | LSIS | MT-12 |  |  | 1 | 1.6 - 2.5 | -
LSIS104.08 |  | OLR | LSIS | MT-12 |  |  | 1 | 2.5 - 4 | -
LSIS104.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS104.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS104.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS104.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS105 | C [ version C2(b)] | CB | LSIS | UTE100E | 240 | 3 | 50 | 30 | 5 | 240 | 3 | 50 | 15.2 | 5 | 1418.3906 | 1
|  | MC | LSIS | MC-12a |  |  | 5 | 15.2 | -
LSIS105.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS105.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS105.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS105.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS105.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS105.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS105.07 |  | OLR | LSIS | MT-12 |  |  | 1 | 1.6 - 2.5 | -
LSIS105.08 |  | OLR | LSIS | MT-12 |  |  | 1 | 2.5 - 4 | -
LSIS105.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS105.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS105.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS105.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS105.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS105.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS106 | C [ version C2(b)] | CB | LSIS | UTE100N | 240 | 3 | 65 | 30 | 5 | 240 | 3 | 65 | 15.2 | 5 | 1418.3906 | 1
|  | MC | LSIS | MC-12a |  |  | 5 | 15.2 | -
LSIS106.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS106.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS106.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS106.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS106.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS106.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS106.07 |  | OLR | LSIS | MT-12 |  |  | 1 | 1.6 - 2.5 | -
LSIS106.08 |  | OLR | LSIS | MT-12 |  |  | 1 | 2.5 - 4 | -
LSIS106.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS106.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS106.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS106.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS106.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS106.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS107 | C [ version C2(b)] | CB | LSIS | UTE100E | 240 | 3 | 50 | 40 | 7.5 | 240 | 3 | 50 | 22 | 7.5 | 1418.3906 | 1
|  | MC | LSIS | MC-18a |  |  | 5 | 22 | -
LSIS107.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS107.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS107.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS107.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS107.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS107.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS107.07 |  | OLR | LSIS | MT-12 |  |  | 1 | 1.6 - 2.5 | -
LSIS107.08 |  | OLR | LSIS | MT-12 |  |  | 1 | 2.5 - 4 | -
LSIS107.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS107.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS107.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS107.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS107.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS107.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS108 | C [ version C2(b)] | CB | LSIS | UTE100N | 240 | 3 | 65 | 40 | 7.5 | 240 | 3 | 65 | 22 | 7.5 | 1418.3906 | 1
|  | MC | LSIS | MC-18a |  |  | 5 | 22 | -
LSIS108.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS108.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS108.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS108.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS108.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS108.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS108.07 |  | OLR | LSIS | MT-12 |  |  | 1 | 1.6 - 2.5 | -
LSIS108.08 |  | OLR | LSIS | MT-12 |  |  | 1 | 2.5 - 4 | -
LSIS108.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS108.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS108.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS108.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS108.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS108.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS109 | C [ version C2(b)] | CB | LSIS | UTS150N | 240 | 3 | 65 | 40 | 10 | 240 | 3 | 65 | 22 | 7.5 | 1784.6107 | 1
|  | MC | LSIS | MC-18a |  |  | 5 | 22 | -
LSIS109.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS109.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS109.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS109.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS109.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS109.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS109.07 |  | OLR | LSIS | MT-12 |  |  | 1 | 1.6 - 2.5 | -
LSIS109.08 |  | OLR | LSIS | MT-12 |  |  | 1 | 2.5 - 4 | -
LSIS109.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS109.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS109.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS109.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS109.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS109.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS110 | C [ version C2(b)] | CB | LSIS | UTS150L | 240 | 3 | 150 | 40 | 10 | 240 | 3 | 100 | 22 | 7.5 | 1784.6107 | 1
|  | MC | LSIS | MC-18a |  |  | 5 | 22 | -
LSIS110.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS110.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS110.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS110.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS110.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS110.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS110.07 |  | OLR | LSIS | MT-12 |  |  | 1 | 1.6 - 2.5 | -
LSIS110.08 |  | OLR | LSIS | MT-12 |  |  | 1 | 2.5 - 4 | -
LSIS110.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS110.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS110.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS110.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS110.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS110.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS111 | C [ version C2(b)] | CB | LSIS | UTE100E | 240 | 3 | 50 | 15 | 3 | 240 | 3 | 50 | 9.6 | 3 | 1418.3906 | 1
|  | MC | LSIS | MC-9b |  |  | 5 | 9.6 | -
LSIS111.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS111.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS111.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS111.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS111.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS111.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS111.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS111.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS111.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS111.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS111.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS111.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS112 | C [ version C2(b)] | CB | LSIS | UTE100N | 240 | 3 | 65 | 15 | 3 | 240 | 3 | 65 | 9.6 | 3 | 1418.3906 | 1
|  | MC | LSIS | MC-9b |  |  | 5 | 9.6 | -
LSIS112.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS112.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS112.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS112.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS112.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS112.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS112.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS112.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS112.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS112.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS112.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS112.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS113 | C [ version C2(b)] | CB | LSIS | UTE100E | 240 | 3 | 50 | 30 | 5 | 240 | 3 | 50 | 15.2 | 5 | 1418.3906 | 1
|  | MC | LSIS | MC-12b |  |  | 5 | 15.2 | -
LSIS113.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS113.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS113.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS113.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS113.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS113.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS113.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS113.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS113.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS113.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS113.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS113.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS113.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS113.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS114 | C [ version C2(b)] | CB | LSIS | UTE100N | 240 | 3 | 65 | 30 | 5 | 240 | 3 | 65 | 15.2 | 5 | 1418.3906 | 1
|  | MC | LSIS | MC-12b |  |  | 5 | 15.2 | -
LSIS114.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS114.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS114.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS114.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS114.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS114.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS114.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS114.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS114.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS114.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS114.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS114.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS114.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS114.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS115 | C [ version C2(b)] | CB | LSIS | UTE100E | 240 | 3 | 50 | 40 | 7.5 | 240 | 3 | 50 | 22 | 7.5 | 1418.3906 | 1
|  | MC | LSIS | MC-18b |  |  | 5 | 22 | -
LSIS115.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS115.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS115.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS115.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS115.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS115.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS115.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS115.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS115.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS115.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS115.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS115.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS115.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS115.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS115.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS115.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS116 | C [ version C2(b)] | CB | LSIS | UTE100N | 240 | 3 | 65 | 40 | 7.5 | 240 | 3 | 65 | 22 | 7.5 | 1418.3906 | 1
|  | MC | LSIS | MC-18b |  |  | 5 | 22 | -
LSIS116.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS116.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS116.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS116.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS116.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS116.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS116.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS116.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS116.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS116.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS116.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS116.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS116.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS116.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS116.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS116.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS117 | C [ version C2(b)] | CB | LSIS | UTS150N | 240 | 3 | 65 | 40 | 10 | 240 | 3 | 65 | 22 | 7.5 | 1784.6107 | 1
|  | MC | LSIS | MC-18b |  |  | 5 | 22 | -
LSIS117.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS117.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS117.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS117.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS117.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS117.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS117.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS117.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS117.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS117.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS117.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS117.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS117.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS117.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS117.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS117.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS118 | C [ version C2(b)] | CB | LSIS | UTS150L | 240 | 3 | 150 | 40 | 10 | 240 | 3 | 100 | 22 | 7.5 | 1784.6107 | 1
|  | MC | LSIS | MC-18b |  |  | 5 | 22 | -
LSIS118.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS118.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS118.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS118.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS118.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS118.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS118.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS118.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS118.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS118.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS118.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS118.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS118.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS118.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS118.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS118.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS119 | C [ version C2(b)] | CB | LSIS | UTE100E | 240 | 3 | 50 | 50 | 10 | 240 | 3 | 50 | 28 | 10 | 1418.3906 | 1
|  | MC | LSIS | MC-22b |  |  | 5 | 28 | -
LSIS119.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS119.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS119.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS119.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS119.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS119.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS119.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS119.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS119.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS119.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS119.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS119.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS119.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS119.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS119.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS119.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS119.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS120 | C [ version C2(b)] | CB | LSIS | UTE100N | 240 | 3 | 65 | 50 | 10 | 240 | 3 | 65 | 28 | 10 | 1418.3906 | 1
|  | MC | LSIS | MC-22b |  |  | 5 | 28 | -
LSIS120.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS120.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS120.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS120.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS120.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS120.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS120.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS120.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS120.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS120.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS120.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS120.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS120.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS120.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS120.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS120.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS120.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS121 | C [ version C2(b)] | CB | LSIS | UTS150N | 240 | 3 | 65 | 50 | 10 | 240 | 3 | 65 | 28 | 10 | 1784.6107 | 1
|  | MC | LSIS | MC-22b |  |  | 5 | 28 | -
LSIS121.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS121.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS121.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS121.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS121.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS121.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS121.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS121.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS121.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS121.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS121.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS121.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS121.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS121.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS121.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS121.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS121.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS122 | C [ version C2(b)] | CB | LSIS | UTS150L | 240 | 3 | 150 | 50 | 10 | 240 | 3 | 100 | 28 | 10 | 1784.6107 | 1
|  | MC | LSIS | MC-22b |  |  | 5 | 28 | -
LSIS122.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS122.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS122.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS122.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS122.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS122.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS122.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS122.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS122.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS122.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS122.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS122.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS122.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS122.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS122.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS122.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS122.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS123 | C [ version C2(b)] | CB | LSIS | UTE100E | 240 | 3 | 50 | 50 | 10 | 240 | 3 | 50 | 28 | 10 | 1418.3906 | 1
|  | MC | LSIS | MC-32a |  |  | 5 | 28 | -
LSIS123.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS123.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS123.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS123.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS123.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS123.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS123.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS123.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS123.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS123.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS123.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS123.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS123.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS123.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS123.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS123.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS123.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS124 | C [ version C2(b)] | CB | LSIS | UTE100N | 240 | 3 | 65 | 50 | 10 | 240 | 3 | 65 | 28 | 10 | 1418.3906 | 1
|  | MC | LSIS | MC-32a |  |  | 5 | 28 | -
LSIS124.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS124.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS124.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS124.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS124.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS124.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS124.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS124.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS124.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS124.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS124.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS124.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS124.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS124.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS124.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS124.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS124.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS125 | C [ version C2(b)] | CB | LSIS | UTS150N | 240 | 3 | 65 | 50 | 10 | 240 | 3 | 65 | 28 | 10 | 1784.6107 | 1
|  | MC | LSIS | MC-32a |  |  | 5 | 28 | -
LSIS125.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS125.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS125.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS125.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS125.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS125.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS125.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS125.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS125.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS125.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS125.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS125.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS125.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS125.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS125.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS125.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS125.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS126 | C [ version C2(b)] | CB | LSIS | UTS150L | 240 | 3 | 150 | 50 | 10 | 240 | 3 | 100 | 28 | 10 | 1784.6107 | 1
|  | MC | LSIS | MC-32a |  |  | 5 | 28 | -
LSIS126.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS126.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS126.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS126.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS126.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS126.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS126.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS126.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS126.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS126.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS126.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS126.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS126.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS126.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS126.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS126.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS126.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS127 | C [ version C2(b)] | CB | LSIS | UTE100E | 240 | 3 | 50 | 50 | 15 | 240 | 3 | 50 | 42 | 15 | 1418.3906 | 1
|  | MC | LSIS | MC-40a |  |  | 5 | 42 | -
LSIS127.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS127.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS127.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS127.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS127.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS127.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS127.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS127.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS127.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS127.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS127.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS127.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS127.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS127.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS127.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS127.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS127.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS127.18 |  | OLR | LSIS | MT-32 |  |  | 5 | 28 - 40 | -
LSIS128 | C [ version C2(b)] | CB | LSIS | UTE100N | 240 | 3 | 65 | 60 | 15 | 240 | 3 | 65 | 42 | 15 | 1418.3906 | 1
|  | MC | LSIS | MC-40a |  |  | 5 | 42 | -
LSIS128.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS128.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS128.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS128.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS128.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS128.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS128.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS128.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS128.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS128.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS128.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS128.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS128.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS128.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS128.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS128.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS128.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS128.18 |  | OLR | LSIS | MT-32 |  |  | 5 | 28 - 40 | -
LSIS129 | C [ version C2(b)] | CB | LSIS | UTS150N | 240 | 3 | 65 | 60 | 15 | 240 | 3 | 65 | 42 | 15 | 1784.6107 | 1
|  | MC | LSIS | MC-40a |  |  | 5 | 42 | -
LSIS129.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS129.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS129.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS129.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS129.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS129.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS129.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS129.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS129.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS129.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS129.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS129.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS129.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS129.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS129.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS129.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS129.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS129.18 |  | OLR | LSIS | MT-32 |  |  | 5 | 28 - 40 | -
LSIS130 | C [ version C2(b)] | CB | LSIS | UTS150L | 240 | 3 | 150 | 60 | 15 | 240 | 3 | 100 | 42 | 15 | 1784.6107 | 1
|  | MC | LSIS | MC-40a |  |  | 5 | 42 | -
LSIS130.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS130.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS130.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS130.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS130.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS130.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS130.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS130.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS130.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS130.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS130.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS130.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS130.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS130.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS130.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS130.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS130.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS130.18 |  | OLR | LSIS | MT-32 |  |  | 5 | 28 - 40 | -
LSIS131 | C [ version C2(b)] | CB | LSIS | UTE100E | 240 | 3 | 50 | 80 | 25 | 240 | 3 | 50 | 65 | 25 | 1418.3906 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 65 | -
LSIS131.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS131.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS131.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS131.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS131.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS131.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS131.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS131.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS131.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS131.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS131.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS131.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS132 | C [ version C2(b)] | CB | LSIS | UTE100N | 240 | 3 | 65 | 80 | 25 | 240 | 3 | 65 | 65 | 25 | 1418.3906 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 65 | -
LSIS132.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS132.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS132.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS132.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS132.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS132.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS132.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS132.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS132.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS132.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS132.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS132.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS133 | C [ version C2(b)] | CB | LSIS | UTS150N | 240 | 3 | 65 | 80 | 25 | 240 | 3 | 65 | 65 | 25 | 1784.6107 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 65 | -
LSIS133.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS133.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS133.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS133.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS133.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS133.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS133.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS133.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS133.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS133.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS133.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS133.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS134 | C [ version C2(b)] | CB | LSIS | UTS150L | 240 | 3 | 150 | 80 | 25 | 240 | 3 | 100 | 65 | 25 | 1784.6107 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 65 | -
LSIS134.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS134.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS134.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS134.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS134.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS134.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS134.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS134.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS134.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS134.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS134.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS134.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS135 | C [ version C2(b)] | CB | LSIS | UTE100E | 240 | 3 | 50 | 100 | 30 | 240 | 3 | 50 | 80 | 30 | 1418 | 1
|  | MC | LSIS | MC-65a |  |  | 5 | 80 | -
LSIS135.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS135.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS135.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS135.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS135.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS135.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS135.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS135.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS135.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS135.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS135.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS135.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS136 | C [ version C2(b)] | CB | LSIS | UTE100N | 240 | 3 | 65 | 100 | 30 | 240 | 3 | 65 | 80 | 30 | 1418 | 1
|  | MC | LSIS | MC-65a |  |  | 5 | 80 | -
LSIS136.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS136.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS136.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS136.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS136.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS136.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS136.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS136.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS136.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS136.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS136.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS136.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS137 | C [ version C2(b)] | CB | LSIS | UTS150N | 240 | 3 | 65 | 100 | 30 | 240 | 3 | 65 | 80 | 30 | 1785 | 1
|  | MC | LSIS | MC-65a |  |  | 5 | 80 | -
LSIS137.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS137.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS137.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS137.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS137.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS137.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS137.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS137.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS137.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS137.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS137.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS137.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS138 | C [ version C2(b)] | CB | LSIS | UTS150L | 240 | 3 | 150 | 100 | 30 | 240 | 3 | 100 | 80 | 30 | 1785 | 1
|  | MC | LSIS | MC-65a |  |  | 5 | 80 | -
LSIS138.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS138.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS138.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS138.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS138.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS138.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS138.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS138.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS138.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS138.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS138.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS138.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS139 | C [ version C2(b)] | CB | LSIS | UTS150N | 240 | 3 | 65 | 150 | 30 | 240 | 3 | 65 | 80 | 30 | 1785 | 1
|  | MC | LSIS | MC-75a |  |  | 5 | 80 | -
LSIS139.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS139.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS139.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS139.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS139.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS139.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS139.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS139.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS139.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS139.10 |  | OLR | LSIS | MT-95 |  |  | 5 | 54 - 75 | -
LSIS139.11 |  | OLR | LSIS | MT-95 |  |  | 5 | 63 - 85 | -
LSIS139.12 |  | OLR | LSIS | MT-95 |  |  | 5 | 70 - 95 | -
LSIS140 | C [ version C2(b)] | CB | LSIS | UTS150L | 240 | 3 | 150 | 150 | 30 | 240 | 3 | 100 | 80 | 30 | 1784.6107 | 1
|  | MC | LSIS | MC-75a |  |  | 5 | 80 | -
LSIS140.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS140.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS140.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS140.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS140.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS140.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS140.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS140.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS140.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS140.10 |  | OLR | LSIS | MT-95 |  |  | 5 | 54 - 75 | -
LSIS140.11 |  | OLR | LSIS | MT-95 |  |  | 5 | 63 - 85 | -
LSIS140.12 |  | OLR | LSIS | MT-95 |  |  | 5 | 70 - 95 | -
LSIS141 | C [ version C2(b)] | CB | LSIS | UTS150N | 240 | 3 | 65 | 150 | 40 | 240 | 3 | 65 | 104 | 40 | 1785 | 1
|  | MC | LSIS | MC-85a |  |  | 5 | 104 | -
LSIS141.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS141.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS141.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS141.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS141.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS141.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS141.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS141.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS141.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS141.10 |  | OLR | LSIS | MT-95 |  |  | 5 | 54 - 75 | -
LSIS141.11 |  | OLR | LSIS | MT-95 |  |  | 5 | 63 - 85 | -
LSIS141.12 |  | OLR | LSIS | MT-95 |  |  | 5 | 70 - 95 | -
LSIS141.13 |  | OLR | LSIS | MT-95 |  |  | 5 | 80 - 100 | -
LSIS142 | C [ version C2(b)] | CB | LSIS | UTS150L | 240 | 3 | 150 | 150 | 40 | 240 | 3 | 100 | 104 | 40 | 1785 | 1
|  | MC | LSIS | MC-85a |  |  | 5 | 104 | -
LSIS142.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS142.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS142.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS142.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS142.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS142.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS142.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS142.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS142.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS142.10 |  | OLR | LSIS | MT-95 |  |  | 5 | 54 - 75 | -
LSIS142.11 |  | OLR | LSIS | MT-95 |  |  | 5 | 63 - 85 | -
LSIS142.12 |  | OLR | LSIS | MT-95 |  |  | 5 | 70 - 95 | -
LSIS142.13 |  | OLR | LSIS | MT-95 |  |  | 5 | 80 - 100 | -
LSIS143 | C [ version C2(b)] | CB | LSIS | UTS150N | 240 | 3 | 65 | 150 | 40 | 240 | 3 | 65 | 104 | 40 | 1785 | 1
|  | MC | LSIS | MC-100a |  |  | 5 | 104 | -
LSIS143.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS143.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS143.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS143.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS143.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS143.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS143.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS143.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS143.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS143.10 |  | OLR | LSIS | MT-95 |  |  | 5 | 54 - 75 | -
LSIS143.11 |  | OLR | LSIS | MT-95 |  |  | 5 | 63 - 85 | -
LSIS143.12 |  | OLR | LSIS | MT-95 |  |  | 5 | 70 - 95 | -
LSIS143.13 |  | OLR | LSIS | MT-95 |  |  | 5 | 80 - 100 | -
LSIS144 | C [ version C2(b)] | CB | LSIS | UTS150L | 240 | 3 | 150 | 150 | 40 | 240 | 3 | 100 | 104 | 40 | 1785 | 1
|  | MC | LSIS | MC-100a |  |  | 5 | 104 | -
LSIS144.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS144.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS144.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS144.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS144.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS144.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS144.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS144.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS144.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS144.10 |  | OLR | LSIS | MT-95 |  |  | 5 | 54 - 75 | -
LSIS144.11 |  | OLR | LSIS | MT-95 |  |  | 5 | 63 - 85 | -
LSIS144.12 |  | OLR | LSIS | MT-95 |  |  | 5 | 70 - 95 | -
LSIS144.13 |  | OLR | LSIS | MT-95 |  |  | 5 | 80 - 100 | -
LSIS145 | C [ version C2(b)] | CB | LSIS | UTS150N | 240 | 3 | 65 | 150 | 40 | 240 | 3 | 65 | 104 | 40 | 1785 | 1
|  | MC | LSIS | MC-130a |  |  | 5 | 104 | -
LSIS145.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS145.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS145.03 |  | OLR | LSIS | MT-150 |  |  | 5 | 54 - 75 | -
LSIS145.04 |  | OLR | LSIS | MT-150 |  |  | 5 | 63 - 85 | -
LSIS145.05 |  | OLR | LSIS | MT-150 |  |  | 5 | 80 - 105 | -
LSIS145.06 |  | OLR | LSIS | MT-150 |  |  | 5 | 95 - 130 | -
LSIS146 | C [ version C2(b)] | CB | LSIS | UTS150L | 240 | 3 | 150 | 150 | 40 | 240 | 3 | 100 | 104 | 40 | 1785 | 1
|  | MC | LSIS | MC-130a |  |  | 5 | 104 | -
LSIS146.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS146.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS146.03 |  | OLR | LSIS | MT-150 |  |  | 5 | 54 - 75 | -
LSIS146.04 |  | OLR | LSIS | MT-150 |  |  | 5 | 63 - 85 | -
LSIS146.05 |  | OLR | LSIS | MT-150 |  |  | 5 | 80 - 105 | -
LSIS146.06 |  | OLR | LSIS | MT-150 |  |  | 5 | 95 - 130 | -
LSIS147 | C [ version C2(b)] | CB | LSIS | UTS150N | 240 | 3 | 65 | 150 | 50 | 240 | 3 | 65 | 130 | 50 | 1785 | 1
|  | MC | LSIS | MC-150a |  |  | 5 | 130 | -
LSIS147.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS147.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS147.03 |  | OLR | LSIS | MT-150 |  |  | 5 | 54 - 75 | -
LSIS147.04 |  | OLR | LSIS | MT-150 |  |  | 5 | 63 - 85 | -
LSIS147.05 |  | OLR | LSIS | MT-150 |  |  | 5 | 80 - 105 | -
LSIS147.06 |  | OLR | LSIS | MT-150 |  |  | 5 | 95 - 130 | -
LSIS148 | C [ version C2(b)] | CB | LSIS | UTS150L | 240 | 3 | 150 | 150 | 50 | 240 | 3 | 100 | 130 | 50 | 1785 | 1
|  | MC | LSIS | MC-150a |  |  | 5 | 130 | -
LSIS148.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS148.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS148.03 |  | OLR | LSIS | MT-150 |  |  | 5 | 54 - 75 | -
LSIS148.04 |  | OLR | LSIS | MT-150 |  |  | 5 | 63 - 85 | -
LSIS148.05 |  | OLR | LSIS | MT-150 |  |  | 5 | 80 - 105 | -
LSIS148.06 |  | OLR | LSIS | MT-150 |  |  | 5 | 95 - 130 | -
LSIS149 | C [ version C2(b)] | CB | LSIS | UTS250N | 240 | 3 | 65 | 175 | 50 | 240 | 3 | 65 | 130 | 50 | 7447 | 1
|  | MC | LSIS | MC-150a |  |  | 5 | 130 | -
LSIS149.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS149.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS149.03 |  | OLR | LSIS | MT-150 |  |  | 5 | 54 - 75 | -
LSIS149.04 |  | OLR | LSIS | MT-150 |  |  | 5 | 63 - 85 | -
LSIS149.05 |  | OLR | LSIS | MT-150 |  |  | 5 | 80 - 105 | -
LSIS149.06 |  | OLR | LSIS | MT-150 |  |  | 5 | 95 - 130 | -
LSIS150 | C [ version C2(b)] | CB | LSIS | UTS250L | 240 | 3 | 150 | 175 | 50 | 240 | 3 | 100 | 130 | 50 | 7447 | 1
|  | MC | LSIS | MC-150a |  |  | 5 | 130 | -
LSIS150.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS150.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS150.03 |  | OLR | LSIS | MT-150 |  |  | 5 | 54 - 75 | -
LSIS150.04 |  | OLR | LSIS | MT-150 |  |  | 5 | 63 - 85 | -
LSIS150.05 |  | OLR | LSIS | MT-150 |  |  | 5 | 80 - 105 | -
LSIS150.06 |  | OLR | LSIS | MT-150 |  |  | 5 | 95 - 130 | -
LSIS151 | C [ version C2(b)] | CB | LSIS | UTS250N | 240 | 3 | 65 | 250 | 60 | 240 | 3 | 65 | 154 | 60 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 154 | -
LSIS151.01 |  | OLR | LSIS | MT-225 |  |  | 5 | 65 - 100 | -
LSIS151.02 |  | OLR | LSIS | MT-225 |  |  | 5 | 85 - 125 | -
LSIS151.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS151.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS152 | C [ version C2(b)] | CB | LSIS | UTS250L | 240 | 3 | 150 | 250 | 60 | 240 | 3 | 100 | 154 | 60 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 154 | -
LSIS152.01 |  | OLR | LSIS | MT-225 |  |  | 5 | 65 - 100 | -
LSIS152.02 |  | OLR | LSIS | MT-225 |  |  | 5 | 85 - 125 | -
LSIS152.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS152.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS153 | C [ version C2(b)] | CB | LSIS | UTS250N | 240 | 3 | 65 | 250 | 75 | 240 | 3 | 65 | 192 | 75 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 192 | -
LSIS153.01 |  | OLR | LSIS | MT-225 |  |  | 5 | 65 - 100 | -
LSIS153.02 |  | OLR | LSIS | MT-225 |  |  | 5 | 85 - 125 | -
LSIS153.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS153.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS153.05 |  | OLR | LSIS | MT-225 |  |  | 10 | 160 - 240 | -
LSIS154 | C [ version C2(b)] | CB | LSIS | UTS250L | 240 | 3 | 150 | 250 | 75 | 240 | 3 | 100 | 192 | 75 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 192 | -
LSIS154.01 |  | OLR | LSIS | MT-225 |  |  | 5 | 65 - 100 | -
LSIS154.02 |  | OLR | LSIS | MT-225 |  |  | 5 | 85 - 125 | -
LSIS154.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS154.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS154.05 |  | OLR | LSIS | MT-225 |  |  | 10 | 160 - 240 | -
LSIS155 | C [ version C2(b)] | CB | LSIS | UTS400N | 240 | 3 | 65 | 300 | 100 | 240 | 3 | 65 | 154 | 60 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 154 | -
LSIS155.01 |  | OLR | LSIS | MT-225 |  |  | 5 | 65 - 100 | -
LSIS155.02 |  | OLR | LSIS | MT-225 |  |  | 5 | 85 - 125 | -
LSIS155.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS155.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS156 | C [ version C2(b)] | CB | LSIS | UTS400L | 240 | 3 | 150 | 300 | 100 | 240 | 3 | 100 | 154 | 60 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 154 | -
LSIS156.01 |  | OLR | LSIS | MT-225 |  |  | 5 | 65 - 100 | -
LSIS156.02 |  | OLR | LSIS | MT-225 |  |  | 5 | 85 - 125 | -
LSIS156.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS156.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS157 | C [ version C2(b)] | CB | LSIS | UTS400N | 240 | 3 | 65 | 300 | 100 | 240 | 3 | 65 | 192 | 75 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 192 | -
LSIS157.01 |  | OLR | LSIS | MT-225 |  |  | 5 | 65 - 100 | -
LSIS157.02 |  | OLR | LSIS | MT-225 |  |  | 5 | 85 - 125 | -
LSIS157.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS157.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS157.05 |  | OLR | LSIS | MT-225 |  |  | 10 | 160 - 240 | -
LSIS158 | C [ version C2(b)] | CB | LSIS | UTS400L | 240 | 3 | 150 | 300 | 100 | 240 | 3 | 100 | 192 | 75 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 192 | -
LSIS158.01 |  | OLR | LSIS | MT-225 |  |  | 5 | 65 - 100 | -
LSIS158.02 |  | OLR | LSIS | MT-225 |  |  | 5 | 85 - 125 | -
LSIS158.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS158.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS158.05 |  | OLR | LSIS | MT-225 |  |  | 10 | 160 - 240 | -
LSIS159 | C [ version C2(b)] | CB | LSIS | UTS400N | 240 | 3 | 65 | 400 | 100 | 240 | 3 | 65 | 248 | 100 | 7447 | 1
|  | MC | LSIS | MC-265a | 240 | 3 | 10 | 248 | - | 240 | 3
LSIS159.01 |  | OLR | LSIS | MT-400 |  |  | 5 | 85 - 125 | -
LSIS159.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS159.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS159.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS159.05 |  | OLR | LSIS | MT-400 |  |  | 10 | 200 - 330 | -
LSIS160 | C [ version C2(b)] | CB | LSIS | UTS400L | 240 | 3 | 150 | 400 | 100 | 240 | 3 | 100 | 248 | 100 | 7447 | 1
|  | MC | LSIS | MC-265a | 240 | 3 | 10 | 248 | - | 240 | 3
LSIS160.01 |  | OLR | LSIS | MT-400 |  |  | 5 | 85 - 125 | -
LSIS160.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS160.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS160.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS160.05 |  | OLR | LSIS | MT-400 |  |  | 10 | 200 - 330 | -
LSIS161 | C [ version C2(b)] | CB | LSIS | UTS400N | 240 | 3 | 65 | 400 | 125 | 240 | 3 | 65 | 248 | 100 | 7447 | 1
|  | MC | LSIS | MC-330a | 240 | 3 | 10 | 312 | - | 240 | 3
LSIS161.01 |  | OLR | LSIS | MT-400 |  |  | 5 | 85 - 125 | -
LSIS161.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS161.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS161.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS161.05 |  | OLR | LSIS | MT-400 |  |  | 10 | 200 - 330 | -
LSIS162 | C [ version C2(b)] | CB | LSIS | UTS400L | 240 | 3 | 150 | 400 | 125 | 240 | 3 | 100 | 248 | 100 | 7447 | 1
|  | MC | LSIS | MC-330a | 240 | 3 | 10 | 312 | - | 240 | 3
LSIS162.01 |  | OLR | LSIS | MT-400 |  |  | 5 | 85 - 125 | -
LSIS162.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS162.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS162.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS162.05 |  | OLR | LSIS | MT-400 |  |  | 10 | 200 - 330 | -
LSIS163 | C [ version C2(b)] | CB | LSIS | UTS600N | 240 | 3 | 65 | 500 | 200 | 240 | 3 | 65 | 360 | 150 | 7447 | 1
|  | MC | LSIS | MC-400a |  |  | 10 | 360 | -
LSIS163.01 |  | OLR | LSIS | MT-400 |  |  | 5 | 85 - 125 | -
LSIS163.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS163.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS163.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS163.05 |  | OLR | LSIS | MT-400 |  |  | 10 | 200 - 330 | -
LSIS163.06 |  | OLR | LSIS | MT-400 |  |  | 10 | 260 - 400 | -
LSIS164 | C [ version C2(b)] | CB | LSIS | UTS600L | 240 | 3 | 150 | 500 | 200 | 240 | 3 | 100 | 360 | 150 | 7447 | 1
|  | MC | LSIS | MC-400a |  |  | 10 | 360 | -
LSIS164.01 |  | OLR | LSIS | MT-400 |  |  | 5 | 85 - 125 | -
LSIS164.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS164.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS164.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS164.05 |  | OLR | LSIS | MT-400 |  |  | 10 | 200 - 330 | -
LSIS164.06 |  | OLR | LSIS | MT-400 |  |  | 10 | 260 - 400 | -
LSIS165 | C [ version C2(b)] | CB | LSIS | UTS800L | 240 | 3 | 150 | 800 | 200 | 240 | 3 | 100 | 480 | 200 | 15980 | 1
|  | MC | LSIS | MC-500a |  |  | 10 | 480 | -
LSIS165.01 |  | OLR | LSIS | MT-800 |  |  | 10 | 200 - 330 | -
LSIS165.02 |  | OLR | LSIS | MT-800 |  |  | 10 | 260 - 400 | -
LSIS165.03 |  | OLR | LSIS | MT-800 |  |  | 10 | 400 - 600 | -
LSIS166 | C [ version C2(b)] | CB | LSIS | UTS800L | 240 | 3 | 150 | 800 | 250 | 240 | 3 | 100 | 604 | 250 | 15980 | 1
|  | MC | LSIS | MC-630a |  |  | 18 | 604 | -
LSIS166.01 |  | OLR | LSIS | MT-800 |  |  | 10 | 200 - 330 | -
LSIS166.02 |  | OLR | LSIS | MT-800 |  |  | 10 | 260 - 400 | -
LSIS166.03 |  | OLR | LSIS | MT-800 |  |  | 18 | 400 - 600 | -
LSIS166.04 |  | OLR | LSIS | MT-800 |  |  | 18 | 520 - 800 | -
LSIS167 | C [ version C2(b)] | CB | LSIS | UTE100E | 480 | 3 | 25 | 15 | 10 | 480 | 3 | 25 | 7.6 | 5 | 1418 | 1
|  | MC | LSIS | MC-6a |  |  | 5 | 7.6 | -
LSIS167.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS167.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS167.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS167.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS167.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS167.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS167.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS167.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS167.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS167.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS167.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS167.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS168 | C [ version C2(b)] | CB | LSIS | UTE100N | 480 | 3 | 35 | 15 | 10 | 480 | 3 | 35 | 7.6 | 5 | 1418 | 1
|  | MC | LSIS | MC-6a |  |  | 5 | 7.6 | -
LSIS168.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS168.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS168.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS168.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS168.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS168.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS168.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS168.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS168.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS168.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS168.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS168.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS169 | C [ version C2(b)] | CB | LSIS | UTE100E | 480 | 3 | 25 | 20 | 10 | 480 | 3 | 25 | 7.6 | 5 | 1418 | 1
|  | MC | LSIS | MC-9a |  |  | 5 | 7.6 | -
LSIS169.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS169.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS169.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS169.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS169.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS169.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS169.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS169.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS169.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS169.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS169.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS169.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS170 | C [ version C2(b)] | CB | LSIS | UTE100N | 480 | 3 | 35 | 20 | 10 | 480 | 3 | 35 | 7.6 | 5 | 1418 | 1
|  | MC | LSIS | MC-9a |  |  | 5 | 7.6 | -
LSIS170.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS170.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS170.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS170.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS170.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS170.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS170.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS170.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS170.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS170.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS170.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS170.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS171 | C [ version C2(b)] | CB | LSIS | UTE100E | 480 | 3 | 25 | 30 | 10 | 480 | 3 | 25 | 11 | 7.5 | 1418 | 1
|  | MC | LSIS | MC-12a |  |  | 5 | 11 | -
LSIS171.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS171.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS171.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS171.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS171.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS171.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS171.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS171.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS171.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS171.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS171.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS171.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS171.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS172 | C [ version C2(b)] | CB | LSIS | UTE100N | 480 | 3 | 35 | 30 | 10 | 480 | 3 | 35 | 11 | 7.5 | 1418 | 1
|  | MC | LSIS | MC-12a |  |  | 5 | 11 | -
LSIS172.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS172.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS172.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS172.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS172.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS172.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS172.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS172.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS172.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS172.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS172.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS172.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS172.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS173 | C [ version C2(b)] | CB | LSIS | UTE100E | 480 | 3 | 25 | 40 | 10 | 480 | 3 | 25 | 14 | 10 | 1418 | 1
|  | MC | LSIS | MC-18a |  |  | 5 | 14 | -
LSIS173.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS173.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS173.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS173.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS173.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS173.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS173.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS173.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS173.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS173.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS173.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS173.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS173.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS173.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS174 | C [ version C2(b)] | CB | LSIS | UTE100N | 480 | 3 | 35 | 40 | 10 | 480 | 3 | 35 | 14 | 10 | 1418 | 1
|  | MC | LSIS | MC-18a |  |  | 5 | 14 | -
LSIS174.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS174.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS174.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS174.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS174.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS174.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS174.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS174.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS174.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS174.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS174.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS174.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS174.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS174.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS175 | C [ version C2(b)] | CB | LSIS | UTS150N | 480 | 3 | 35 | 40 | 25 | 480 | 3 | 35 | 14 | 10 | 1785 | 1
|  | MC | LSIS | MC-18a |  |  | 5 | 14 | -
LSIS175.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS175.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS175.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS175.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS175.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS175.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS175.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS175.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS175.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS175.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS175.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS175.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS175.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS175.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS176 | C [ version C2(b)] | CB | LSIS | UTS150H | 480 | 3 | 65 | 40 | 25 | 480 | 3 | 65 | 14 | 10 | 1785 | 1
|  | MC | LSIS | MC-18a |  |  | 5 | 14 | -
LSIS176.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS176.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS176.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS176.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS176.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS176.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS176.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS176.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS176.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS176.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS176.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS176.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS176.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS176.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS177 | C [ version C2(b)] | CB | LSIS | UTS150L | 480 | 3 | 100 | 40 | 25 | 480 | 3 | 100 | 14 | 10 | 1785 | 1
|  | MC | LSIS | MC-18a |  |  | 5 | 14 | -
LSIS177.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS177.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS177.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS177.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS177.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS177.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS177.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS177.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS177.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS177.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS177.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS177.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS177.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS177.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS178 | C [ version C2(b)] | CB | LSIS | UTE100E | 480 | 3 | 25 | 15 | 10 | 480 | 3 | 25 | 7.6 | 5 | 1418 | 1
|  | MC | LSIS | MC-9b |  |  | 5 | 7.6 | -
LSIS178.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS178.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS178.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS178.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS178.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS178.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS178.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS178.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS178.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS178.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS178.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS178.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS179 | C [ version C2(b)] | CB | LSIS | UTE100N | 480 | 3 | 35 | 15 | 10 | 480 | 3 | 35 | 7.6 | 5 | 1418 | 1
|  | MC | LSIS | MC-9b |  |  | 5 | 7.6 | -
LSIS179.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS179.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS179.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS179.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS179.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS179.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS179.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS179.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS179.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS179.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS179.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS179.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS180 | C [ version C2(b)] | CB | LSIS | UTE100E | 480 | 3 | 25 | 20 | 10 | 480 | 3 | 25 | 11 | 7.5 | 1418 | 1
|  | MC | LSIS | MC-12b |  |  | 5 | 11 | -
LSIS180.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS180.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS180.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS180.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS180.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS180.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS180.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS180.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS180.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS180.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS180.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS180.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS180.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS181 | C [ version C2(b)] | CB | LSIS | UTE100N | 480 | 3 | 35 | 20 | 10 | 480 | 3 | 35 | 11 | 7.5 | 1418 | 1
|  | MC | LSIS | MC-12b |  |  | 5 | 11 | -
LSIS181.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS181.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS181.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS181.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS181.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS181.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS181.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS181.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS181.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS181.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS181.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS181.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS181.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS182 | C [ version C2(b)] | CB | LSIS | UTE100E | 480 | 3 | 25 | 30 | 10 | 480 | 3 | 25 | 14 | 10 | 1418 | 1
|  | MC | LSIS | MC-18b |  |  | 5 | 14 | -
LSIS182.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS182.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS182.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS182.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS182.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS182.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS182.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS182.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS182.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS182.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS182.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS182.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS182.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS182.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS183 | C [ version C2(b)] | CB | LSIS | UTE100N | 480 | 3 | 35 | 30 | 10 | 480 | 3 | 35 | 14 | 10 | 1418 | 1
|  | MC | LSIS | MC-18b |  |  | 5 | 14 | -
LSIS183.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS183.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS183.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS183.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS183.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS183.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS183.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS183.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS183.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS183.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS183.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS183.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS183.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS183.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS184 | C [ version C2(b)] | CB | LSIS | UTE100E | 480 | 3 | 25 | 40 | 15 | 480 | 3 | 25 | 21 | 15 | 1418 | 1
|  | MC | LSIS | MC-22b |  |  | 5 | 21 | -
LSIS184.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS184.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS184.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS184.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS184.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS184.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS184.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS184.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS184.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS184.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS184.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS184.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS184.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS184.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS184.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS184.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS185 | C [ version C2(b)] | CB | LSIS | UTE100N | 480 | 3 | 35 | 40 | 15 | 480 | 3 | 35 | 21 | 15 | 1418 | 1
|  | MC | LSIS | MC-22b |  |  | 5 | 21 | -
LSIS185.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS185.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS185.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS185.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS185.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS185.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS185.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS185.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS185.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS185.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS185.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS185.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS185.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS185.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS185.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS185.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS186 | C [ version C2(b)] | CB | LSIS | UTS150N | 480 | 3 | 35 | 40 | 30 | 480 | 3 | 35 | 21 | 15 | 1785 | 1
|  | MC | LSIS | MC-22b |  |  | 5 | 21 | -
LSIS186.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS186.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS186.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS186.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS186.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS186.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS186.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS186.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS186.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS186.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS186.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS186.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS186.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS186.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS186.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS186.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS187 | C [ version C2(b)] | CB | LSIS | UTS150H | 480 | 3 | 65 | 40 | 30 | 480 | 3 | 65 | 21 | 15 | 1785 | 1
|  | MC | LSIS | MC-22b |  |  | 5 | 21 | -
LSIS187.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS187.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS187.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS187.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS187.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS187.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS187.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS187.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS187.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS187.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS187.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS187.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS187.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS187.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS187.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS187.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS188 | C [ version C2(b)] | CB | LSIS | UTS150L | 480 | 3 | 100 | 40 | 30 | 480 | 3 | 100 | 21 | 15 | 1785 | 1
|  | MC | LSIS | MC-22b |  |  | 5 | 21 | -
LSIS188.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS188.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS188.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS188.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS188.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS188.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS188.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS188.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS188.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS188.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS188.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS188.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS188.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS188.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS188.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS188.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS189 | C [ version C2(b)] | CB | LSIS | UTE100E | 480 | 3 | 25 | 50 | 20 | 480 | 3 | 25 | 27 | 20 | 1418 | 1
|  | MC | LSIS | MC-32a |  |  | 5 | 27 | -
LSIS189.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS189.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS189.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS189.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS189.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS189.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS189.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS189.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS189.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS189.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS189.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS189.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS189.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS189.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS189.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS189.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS189.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS190 | C [ version C2(b)] | CB | LSIS | UTE100N | 480 | 3 | 35 | 50 | 20 | 480 | 3 | 35 | 27 | 20 | 1418 | 1
|  | MC | LSIS | MC-32a |  |  | 5 | 27 | -
LSIS190.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS190.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS190.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS190.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS190.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS190.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS190.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS190.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS190.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS190.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS190.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS190.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS190.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS190.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS190.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS190.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS190.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS191 | C [ version C2(b)] | CB | LSIS | UTS150N | 480 | 3 | 35 | 50 | 30 | 480 | 3 | 35 | 27 | 20 | 1785 | 1
|  | MC | LSIS | MC-32a |  |  | 5 | 27 | -
LSIS191.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS191.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS191.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS191.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS191.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS191.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS191.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS191.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS191.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS191.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS191.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS191.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS191.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS191.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS191.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS191.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS191.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS192 | C [ version C2(b)] | CB | LSIS | UTS150H | 480 | 3 | 65 | 50 | 30 | 480 | 3 | 65 | 27 | 20 | 1785 | 1
|  | MC | LSIS | MC-32a |  |  | 5 | 27 | -
LSIS192.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS192.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS192.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS192.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS192.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS192.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS192.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS192.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS192.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS192.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS192.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS192.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS192.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS192.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS192.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS192.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS192.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS193 | C [ version C2(b)] | CB | LSIS | UTS150L | 480 | 3 | 100 | 50 | 30 | 480 | 3 | 100 | 27 | 20 | 1785 | 1
|  | MC | LSIS | MC-32a |  |  | 5 | 27 | -
LSIS193.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS193.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS193.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS193.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS193.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS193.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS193.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS193.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS193.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS193.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS193.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS193.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS193.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS193.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS193.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS193.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS193.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS194 | C [ version C2(b)] | CB | LSIS | UTE100E | 480 | 3 | 25 | 60 | 30 | 480 | 3 | 25 | 40 | 30 | 1418 | 1
|  | MC | LSIS | MC-40a |  |  | 5 | 40 | -
LSIS194.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS194.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS194.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS194.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS194.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS194.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS194.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS194.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS194.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS194.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS194.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS194.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS194.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS194.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS194.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS194.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS194.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS194.18 |  | OLR | LSIS | MT-32 |  |  | 5 | 28 - 40 | -
LSIS195 | C [ version C2(b)] | CB | LSIS | UTE100N | 480 | 3 | 35 | 60 | 30 | 480 | 3 | 35 | 40 | 30 | 1418 | 1
|  | MC | LSIS | MC-40a |  |  | 5 | 40 | -
LSIS195.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS195.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS195.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS195.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS195.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS195.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS195.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS195.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS195.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS195.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS195.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS195.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS195.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS195.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS195.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS195.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS195.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS195.18 |  | OLR | LSIS | MT-32 |  |  | 5 | 28 - 40 | -
LSIS196 | C [ version C2(b)] | CB | LSIS | UTS150N | 480 | 3 | 35 | 60 | 30 | 480 | 3 | 35 | 40 | 30 | 1785 | 1
|  | MC | LSIS | MC-40a |  |  | 5 | 40 | -
LSIS196.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS196.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS196.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS196.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS196.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS196.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS196.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS196.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS196.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS196.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS196.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS196.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS196.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS196.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS196.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS196.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS196.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS196.18 |  | OLR | LSIS | MT-32 |  |  | 5 | 28 - 40 | -
LSIS197 | C [ version C2(b)] | CB | LSIS | UTS150H | 480 | 3 | 65 | 60 | 30 | 480 | 3 | 65 | 40 | 30 | 1785 | 1
|  | MC | LSIS | MC-40a |  |  | 5 | 40 | -
LSIS197.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS197.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS197.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS197.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS197.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS197.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS197.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS197.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS197.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS197.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS197.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS197.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS197.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS197.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS197.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS197.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS197.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS197.18 |  | OLR | LSIS | MT-32 |  |  | 5 | 28 - 40 | -
LSIS198 | C [ version C2(b)] | CB | LSIS | UTS150L | 480 | 3 | 100 | 60 | 30 | 480 | 3 | 100 | 40 | 30 | 1785 | 1
|  | MC | LSIS | MC-40a |  |  | 5 | 40 | -
LSIS198.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS198.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS198.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS198.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS198.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS198.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS198.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS198.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS198.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS198.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS198.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS198.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS198.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS198.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS198.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS198.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS198.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS198.18 |  | OLR | LSIS | MT-32 |  |  | 5 | 28 - 40 | -
LSIS199 | C [ version C2(b)] | CB | LSIS | UTE100E | 480 | 3 | 25 | 80 | 40 | 480 | 3 | 25 | 52 | 40 | 1418 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 52 | -
LSIS199.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS199.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS199.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS199.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS199.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS199.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS199.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS199.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS199.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS199.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS199.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS199.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS200 | C [ version C2(b)] | CB | LSIS | UTE100N | 480 | 3 | 35 | 80 | 40 | 480 | 3 | 35 | 52 | 40 | 1418 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 52 | -
LSIS200.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS200.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS200.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS200.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS200.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS200.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS200.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS200.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS200.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS200.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS200.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS200.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS201 | C [ version C2(b)] | CB | LSIS | UTS150N | 480 | 3 | 35 | 80 | 40 | 480 | 3 | 35 | 52 | 40 | 1785 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 52 | -
LSIS201.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS201.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS201.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS201.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS201.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS201.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS201.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS201.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS201.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS201.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS201.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS201.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS202 | C [ version C2(b)] | CB | LSIS | UTS150H | 480 | 3 | 65 | 80 | 40 | 480 | 3 | 65 | 52 | 40 | 1785 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 52 | -
LSIS202.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS202.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS202.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS202.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS202.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS202.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS202.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS202.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS202.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS202.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS202.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS202.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS203 | C [ version C2(b)] | CB | LSIS | UTS150L | 480 | 3 | 100 | 80 | 40 | 480 | 3 | 100 | 52 | 40 | 1785 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 52 | -
LSIS203.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS203.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS203.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS203.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS203.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS203.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS203.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS203.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS203.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS203.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS203.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS203.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS204 | C [ version C2(b)] | CB | LSIS | UTE100E | 480 | 3 | 25 | 100 | 50 | 480 | 3 | 25 | 65 | 50 | 1418 | 1
|  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS204.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS204.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS204.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS204.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS204.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS204.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS204.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS204.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS204.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS204.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS204.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS204.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS205 | C [ version C2(b)] | CB | LSIS | UTE100N | 480 | 3 | 35 | 100 | 50 | 480 | 3 | 35 | 65 | 50 | 1418 | 1
|  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS205.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS205.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS205.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS205.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS205.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS205.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS205.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS205.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS205.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS205.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS205.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS205.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS206 | C [ version C2(b)] | CB | LSIS | UTS150N | 480 | 3 | 35 | 100 | 60 | 480 | 3 | 35 | 65 | 50 | 1785 | 1
|  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS206.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS206.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS206.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS206.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS206.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS206.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS206.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS206.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS206.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS206.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS206.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS206.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS207 | C [ version C2(b)] | CB | LSIS | UTS150H | 480 | 3 | 65 | 100 | 60 | 480 | 3 | 65 | 65 | 50 | 1785 | 1
|  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS207.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS207.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS207.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS207.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS207.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS207.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS207.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS207.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS207.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS207.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS207.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS207.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS208 | C [ version C2(b)] | CB | LSIS | UTS150L | 480 | 3 | 100 | 100 | 60 | 480 | 3 | 100 | 65 | 50 | 1785 | 1
|  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS208.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS208.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS208.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS208.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS208.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS208.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS208.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS208.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS208.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS208.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS208.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS208.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS209 | C [ version C2(b)] | CB | LSIS | UTS150N | 480 | 3 | 35 | 150 | 60 | 480 | 3 | 35 | 65 | 50 | 1785 | 1
|  | MC | LSIS | MC-75a |  |  | 5 | 65 | -
LSIS209.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS209.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS209.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS209.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS209.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS209.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS209.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS209.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS209.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS209.10 |  | OLR | LSIS | MT-95 |  |  | 5 | 54 - 75 | -
LSIS210 | C [ version C2(b)] | CB | LSIS | UTS150H | 480 | 3 | 65 | 150 | 60 | 480 | 3 | 65 | 65 | 50 | 1785 | 1
|  | MC | LSIS | MC-75a |  |  | 5 | 65 | -
LSIS210.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS210.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS210.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS210.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS210.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS210.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS210.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS210.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS210.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS210.10 |  | OLR | LSIS | MT-95 |  |  | 5 | 54 - 75 | -
LSIS211 | C [ version C2(b)] | CB | LSIS | UTS150L | 480 | 3 | 100 | 150 | 60 | 480 | 3 | 100 | 65 | 50 | 1785 | 1
|  | MC | LSIS | MC-75a |  |  | 5 | 65 | -
LSIS211.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS211.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS211.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS211.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS211.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS211.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS211.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS211.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS211.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS211.10 |  | OLR | LSIS | MT-95 |  |  | 5 | 54 - 75 | -
LSIS212 | C [ version C2(b)] | CB | LSIS | UTS150N | 480 | 3 | 35 | 150 | 60 | 480 | 3 | 35 | 77 | 60 | 1785 | 1
|  | MC | LSIS | MC-85a |  |  | 10 | 77 | -
LSIS212.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS212.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS212.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS212.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS212.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS212.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS212.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS212.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS212.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS212.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS212.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS213 | C [ version C2(b)] | CB | LSIS | UTS150H | 480 | 3 | 65 | 150 | 60 | 480 | 3 | 65 | 77 | 60 | 1785 | 1
|  | MC | LSIS | MC-85a |  |  | 10 | 77 | -
LSIS213.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS213.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS213.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS213.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS213.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS213.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS213.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS213.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS213.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS213.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS213.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS214 | C [ version C2(b)] | CB | LSIS | UTS150L | 480 | 3 | 100 | 150 | 60 | 480 | 3 | 100 | 77 | 60 | 1785 | 1
|  | MC | LSIS | MC-85a |  |  | 10 | 77 | -
LSIS214.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS214.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS214.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS214.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS214.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS214.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS214.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS214.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS214.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS214.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS214.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS215 | C [ version C2(b)] | CB | LSIS | UTS150N | 480 | 3 | 35 | 150 | 75 | 480 | 3 | 35 | 96 | 75 | 1785 | 1
|  | MC | LSIS | MC-100a |  |  | 10 | 96 | -
LSIS215.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS215.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS215.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS215.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS215.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS215.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS215.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS215.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS215.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS215.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS215.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS215.12 |  | OLR | LSIS | MT-95 |  |  | 10 | 70 - 95 | -
LSIS215.13 |  | OLR | LSIS | MT-95 |  |  | 10 | 80 - 100 | -
LSIS216 | C [ version C2(b)] | CB | LSIS | UTS150H | 480 | 3 | 65 | 150 | 75 | 480 | 3 | 65 | 96 | 75 | 1785 | 1
|  | MC | LSIS | MC-100a |  |  | 10 | 96 | -
LSIS216.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS216.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS216.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS216.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS216.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS216.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS216.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS216.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS216.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS216.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS216.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS216.12 |  | OLR | LSIS | MT-95 |  |  | 10 | 70 - 95 | -
LSIS216.13 |  | OLR | LSIS | MT-95 |  |  | 10 | 80 - 100 | -
LSIS217 | C [ version C2(b)] | CB | LSIS | UTS150L | 480 | 3 | 100 | 150 | 75 | 480 | 3 | 100 | 96 | 75 | 1785 | 1
|  | MC | LSIS | MC-100a |  |  | 10 | 96 | -
LSIS217.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS217.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS217.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS217.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS217.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS217.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS217.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS217.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS217.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS217.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS217.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS217.12 |  | OLR | LSIS | MT-95 |  |  | 10 | 70 - 95 | -
LSIS217.13 |  | OLR | LSIS | MT-95 |  |  | 10 | 80 - 100 | -
LSIS218 | C [ version C2(b)] | CB | LSIS | UTS150N | 480 | 3 | 35 | 150 | 75 | 480 | 3 | 35 | 96 | 75 | 1785 | 1
|  | MC | LSIS | MC-130a |  |  | 10 | 96 | -
LSIS218.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS218.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS218.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS218.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS218.05 |  | OLR | LSIS | MT-150 |  |  | 10 | 80 - 105 | -
LSIS218.06 |  | OLR | LSIS | MT-150 |  |  | 10 | 95 - 130 | -
LSIS219 | C [ version C2(b)] | CB | LSIS | UTS150H | 480 | 3 | 65 | 150 | 75 | 480 | 3 | 65 | 96 | 75 | 1785 | 1
|  | MC | LSIS | MC-130a |  |  | 10 | 96 | -
LSIS219.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS219.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS219.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS219.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS219.05 |  | OLR | LSIS | MT-150 |  |  | 10 | 80 - 105 | -
LSIS219.06 |  | OLR | LSIS | MT-150 |  |  | 10 | 95 - 130 | -
LSIS220 | C [ version C2(b)] | CB | LSIS | UTS150L | 480 | 3 | 100 | 150 | 75 | 480 | 3 | 100 | 96 | 75 | 1785 | 1
|  | MC | LSIS | MC-130a |  |  | 10 | 96 | -
LSIS220.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS220.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS220.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS220.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS220.05 |  | OLR | LSIS | MT-150 |  |  | 10 | 80 - 105 | -
LSIS220.06 |  | OLR | LSIS | MT-150 |  |  | 10 | 95 - 130 | -
LSIS221 | C [ version C2(b)] | CB | LSIS | UTS150N | 480 | 3 | 35 | 150 | 100 | 480 | 3 | 35 | 124 | 100 | 1785 | 1
|  | MC | LSIS | MC-150a |  |  | 10 | 124 | -
LSIS221.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS221.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS221.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS221.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS221.05 |  | OLR | LSIS | MT-150 |  |  | 10 | 80 - 105 | -
LSIS221.06 |  | OLR | LSIS | MT-150 |  |  | 10 | 95 - 130 | -
LSIS222 | C [ version C2(b)] | CB | LSIS | UTS150H | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 124 | 100 | 1785 | 1
|  | MC | LSIS | MC-150a |  |  | 10 | 124 | -
LSIS222.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS222.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS222.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS222.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS222.05 |  | OLR | LSIS | MT-150 |  |  | 10 | 80 - 105 | -
LSIS222.06 |  | OLR | LSIS | MT-150 |  |  | 10 | 95 - 130 | -
LSIS223 | C [ version C2(b)] | CB | LSIS | UTS150L | 480 | 3 | 100 | 150 | 100 | 480 | 3 | 100 | 124 | 100 | 1785 | 1
|  | MC | LSIS | MC-150a |  |  | 10 | 124 | -
LSIS223.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS223.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS223.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS223.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS223.05 |  | OLR | LSIS | MT-150 |  |  | 10 | 80 - 105 | -
LSIS223.06 |  | OLR | LSIS | MT-150 |  |  | 10 | 95 - 130 | -
LSIS224 | C [ version C2(b)] | CB | LSIS | UTS250N | 480 | 3 | 35 | 175 | 125 | 480 | 3 | 35 | 124 | 100 | 7447 | 1
|  | MC | LSIS | MC-150a |  |  | 10 | 124 | -
LSIS224.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS224.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS224.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS224.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS224.05 |  | OLR | LSIS | MT-150 |  |  | 10 | 80 - 105 | -
LSIS224.06 |  | OLR | LSIS | MT-150 |  |  | 10 | 95 - 130 | -
LSIS225 | C [ version C2(b)] | CB | LSIS | UTS250H | 480 | 3 | 65 | 175 | 125 | 480 | 3 | 65 | 124 | 100 | 7447 | 1
|  | MC | LSIS | MC-150a |  |  | 10 | 124 | -
LSIS225.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS225.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS225.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS225.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS225.05 |  | OLR | LSIS | MT-150 |  |  | 10 | 80 - 105 | -
LSIS225.06 |  | OLR | LSIS | MT-150 |  |  | 10 | 95 - 130 | -
LSIS226 | C [ version C2(b)] | CB | LSIS | UTS250L | 480 | 3 | 100 | 175 | 125 | 480 | 3 | 100 | 124 | 100 | 7447 | 1
|  | MC | LSIS | MC-150a |  |  | 10 | 124 | -
LSIS226.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS226.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS226.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS226.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS226.05 |  | OLR | LSIS | MT-150 |  |  | 10 | 80 - 105 | -
LSIS226.06 |  | OLR | LSIS | MT-150 |  |  | 10 | 95 - 130 | -
LSIS227 | C [ version C2(b)] | CB | LSIS | UTS250N | 480 | 3 | 35 | 250 | 125 | 480 | 3 | 35 | 156 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 156 | -
LSIS227.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS227.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS227.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS227.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS228 | C [ version C2(b)] | CB | LSIS | UTS250H | 480 | 3 | 65 | 250 | 125 | 480 | 3 | 65 | 156 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 156 | -
LSIS228.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS228.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS228.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS228.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS229 | C [ version C2(b)] | CB | LSIS | UTS250L | 480 | 3 | 100 | 250 | 125 | 480 | 3 | 100 | 156 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 156 | -
LSIS229.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS229.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS229.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS229.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS230 | C [ version C2(b)] | CB | LSIS | UTS250N | 480 | 3 | 35 | 250 | 150 | 480 | 3 | 35 | 180 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 180 | -
LSIS230.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS230.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS230.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS230.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS230.05 |  | OLR | LSIS | MT-225 |  |  | 10 | 160 - 240 | -
LSIS231 | C [ version C2(b)] | CB | LSIS | UTS250H | 480 | 3 | 65 | 250 | 150 | 480 | 3 | 65 | 180 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 180 | -
LSIS231.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS231.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS231.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS231.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS231.05 |  | OLR | LSIS | MT-225 |  |  | 10 | 160 - 240 | -
LSIS232 | C [ version C2(b)] | CB | LSIS | UTS250L | 480 | 3 | 100 | 250 | 150 | 480 | 3 | 100 | 180 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 180 | -
LSIS232.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS232.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS232.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS232.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS232.05 |  | OLR | LSIS | MT-225 |  |  | 10 | 160 - 240 | -
LSIS233 | C [ version C2(b)] | CB | LSIS | UTS400N | 480 | 3 | 35 | 300 | 200 | 480 | 3 | 35 | 156 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 156 | -
LSIS233.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS233.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS233.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS233.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS234 | C [ version C2(b)] | CB | LSIS | UTS400H | 480 | 3 | 65 | 300 | 200 | 480 | 3 | 65 | 156 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 156 | -
LSIS234.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS234.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS234.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS234.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS235 | C [ version C2(b)] | CB | LSIS | UTS400L | 480 | 3 | 100 | 300 | 200 | 480 | 3 | 100 | 156 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 156 | -
LSIS235.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS235.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS235.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS235.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS236 | C [ version C2(b)] | CB | LSIS | UTS400N | 480 | 3 | 35 | 300 | 200 | 480 | 3 | 35 | 180 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 180 | -
LSIS236.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS236.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS236.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS236.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS236.05 |  | OLR | LSIS | MT-225 |  |  | 10 | 160 - 240 | -
LSIS237 | C [ version C2(b)] | CB | LSIS | UTS400H | 480 | 3 | 65 | 300 | 200 | 480 | 3 | 65 | 180 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 180 | -
LSIS237.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS237.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS237.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS237.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS237.05 |  | OLR | LSIS | MT-225 |  |  | 10 | 160 - 240 | -
LSIS238 | C [ version C2(b)] | CB | LSIS | UTS400L | 480 | 3 | 100 | 300 | 200 | 480 | 3 | 100 | 180 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 180 | -
LSIS238.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS238.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS238.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS238.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS238.05 |  | OLR | LSIS | MT-225 |  |  | 10 | 160 - 240 | -
LSIS239 | C [ version C2(b)] | CB | LSIS | UTS400N | 480 | 3 | 35 | 400 | 200 | 480 | 3 | 35 | 240 | 200 | 7447 | 1
|  | MC | LSIS | MC-265a | 240 | 3 | 10 | 240 | - | 240 | 3
LSIS239.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS239.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS239.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS239.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS239.05 |  | OLR | LSIS | MT-400 |  |  | 10 | 200 - 330 | -
LSIS240 | C [ version C2(b)] | CB | LSIS | UTS400H | 480 | 3 | 65 | 400 | 200 | 480 | 3 | 65 | 240 | 200 | 7447 | 1
|  | MC | LSIS | MC-265a | 240 | 3 | 10 | 240 | - | 240 | 3
LSIS240.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS240.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS240.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS240.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS240.05 |  | OLR | LSIS | MT-400 |  |  | 10 | 200 - 330 | -
LSIS241 | C [ version C2(b)] | CB | LSIS | UTS400L | 480 | 3 | 100 | 400 | 200 | 480 | 3 | 100 | 240 | 200 | 7447 | 1
|  | MC | LSIS | MC-265a | 240 | 3 | 10 | 240 | - | 240 | 3
LSIS241.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS241.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS241.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS241.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS241.05 |  | OLR | LSIS | MT-400 |  |  | 10 | 200 - 330 | -
LSIS242 | C [ version C2(b)] | CB | LSIS | UTS400N | 480 | 3 | 35 | 400 | 350 | 480 | 3 | 35 | 240 | 200 | 7447 | 1
|  | MC | LSIS | MC-330a | 240 | 3 | 18 | 302 | - | 240 | 3
LSIS242.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS242.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS242.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS242.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS242.05 |  | OLR | LSIS | MT-400 |  |  | 18 | 200 - 330 | -
LSIS243 | C [ version C2(b)] | CB | LSIS | UTS400H | 480 | 3 | 65 | 400 | 350 | 480 | 3 | 65 | 240 | 200 | 7447 | 1
|  | MC | LSIS | MC-330a | 240 | 3 | 18 | 302 | - | 240 | 3
LSIS243.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS243.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS243.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS243.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS243.05 |  | OLR | LSIS | MT-400 |  |  | 18 | 200 - 330 | -
LSIS244 | C [ version C2(b)] | CB | LSIS | UTS400L | 480 | 3 | 100 | 400 | 350 | 480 | 3 | 100 | 240 | 200 | 7447 | 1
|  | MC | LSIS | MC-330a | 240 | 3 | 18 | 302 | - | 240 | 3
LSIS244.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS244.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS244.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS244.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS244.05 |  | OLR | LSIS | MT-400 |  |  | 18 | 200 - 330 | -
LSIS245 | C [ version C2(b)] | CB | LSIS | UTS600N | 480 | 3 | 35 | 500 | 400 | 480 | 3 | 35 | 361 | 300 | 7447 | 1
|  | MC | LSIS | MC-400a |  |  | 18 | 361 | -
LSIS245.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS245.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS245.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS245.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS245.05 |  | OLR | LSIS | MT-400 |  |  | 18 | 200 - 330 | -
LSIS245.06 |  | OLR | LSIS | MT-400 |  |  | 18 | 260 - 400 | -
LSIS246 | C [ version C2(b)] | CB | LSIS | UTS600H | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 361 | 300 | 7447 | 1
|  | MC | LSIS | MC-400a |  |  | 18 | 361 | -
LSIS246.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS246.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS246.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS246.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS246.05 |  | OLR | LSIS | MT-400 |  |  | 18 | 200 - 330 | -
LSIS246.06 |  | OLR | LSIS | MT-400 |  |  | 18 | 260 - 400 | -
LSIS247 | C [ version C2(b)] | CB | LSIS | UTS600L | 480 | 3 | 100 | 500 | 400 | 480 | 3 | 100 | 361 | 300 | 7447 | 1
|  | MC | LSIS | MC-400a |  |  | 18 | 361 | -
LSIS247.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS247.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS247.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS247.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS247.05 |  | OLR | LSIS | MT-400 |  |  | 18 | 200 - 330 | -
LSIS247.06 |  | OLR | LSIS | MT-400 |  |  | 18 | 260 - 400 | -
LSIS248 | C [ version C2(b)] | CB | LSIS | UTS800H | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 477 | 400 | 15980 | 1
|  | MC | LSIS | MC-500a |  |  | 18 | 477 | -
LSIS248.01 |  | OLR | LSIS | MT-800 |  |  | 10 | 200 - 330 | -
LSIS248.02 |  | OLR | LSIS | MT-800 |  |  | 10 | 260 - 400 | -
LSIS248.03 |  | OLR | LSIS | MT-800 |  |  | 18 | 400 - 600 | -
LSIS249 | C [ version C2(b)] | CB | LSIS | UTS800L | 480 | 3 | 100 | 800 | 500 | 480 | 3 | 100 | 477 | 400 | 15980 | 1
|  | MC | LSIS | MC-500a |  |  | 18 | 477 | -
LSIS249.01 |  | OLR | LSIS | MT-800 |  |  | 10 | 200 - 330 | -
LSIS249.02 |  | OLR | LSIS | MT-800 |  |  | 10 | 260 - 400 | -
LSIS249.03 |  | OLR | LSIS | MT-800 |  |  | 18 | 400 - 600 | -
LSIS250 | C [ version C2(b)] | CB | LSIS | UTS800H | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 590 | 500 | 15980 | 1
|  | MC | LSIS | MC-630a |  |  | 30 | 590 | -
LSIS250.01 |  | OLR | LSIS | MT-800 |  |  | 10 | 200 - 330 | -
LSIS250.02 |  | OLR | LSIS | MT-800 |  |  | 10 | 260 - 400 | -
LSIS250.03 |  | OLR | LSIS | MT-800 |  |  | 18 | 400 - 600 | -
LSIS250.04 |  | OLR | LSIS | MT-800 |  |  | 30 | 520 - 800 | -
LSIS251 | C [ version C2(b)] | CB | LSIS | UTS800L | 480 | 3 | 100 | 800 | 500 | 480 | 3 | 100 | 590 | 500 | 15980 | 1
|  | MC | LSIS | MC-630a |  |  | 30 | 590 | -
LSIS251.01 |  | OLR | LSIS | MT-800 |  |  | 10 | 200 - 330 | -
LSIS251.02 |  | OLR | LSIS | MT-800 |  |  | 10 | 260 - 400 | -
LSIS251.03 |  | OLR | LSIS | MT-800 |  |  | 18 | 400 - 600 | -
LSIS251.04 |  | OLR | LSIS | MT-800 |  |  | 30 | 520 - 800 | -
LSIS252 | C [ version C2(b)] | CB | LSIS | UTE100E | 600Y/347 | 3 | 14 | 15 | 10 | 600Y/347 | 3 | 14 | 9 | 7.5 | 1418 | 1
|  | MC | LSIS | MC-6a |  |  | 5 | 9 | -
LSIS252.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS252.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS252.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS252.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS252.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS252.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS252.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS252.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS252.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS252.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS252.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS252.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS253 | C [ version C2(b)] | CB | LSIS | UTE100N | 600Y/347 | 3 | 18 | 15 | 10 | 600Y/347 | 3 | 18 | 9 | 7.5 | 1418 | 1
|  | MC | LSIS | MC-6a |  |  | 5 | 9 | -
LSIS253.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS253.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS253.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS253.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS253.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS253.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS253.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS253.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS253.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS253.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS253.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS253.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS254 | C [ version C2(b)] | CB | LSIS | UTE100E | 600Y/347 | 3 | 14 | 20 | 10 | 600Y/347 | 3 | 14 | 9 | 7.5 | 1418 | 1
|  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS254.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS254.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS254.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS254.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS254.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS254.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS254.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS254.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS254.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS254.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS254.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS254.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS255 | C [ version C2(b)] | CB | LSIS | UTE100N | 600Y/347 | 3 | 18 | 20 | 10 | 600Y/347 | 3 | 18 | 9 | 7.5 | 1418 | 1
|  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS255.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS255.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS255.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS255.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS255.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS255.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS255.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS255.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS255.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS255.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS255.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS255.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS256 | C [ version C2(b)] | CB | LSIS | UTE100E | 600Y/347 | 3 | 14 | 30 | 10 | 600Y/347 | 3 | 14 | 11 | 10 | 1418 | 1
|  | MC | LSIS | MC-12a |  |  | 5 | 11 | -
LSIS256.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS256.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS256.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS256.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS256.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS256.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS256.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS256.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS256.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS256.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS256.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS256.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS256.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS257 | C [ version C2(b)] | CB | LSIS | UTE100N | 600Y/347 | 3 | 18 | 30 | 10 | 600Y/347 | 3 | 18 | 11 | 10 | 1418 | 1
|  | MC | LSIS | MC-12a |  |  | 5 | 11 | -
LSIS257.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS257.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS257.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS257.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS257.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS257.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS257.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS257.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS257.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS257.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS257.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS257.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS257.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS258 | C [ version C2(b)] | CB | LSIS | UTE100E | 600Y/347 | 3 | 14 | 40 | 15 | 600Y/347 | 3 | 14 | 17 | 15 | 1418 | 1
|  | MC | LSIS | MC-18a |  |  | 5 | 17 | -
LSIS258.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS258.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS258.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS258.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS258.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS258.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS258.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS258.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS258.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS258.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS258.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS258.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS258.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS258.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS259 | C [ version C2(b)] | CB | LSIS | UTE100N | 600Y/347 | 3 | 18 | 40 | 15 | 600Y/347 | 3 | 18 | 17 | 15 | 1418 | 1
|  | MC | LSIS | MC-18a |  |  | 5 | 17 | -
LSIS259.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS259.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS259.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS259.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS259.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS259.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS259.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS259.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS259.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS259.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS259.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS259.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS259.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS259.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS260 | C [ version C2(b)] | CB | LSIS | UTS150N | 600 | 3 | 18 | 40 | 30 | 600 | 3 | 18 | 17 | 15 | 1785 | 1
|  | MC | LSIS | MC-18a |  |  | 5 | 17 | -
LSIS260.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS260.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS260.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS260.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS260.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS260.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS260.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS260.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS260.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS260.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS260.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS260.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS260.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS260.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS260 | C [ version C2(b)] | CB | LSIS | UTS150H | 600 | 3 | 35 | 40 | 30 | 600 | 3 | 35 | 17 | 15 | 1785 | 1
|  | MC | LSIS | MC-18a |  |  | 5 | 17 | -
LSIS261.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS261.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS261.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS261.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS261.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS261.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS261.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS261.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS261.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS261.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS261.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS261.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS261.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS261.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS262 | C [ version C2(b)] | CB | LSIS | UTS150L | 600 | 3 | 50 | 40 | 30 | 600 | 3 | 50 | 17 | 15 | 1785 | 1
|  | MC | LSIS | MC-18a |  |  | 5 | 17 | -
LSIS262.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS262.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS262.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS262.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS262.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS262.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS262.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS262.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS262.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS262.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS262.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS262.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS262.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS262.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS263 | C [ version C2(b)] | CB | LSIS | UTE100E | 600Y/347 | 3 | 14 | 15 | 10 | 600Y/347 | 3 | 14 | 9 | 7.5 | 1418 | 1
|  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS263.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS263.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS263.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS263.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS263.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS263.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS263.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS263.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS263.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS263.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS263.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS263.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS264 | C [ version C2(b)] | CB | LSIS | UTE100N | 600Y/347 | 3 | 18 | 15 | 10 | 600Y/347 | 3 | 18 | 9 | 7.5 | 1418 | 1
|  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS264.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS264.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS264.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS264.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS264.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS264.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS264.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS264.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS264.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS264.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS264.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS264.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS265 | C [ version C2(b)] | CB | LSIS | UTE100E | 600Y/347 | 3 | 14 | 20 | 10 | 600Y/347 | 3 | 14 | 11 | 10 | 1418 | 1
|  | MC | LSIS | MC-12b |  |  | 5 | 11 | -
LSIS265.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS265.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS265.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS265.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS265.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS265.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS265.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS265.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS265.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS265.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS265.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS265.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS265.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS266 | C [ version C2(b)] | CB | LSIS | UTE100N | 600Y/347 | 3 | 18 | 20 | 10 | 600Y/347 | 3 | 18 | 11 | 10 | 1418 | 1
|  | MC | LSIS | MC-12b |  |  | 5 | 11 | -
LSIS266.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS266.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS266.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS266.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS266.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS266.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS266.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS266.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS266.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS266.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS266.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS266.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS266.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS267 | C [ version C2(b)] | CB | LSIS | UTE100E | 600Y/347 | 3 | 18 | 30 | 15 | 600Y/347 | 3 | 14 | 17 | 15 | 1418 | 1
|  | MC | LSIS | MC-18b |  |  | 5 | 17 | -
LSIS267.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS267.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS267.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS267.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS267.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS267.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS267.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS267.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS267.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS267.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS267.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS267.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS267.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS267.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS268 | C [ version C2(b)] | CB | LSIS | UTE100N | 600Y/347 | 3 | 18 | 30 | 15 | 600Y/347 | 3 | 18 | 17 | 15 | 1418 | 1
|  | MC | LSIS | MC-18b |  |  | 5 | 17 | -
LSIS268.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS268.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS268.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS268.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS268.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS268.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS268.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS268.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS268.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS268.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS268.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS268.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS268.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS268.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS269 | C [ version C2(b)] | CB | LSIS | UTE100E | 600Y/347 | 3 | 14 | 40 | 20 | 600Y/347 | 3 | 14 | 22 | 20 | 1418 | 1
|  | MC | LSIS | MC-22b |  |  | 5 | 22 | -
LSIS269.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS269.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS269.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS269.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS269.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS269.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS269.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS269.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS269.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS269.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS269.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS269.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS269.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS269.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS269.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS269.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS270 | C [ version C2(b)] | CB | LSIS | UTE100N | 600Y/347 | 3 | 18 | 40 | 20 | 600Y/347 | 3 | 18 | 22 | 20 | 1418 | 1
|  | MC | LSIS | MC-22b |  |  | 5 | 22 | -
LSIS270.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS270.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS270.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS270.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS270.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS270.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS270.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS270.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS270.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS270.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS270.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS270.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS270.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS270.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS270.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS270.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS271 | C [ version C2(b)] | CB | LSIS | UTS150N | 600 | 3 | 18 | 40 | 30 | 600 | 3 | 18 | 22 | 20 | 1785 | 1
|  | MC | LSIS | MC-22b |  |  | 5 | 22 | -
LSIS271.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS271.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS271.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS271.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS271.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS271.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS271.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS271.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS271.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS271.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS271.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS271.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS271.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS271.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS271.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS271.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS272 | C [ version C2(b)] | CB | LSIS | UTS150H | 600 | 3 | 35 | 40 | 30 | 600 | 3 | 35 | 22 | 20 | 1785 | 1
|  | MC | LSIS | MC-22b |  |  | 5 | 22 | -
LSIS272.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS272.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS272.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS272.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS272.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS272.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS272.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS272.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS272.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS272.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS272.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS272.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS272.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS272.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS272.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS272.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS273 | C [ version C2(b)] | CB | LSIS | UTS150L | 600 | 3 | 50 | 40 | 30 | 600 | 3 | 50 | 22 | 20 | 1785 | 1
|  | MC | LSIS | MC-22b |  |  | 5 | 22 | -
LSIS273.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS273.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS273.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS273.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS273.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS273.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS273.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS273.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS273.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS273.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS273.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS273.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS273.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS273.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS273.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS273.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS274 | C [ version C2(b)] | CB | LSIS | UTE100E | 600Y/347 | 3 | 14 | 50 | 25 | 600Y/347 | 3 | 14 | 27 | 25 | 1418 | 1
|  | MC | LSIS | MC-32a |  |  | 5 | 27 | -
LSIS274.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS274.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS274.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS274.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS274.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS274.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS274.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS274.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS274.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS274.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS274.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS274.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS274.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS274.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS274.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS274.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS274.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS275 | C [ version C2(b)] | CB | LSIS | UTE100N | 600Y/347 | 3 | 18 | 50 | 25 | 600Y/347 | 3 | 18 | 27 | 25 | 1418 | 1
|  | MC | LSIS | MC-32a |  |  | 5 | 27 | -
LSIS275.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS275.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS275.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS275.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS275.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS275.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS275.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS275.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS275.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS275.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS275.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS275.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS275.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS275.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS275.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS275.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS275.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS276 | C [ version C2(b)] | CB | LSIS | UTS150N | 600 | 3 | 18 | 50 | 30 | 600 | 3 | 18 | 27 | 25 | 1785 | 1
|  | MC | LSIS | MC-32a |  |  | 5 | 27 | -
LSIS276.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS276.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS276.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS276.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS276.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS276.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS276.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS276.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS276.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS276.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS276.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS276.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS276.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS276.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS276.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS276.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS276.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS277 | C [ version C2(b)] | CB | LSIS | UTS150H | 600 | 3 | 35 | 50 | 30 | 600 | 3 | 35 | 27 | 25 | 1785 | 1
|  | MC | LSIS | MC-32a |  |  | 5 | 27 | -
LSIS277.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS277.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS277.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS277.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS277.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS277.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS277.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS277.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS277.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS277.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS277.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS277.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS277.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS277.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS277.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS277.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS277.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS278 | C [ version C2(b)] | CB | LSIS | UTS150L | 600 | 3 | 50 | 50 | 30 | 600 | 3 | 50 | 27 | 25 | 1785 | 1
|  | MC | LSIS | MC-32a |  |  | 5 | 27 | -
LSIS278.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS278.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS278.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS278.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS278.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS278.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS278.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS278.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS278.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS278.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS278.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS278.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS278.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS278.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS278.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS278.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS278.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS279 | C [ version C2(b)] | CB | LSIS | UTE100E | 600Y/347 | 3 | 14 | 60 | 30 | 600Y/347 | 3 | 14 | 32 | 30 | 1418 | 1
|  | MC | LSIS | MC-40a |  |  | 5 | 32 | -
LSIS279.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS279.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS279.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS279.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS279.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS279.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS279.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS279.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS279.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS279.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS279.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS279.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS279.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS279.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS279.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS279.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS279.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS280 | C [ version C2(b)] | CB | LSIS | UTE100N | 600Y/347 | 3 | 18 | 60 | 30 | 600Y/347 | 3 | 18 | 32 | 30 | 1418 | 1
|  | MC | LSIS | MC-40a |  |  | 5 | 32 | -
LSIS280.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS280.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS280.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS280.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS280.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS280.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS280.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS280.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS280.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS280.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS280.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS280.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS280.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS280.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS280.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS280.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS280.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS281 | C [ version C2(b)] | CB | LSIS | UTS150N | 600 | 3 | 18 | 60 | 30 | 600 | 3 | 18 | 32 | 30 | 1785 | 1
|  | MC | LSIS | MC-40a |  |  | 5 | 32 | -
LSIS281.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS281.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS281.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS281.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS281.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS281.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS281.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS281.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS281.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS281.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS281.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS281.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS281.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS281.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS281.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS281.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS281.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS282 | C [ version C2(b)] | CB | LSIS | UTS150H | 600 | 3 | 35 | 60 | 30 | 600 | 3 | 35 | 32 | 30 | 1785 | 1
|  | MC | LSIS | MC-40a |  |  | 5 | 32 | -
LSIS282.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS282.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS282.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS282.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS282.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS282.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS282.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS282.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS282.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS282.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS282.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS282.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS282.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS282.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS282.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS282.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS282.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS283 | C [ version C2(b)] | CB | LSIS | UTS150L | 600 | 3 | 50 | 60 | 30 | 600 | 3 | 50 | 32 | 30 | 1785 | 1
|  | MC | LSIS | MC-40a |  |  | 5 | 32 | -
LSIS283.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS283.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS283.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS283.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS283.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS283.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS283.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS283.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS283.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS283.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS283.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS283.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS283.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS283.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS283.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS283.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS283.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS284 | C [ version C2(b)] | CB | LSIS | UTE100E | 600Y/347 | 3 | 14 | 80 | 50 | 600Y/347 | 3 | 14 | 52 | 50 | 1418 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 52 | -
LSIS284.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS284.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS284.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS284.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS284.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS284.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS284.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS284.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 26 | -
LSIS284.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS284.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS284.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS284.12 |  | OLR | LSIS | MT-63 |  |  | 10 | 45 - 65 | -
LSIS285 | C [ version C2(b)] | CB | LSIS | UTE100N | 600Y/347 | 3 | 18 | 80 | 50 | 600Y/347 | 3 | 18 | 52 | 50 | 1418 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 52 | -
LSIS285.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS285.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS285.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS285.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS285.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS285.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS285.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS285.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 26 | -
LSIS285.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS285.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS285.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS285.12 |  | OLR | LSIS | MT-63 |  |  | 10 | 45 - 65 | -
LSIS286 | C [ version C2(b)] | CB | LSIS | UTS150N | 600 | 3 | 18 | 80 | 50 | 600 | 3 | 18 | 52 | 50 | 1785 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 52 | -
LSIS286.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS286.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS286.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS286.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS286.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS286.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS286.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS286.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 26 | -
LSIS286.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS286.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS286.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS286.12 |  | OLR | LSIS | MT-63 |  |  | 10 | 45 - 65 | -
LSIS287 | C [ version C2(b)] | CB | LSIS | UTS150H | 600 | 3 | 35 | 80 | 50 | 600 | 3 | 35 | 52 | 50 | 1785 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 52 | -
LSIS287.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS287.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS287.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS287.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS287.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS287.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS287.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS287.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 26 | -
LSIS287.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS287.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS287.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS287.12 |  | OLR | LSIS | MT-63 |  |  | 10 | 45 - 65 | -
LSIS288 | C [ version C2(b)] | CB | LSIS | UTS150L | 600 | 3 | 50 | 80 | 50 | 600 | 3 | 50 | 52 | 50 | 1785 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 52 | -
LSIS288.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS288.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS288.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS288.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS288.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS288.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS288.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS288.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 26 | -
LSIS288.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS288.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS288.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS288.12 |  | OLR | LSIS | MT-63 |  |  | 10 | 45 - 65 | -
LSIS289 | C [ version C2(b)] | CB | LSIS | UTE100E | 600Y/347 | 3 | 14 | 100 | 60 | 600Y/347 | 3 | 14 | 62 | 60 | 1418 | 1
|  | MC | LSIS | MC-65a |  |  | 10 | 62 | -
LSIS289.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS289.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS289.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS289.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS289.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS289.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS289.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS289.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 26 | -
LSIS289.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS289.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS289.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS289.12 |  | OLR | LSIS | MT-63 |  |  | 10 | 45 - 65 | -
LSIS290 | C [ version C2(b)] | CB | LSIS | UTE100N | 600Y/347 | 3 | 18 | 100 | 60 | 600Y/347 | 3 | 18 | 62 | 60 | 1418 | 1
|  | MC | LSIS | MC-65a |  |  | 10 | 62 | -
LSIS290.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS290.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS290.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS290.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS290.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS290.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS290.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS290.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 26 | -
LSIS290.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS290.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS290.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS290.12 |  | OLR | LSIS | MT-63 |  |  | 10 | 45 - 65 | -
LSIS291 | C [ version C2(b)] | CB | LSIS | UTS150N | 600 | 3 | 18 | 100 | 60 | 600 | 3 | 18 | 62 | 60 | 1785 | 1
|  | MC | LSIS | MC-65a |  |  | 10 | 62 | -
LSIS291.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS291.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS291.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS291.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS291.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS291.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS291.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS291.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 26 | -
LSIS291.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS291.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS291.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS291.12 |  | OLR | LSIS | MT-63 |  |  | 10 | 45 - 65 | -
LSIS292 | C [ version C2(b)] | CB | LSIS | UTS150H | 600 | 3 | 35 | 100 | 75 | 600 | 3 | 35 | 62 | 60 | 1785 | 1
|  | MC | LSIS | MC-65a |  |  | 10 | 62 | -
LSIS292.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS292.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS292.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS292.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS292.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS292.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS292.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS292.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 26 | -
LSIS292.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS292.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS292.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS292.12 |  | OLR | LSIS | MT-63 |  |  | 10 | 45 - 65 | -
LSIS293 | C [ version C2(b)] | CB | LSIS | UTS150L | 600 | 3 | 50 | 100 | 75 | 600 | 3 | 50 | 62 | 60 | 1785 | 1
|  | MC | LSIS | MC-65a |  |  | 10 | 62 | -
LSIS293.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS293.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS293.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS293.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS293.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS293.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS293.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS293.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 26 | -
LSIS293.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS293.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS293.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS293.12 |  | OLR | LSIS | MT-63 |  |  | 10 | 45 - 65 | -
LSIS294 | C [ version C2(b)] | CB | LSIS | UTS150N | 600 | 3 | 18 | 150 | 75 | 600 | 3 | 18 | 62 | 60 | 1785 | 1
|  | MC | LSIS | MC-75a |  |  | 10 | 62 | -
LSIS294.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS294.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS294.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS294.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS294.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS294.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS294.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS294.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS294.09 |  | OLR | LSIS | MT-95 |  |  | 10 | 45 - 65 | -
LSIS294.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS295 | C [ version C2(b)] | CB | LSIS | UTS150H | 600 | 3 | 35 | 150 | 75 | 600 | 3 | 35 | 62 | 60 | 1785 | 1
|  | MC | LSIS | MC-75a |  |  | 10 | 62 | -
LSIS295.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS295.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS295.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS295.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS295.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS295.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS295.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS295.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS295.09 |  | OLR | LSIS | MT-95 |  |  | 10 | 45 - 65 | -
LSIS295.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS296 | C [ version C2(b)] | CB | LSIS | UTS150L | 600 | 3 | 50 | 150 | 75 | 600 | 3 | 50 | 62 | 60 | 1785 | 1
|  | MC | LSIS | MC-75a |  |  | 10 | 62 | -
LSIS296.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS296.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS296.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS296.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS296.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS296.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS296.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS296.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS296.09 |  | OLR | LSIS | MT-95 |  |  | 10 | 45 - 65 | -
LSIS296.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS297 | C [ version C2(b)] | CB | LSIS | UTS150N | 600 | 3 | 18 | 150 | 75 | 600 | 3 | 18 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-85a |  |  | 10 | 77 | -
LSIS297.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS297.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS297.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS297.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS297.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS297.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS297.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS297.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS297.09 |  | OLR | LSIS | MT-95 |  |  | 10 | 45 - 65 | -
LSIS297.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS297.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS298 | C [ version C2(b)] | CB | LSIS | UTS150H | 600 | 3 | 35 | 150 | 75 | 600 | 3 | 35 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-85a |  |  | 10 | 77 | -
LSIS298.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS298.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS298.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS298.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS298.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS298.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS298.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS298.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS298.09 |  | OLR | LSIS | MT-95 |  |  | 10 | 45 - 65 | -
LSIS298.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS298.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS299 | C [ version C2(b)] | CB | LSIS | UTS150L | 600 | 3 | 50 | 150 | 75 | 600 | 3 | 50 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-85a |  |  | 10 | 77 | -
LSIS299.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS299.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS299.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS299.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS299.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS299.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS299.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS299.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS299.09 |  | OLR | LSIS | MT-95 |  |  | 10 | 45 - 65 | -
LSIS299.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS299.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS300 | C [ version C2(b)] | CB | LSIS | UTS150N | 600 | 3 | 18 | 150 | 75 | 600 | 3 | 18 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-100a |  |  | 10 | 77 | -
LSIS300.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS300.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS300.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS300.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS300.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS300.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS300.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS300.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS300.09 |  | OLR | LSIS | MT-95 |  |  | 10 | 45 - 65 | -
LSIS300.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS300.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS301 | C [ version C2(b)] | CB | LSIS | UTS150H | 600 | 3 | 35 | 150 | 75 | 600 | 3 | 35 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-100a |  |  | 10 | 77 | -
LSIS301.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS301.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS301.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS301.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS301.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS301.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS301.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS301.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS301.09 |  | OLR | LSIS | MT-95 |  |  | 10 | 45 - 65 | -
LSIS301.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS301.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS302 | C [ version C2(b)] | CB | LSIS | UTS150L | 600 | 3 | 50 | 150 | 75 | 600 | 3 | 50 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-100a |  |  | 10 | 77 | -
LSIS302.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS302.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS302.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS302.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS302.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS302.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS302.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS302.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS302.09 |  | OLR | LSIS | MT-95 |  |  | 10 | 45 - 65 | -
LSIS302.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS302.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS303 | C [ version C2(b)] | CB | LSIS | UTS150N | 600 | 3 | 18 | 150 | 75 | 600 | 3 | 18 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-130a |  |  | 10 | 77 | -
LSIS303.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS303.02 |  | OLR | LSIS | MT-150 |  |  | 10 | 45 - 65 | -
LSIS303.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS303.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS304 | C [ version C2(b)] | CB | LSIS | UTS150H | 600 | 3 | 35 | 150 | 75 | 600 | 3 | 35 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-130a |  |  | 10 | 77 | -
LSIS304.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS304.02 |  | OLR | LSIS | MT-150 |  |  | 10 | 45 - 65 | -
LSIS304.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS304.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS305 | C [ version C2(b)] | CB | LSIS | UTS150L | 600 | 3 | 50 | 150 | 75 | 600 | 3 | 50 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-130a |  |  | 10 | 77 | -
LSIS305.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS305.02 |  | OLR | LSIS | MT-150 |  |  | 10 | 45 - 65 | -
LSIS305.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS305.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS306 | C [ version C2(b)] | CB | LSIS | UTS150N | 600 | 3 | 18 | 150 | 75 | 600 | 3 | 18 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-150a |  |  | 10 | 77 | -
LSIS306.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS306.02 |  | OLR | LSIS | MT-150 |  |  | 10 | 45 - 65 | -
LSIS306.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS306.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS307 | C [ version C2(b)] | CB | LSIS | UTS150H | 600 | 3 | 35 | 150 | 75 | 600 | 3 | 35 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-150a |  |  | 10 | 77 | -
LSIS307.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS307.02 |  | OLR | LSIS | MT-150 |  |  | 10 | 45 - 65 | -
LSIS307.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS307.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS308 | C [ version C2(b)] | CB | LSIS | UTS150L | 600 | 3 | 50 | 150 | 75 | 600 | 3 | 50 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-150a |  |  | 10 | 77 | -
LSIS308.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS308.02 |  | OLR | LSIS | MT-150 |  |  | 10 | 45 - 65 | -
LSIS308.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS308.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS309 | C [ version C2(b)] | CB | LSIS | UTS250N | 600 | 3 | 18 | 250 | 150 | 600 | 3 | 18 | 125 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 125 | -
LSIS309.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS309.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS309.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS309.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS310 | C [ version C2(b)] | CB | LSIS | UTS250H | 600 | 3 | 35 | 250 | 150 | 600 | 3 | 35 | 125 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 125 | -
LSIS310.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS310.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS310.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS310.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS311 | C [ version C2(b)] | CB | LSIS | UTS250L | 600 | 3 | 50 | 250 | 150 | 600 | 3 | 50 | 125 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 125 | -
LSIS311.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS311.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS311.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS311.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS312 | C [ version C2(b)] | CB | LSIS | UTS250N | 600 | 3 | 18 | 250 | 150 | 600 | 3 | 18 | 144 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 144 | -
LSIS312.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS312.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS312.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS312.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS313 | C [ version C2(b)] | CB | LSIS | UTS250H | 600 | 3 | 35 | 250 | 150 | 600 | 3 | 35 | 144 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 144 | -
LSIS313.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS313.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS313.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS313.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS314 | C [ version C2(b)] | CB | LSIS | UTS250L | 600 | 3 | 50 | 300 | 150 | 600 | 3 | 50 | 144 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 144 | -
LSIS314.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS314.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS314.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS314.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS315 | C [ version C2(b)] | CB | LSIS | UTS400N | 600 | 3 | 18 | 300 | 250 | 600 | 3 | 18 | 125 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 125 | -
LSIS315.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS315.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS315.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS315.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS316 | C [ version C2(b)] | CB | LSIS | UTS400H | 600 | 3 | 35 | 300 | 250 | 600 | 3 | 35 | 125 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 125 | -
LSIS316.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS316.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS316.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS316.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS317 | C [ version C2(b)] | CB | LSIS | UTS400L | 600 | 3 | 50 | 300 | 250 | 600 | 3 | 50 | 125 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 125 | -
LSIS317.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS317.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS317.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS317.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS318 | C [ version C2(b)] | CB | LSIS | UTS400N | 600 | 3 | 18 | 300 | 250 | 600 | 3 | 18 | 144 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 144 | -
LSIS318.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS318.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS318.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS318.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS319 | C [ version C2(b)] | CB | LSIS | UTS400H | 600 | 3 | 35 | 300 | 250 | 600 | 3 | 35 | 144 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 144 | -
LSIS319.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS319.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS319.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS319.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS320 | C [ version C2(b)] | CB | LSIS | UTS400L | 600 | 3 | 50 | 300 | 250 | 600 | 3 | 50 | 144 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 144 | -
LSIS320.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS320.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS320.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS320.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS321 | C [ version C2(b)] | CB | LSIS | UTS400N | 600 | 3 | 18 | 400 | 250 | 600 | 3 | 18 | 192 | 200 | 7447 | 1
|  | MC | LSIS | MC-265a | 240 | 3 | 10 | 192 | - | 240 | 3
LSIS321.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS321.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS321.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS321.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS322 | C [ version C2(b)] | CB | LSIS | UTS400H | 600 | 3 | 35 | 400 | 250 | 600 | 3 | 35 | 192 | 200 | 7447 | 1
|  | MC | LSIS | MC-265a | 240 | 3 | 10 | 192 | - | 240 | 3
LSIS322.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS322.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS322.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS322.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS323 | C [ version C2(b)] | CB | LSIS | UTS400L | 600 | 3 | 50 | 400 | 250 | 600 | 3 | 50 | 192 | 200 | 7447 | 1
|  | MC | LSIS | MC-265a | 240 | 3 | 10 | 192 | - | 240 | 3
LSIS323.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS323.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS323.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS323.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS324 | C [ version C2(b)] | CB | LSIS | UTS400N | 600 | 3 | 18 | 400 | 250 | 600 | 3 | 18 | 192 | 200 | 7447 | 1
|  | MC | LSIS | MC-330a | 240 | 3 | 18 | 242 | - | 240 | 3
LSIS324.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS324.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS324.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS324.04 |  | OLR | LSIS | MT-400 |  |  | 18 | 160 - 240 | -
LSIS325 | C [ version C2(b)] | CB | LSIS | UTS400H | 600 | 3 | 35 | 400 | 250 | 600 | 3 | 35 | 192 | 200 | 7447 | 1
|  | MC | LSIS | MC-330a | 240 | 3 | 18 | 242 | - | 240 | 3
LSIS325.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS325.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS325.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS325.04 |  | OLR | LSIS | MT-400 |  |  | 18 | 160 - 240 | -
LSIS326 | C [ version C2(b)] | CB | LSIS | UTS400L | 600 | 3 | 50 | 400 | 250 | 600 | 3 | 50 | 192 | 200 | 7447 | 1
|  | MC | LSIS | MC-330a | 240 | 3 | 18 | 242 | - | 240 | 3
LSIS326.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS326.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS326.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS326.04 |  | OLR | LSIS | MT-400 |  |  | 18 | 160 - 240 | -
LSIS327 | C [ version C2(b)] | CB | LSIS | UTS600N | 600 | 3 | 18 | 500 | 500 | 600 | 3 | 18 | 289 | 300 | 7447 | 1
|  | MC | LSIS | MC-400a |  |  | 18 | 289 | -
LSIS327.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS327.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS327.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS327.04 |  | OLR | LSIS | MT-400 |  |  | 18 | 160 - 240 | -
LSIS327.05 |  | OLR | LSIS | MT-400 |  |  | 18 | 200 - 330 | -
LSIS327.06 |  | OLR | LSIS | MT-400 |  |  | 18 | 260 - 400 | -
LSIS328 | C [ version C2(b)] | CB | LSIS | UTS600H | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 289 | 300 | 7447 | 1
|  | MC | LSIS | MC-400a |  |  | 18 | 289 | -
LSIS328.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS328.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS328.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS328.04 |  | OLR | LSIS | MT-400 |  |  | 18 | 160 - 240 | -
LSIS328.05 |  | OLR | LSIS | MT-400 |  |  | 18 | 200 - 330 | -
LSIS328.06 |  | OLR | LSIS | MT-400 |  |  | 18 | 260 - 400 | -
LSIS329 | C [ version C2(b)] | CB | LSIS | UTS600L | 600 | 3 | 50 | 500 | 500 | 600 | 3 | 50 | 289 | 300 | 7447 | 1
|  | MC | LSIS | MC-400a |  |  | 18 | 289 | -
LSIS329.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS329.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS329.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS329.04 |  | OLR | LSIS | MT-400 |  |  | 18 | 160 - 240 | -
LSIS329.05 |  | OLR | LSIS | MT-400 |  |  | 18 | 200 - 330 | -
LSIS329.06 |  | OLR | LSIS | MT-400 |  |  | 18 | 260 - 400 | -
LSIS330 | C [ version C2(b)] | CB | LSIS | UTS800H | 600 | 3 | 35 | 800 | 400 | 600 | 3 | 35 | 382 | 400 | 15980 | 1
|  | MC | LSIS | MC-500a |  |  | 18 | 382 | -
LSIS330.01 |  | OLR | LSIS | MT-800 |  |  | 18 | 200 - 330 | -
LSIS330.02 |  | OLR | LSIS | MT-800 |  |  | 18 | 260 - 400 | -
LSIS331 | C [ version C2(b)] | CB | LSIS | UTS800L | 600 | 3 | 50 | 800 | 400 | 600 | 3 | 50 | 382 | 400 | 15980 | 1
|  | MC | LSIS | MC-500a |  |  | 18 | 382 | -
LSIS331.01 |  | OLR | LSIS | MT-800 |  |  | 18 | 200 - 330 | -
LSIS331.02 |  | OLR | LSIS | MT-800 |  |  | 18 | 260 - 400 | -
LSIS322 | C [ version C2(b)] | CB | LSIS | UTS800H | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 472 | 500 | 15980 | 1
|  | MC | LSIS | MC-630a |  |  | 30 | 472 | -
LSIS332.01 |  | OLR | LSIS | MT-800 |  |  | 18 | 200 - 330 | -
LSIS332.02 |  | OLR | LSIS | MT-800 |  |  | 18 | 260 - 400 | -
LSIS332.03 |  | OLR | LSIS | MT-800 |  |  | 18 | 400 - 600 | -
LSIS333 | C [ version C2(b)] | CB | LSIS | UTS800L | 600 | 3 | 50 | 800 | 500 | 600 | 3 | 50 | 472 | 500 | 15980 | 1
|  | MC | LSIS | MC-630a |  |  | 30 | 472 | -
LSIS333.01 |  | OLR | LSIS | MT-800 |  |  | 18 | 200 - 330 | -
LSIS333.02 |  | OLR | LSIS | MT-800 |  |  | 18 | 260 - 400 | -
LSIS333.03 |  | OLR | LSIS | MT-800 |  |  | 18 | 400 - 600 | -

## Type D
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | Conditions of Use
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating
LSIS401 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 240 | 3 | - | 3.2 | - | 240 | 3 | 100 | 2.2 | 0.5 | 1785 | 1
|  | MC | LSIS | MC-6a |  |  | 5 | 2.2 | -
LSIS401.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS401.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS401.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS401.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS401.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS401.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS401.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS402 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 240 | 3 | - | 6.3 | - | 240 | 3 | 100 | 4.2 | 1 | 1785 | 1
|  | MC | LSIS | MC-6a |  |  | 5 | 4.2 | -
LSIS402.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS402.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS402.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS402.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS402.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS402.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS402.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS402.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS402.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS403 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 240 | 3 | - | 12 | - | 240 | 3 | 100 | 9.6 | 3 | 1785 | 1
|  | MC | LSIS | MC-6a |  |  | 5 | 9.6 | -
LSIS403.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS403.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS403.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS403.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS403.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS403.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS403.07 |  | OLR | LSIS | MT-12 |  |  | 1 | 1.6 - 2.5 | -
LSIS403.08 |  | OLR | LSIS | MT-12 |  |  | 1 | 2.5 - 4 | -
LSIS403.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS403.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS403.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS403.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS404 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 240 | 3 | - | 12 | - | 240 | 3 | 100 | 9.6 | 3 | 1785 | 1
|  | MC | LSIS | MC-9a |  |  | 5 | 9.6 | -
LSIS404.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS404.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS404.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS404.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS404.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS404.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS404.07 |  | OLR | LSIS | MT-12 |  |  | 1 | 1.6 - 2.5 | -
LSIS404.08 |  | OLR | LSIS | MT-12 |  |  | 1 | 2.5 - 4 | -
LSIS404.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS404.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS404.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS404.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS405 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 240 | 3 | - | 20 | - | 240 | 3 | 100 | 15.2 | 5 | 1785 | 1
|  | MC | LSIS | MC-12a |  |  | 5 | 15.2 | -
LSIS405.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS405.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS405.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS405.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS405.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS405.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS405.07 |  | OLR | LSIS | MT-12 |  |  | 1 | 1.6 - 2.5 | -
LSIS405.08 |  | OLR | LSIS | MT-12 |  |  | 1 | 2.5 - 4 | -
LSIS405.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS405.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS405.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS405.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS405.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS405.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS406 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 240 | 3 | - | 32 | - | 240 | 3 | 100 | 22 | 7.5 | 1785 | 1
|  | MC | LSIS | MC-18a |  |  | 5 | 22 | -
LSIS406.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS406.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS406.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS406.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS406.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS406.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS406.07 |  | OLR | LSIS | MT-12 |  |  | 1 | 1.6 - 2.5 | -
LSIS406.08 |  | OLR | LSIS | MT-12 |  |  | 1 | 2.5 - 4 | -
LSIS406.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS406.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS406.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS406.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS406.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS406.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS407 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 240 | 3 | - | 12 | - | 240 | 3 | 100 | 9.6 | 3 | 1785 | 1
|  | MC | LSIS | MC-9b |  |  | 5 | 9.6 | -
LSIS407.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS407.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS407.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS407.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS407.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS407.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS407.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS407.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS407.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS407.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS407.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS407.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS408 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 240 | 3 | - | 20 | - | 240 | 3 | 100 | 15.2 | 5 | 1785 | 1
|  | MC | LSIS | MC-12b |  |  | 5 | 15.2 | -
LSIS408.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS408.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS408.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS408.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS408.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS408.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS408.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS408.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS408.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS408.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS408.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS408.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS408.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS408.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS409 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 240 | 3 | - | 32 | - | 240 | 3 | 100 | 22 | 7.5 | 1785 | 1
|  | MC | LSIS | MC-18b |  |  | 5 | 22 | -
LSIS409.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS409.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS409.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS409.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS409.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS409.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS409.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS409.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS409.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS409.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS409.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS409.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS409.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS409.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS409.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS409.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS410 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 240 | 3 | - | 50 | - | 240 | 3 | 100 | 28 | 10 | 1785 | 1
|  | MC | LSIS | MC-22b |  |  | 5 | 28 | -
LSIS410.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS410.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS410.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS410.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS410.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS410.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS410.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS410.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS410.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS410.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS410.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS410.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS410.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS410.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS410.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS410.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS410.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS411 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 240 | 3 | - | 50 | - | 240 | 3 | 100 | 28 | 10 | 1785 | 1
|  | MC | LSIS | MC-32a |  |  | 5 | 28 | -
LSIS411.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS411.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS411.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS411.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS411.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS411.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS411.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS411.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS411.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS411.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS411.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS411.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS411.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS411.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS411.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS411.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS411.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS412 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 240 | 3 | - | 60 | - | 240 | 3 | 100 | 42 | 15 | 1785 | 1
|  | MC | LSIS | MC-40a |  |  | 5 | 42 | -
LSIS412.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS412.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS412.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS412.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS412.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS412.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS412.07 |  | OLR | LSIS | MT-32 |  |  | 1 | 1.6 - 2.5 | -
LSIS412.08 |  | OLR | LSIS | MT-32 |  |  | 1 | 2.5 - 4 | -
LSIS412.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS412.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS412.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS412.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS412.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS412.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS412.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS412.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS412.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS412.18 |  | OLR | LSIS | MT-32 |  |  | 5 | 28 - 40 | -
LSIS413 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 240 | 3 | - | 100 | - | 240 | 3 | 100 | 65 | 25 | 1785 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 65 | -
LSIS413.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS413.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS413.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS413.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS413.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS413.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS413.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS413.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS413.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS413.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS413.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS413.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS414 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 240 | 3 | - | 100 | - | 240 | 3 | 100 | 80 | 30 | 1785 | 1
|  | MC | LSIS | MC-65a |  |  | 5 | 80 | -
LSIS414.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS414.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS414.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS414.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS414.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS414.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS414.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS414.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS414.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS414.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS414.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS414.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS415 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 240 | 3 | - | 150 | - | 240 | 3 | 100 | 80 | 30 | 1785 | 1
|  | MC | LSIS | MC-75a |  |  | 5 | 80 | -
LSIS415.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS415.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS415.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS415.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS415.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS415.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS415.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS415.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS415.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS415.10 |  | OLR | LSIS | MT-95 |  |  | 5 | 54 - 75 | -
LSIS415.11 |  | OLR | LSIS | MT-95 |  |  | 5 | 63 - 85 | -
LSIS415.12 |  | OLR | LSIS | MT-95 |  |  | 5 | 70 - 95 | -
LSIS416 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 240 | 3 | - | 150 | - | 240 | 3 | 100 | 104 | 40 | 1785 | 1
|  | MC | LSIS | MC-85a |  |  | 5 | 104 | -
LSIS416.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS416.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS416.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS416.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS416.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS416.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS416.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS416.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS416.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS416.10 |  | OLR | LSIS | MT-95 |  |  | 5 | 54 - 75 | -
LSIS416.11 |  | OLR | LSIS | MT-95 |  |  | 5 | 63 - 85 | -
LSIS416.12 |  | OLR | LSIS | MT-95 |  |  | 5 | 70 - 95 | -
LSIS416.13 |  | OLR | LSIS | MT-95 |  |  | 5 | 80 - 100 | -
LSIS417 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 240 | 3 | - | 150 | - | 240 | 3 | 100 | 104 | 40 | 1785 | 1
|  | MC | LSIS | MC-100a |  |  | 5 | 104 | -
LSIS417.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS417.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS417.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS417.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS417.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS417.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS417.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS417.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS417.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS417.10 |  | OLR | LSIS | MT-95 |  |  | 5 | 54 - 75 | -
LSIS417.11 |  | OLR | LSIS | MT-95 |  |  | 5 | 63 - 85 | -
LSIS417.12 |  | OLR | LSIS | MT-95 |  |  | 5 | 70 - 95 | -
LSIS417.13 |  | OLR | LSIS | MT-95 |  |  | 5 | 80 - 100 | -
LSIS418 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 240 | 3 | - | 150 | - | 240 | 3 | 100 | 104 | 40 | 1785 | 1
|  | MC | LSIS | MC-130a |  |  | 5 | 104 | -
LSIS418.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS418.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS418.03 |  | OLR | LSIS | MT-150 |  |  | 5 | 54 - 75 | -
LSIS418.04 |  | OLR | LSIS | MT-150 |  |  | 5 | 63 - 85 | -
LSIS418.05 |  | OLR | LSIS | MT-150 |  |  | 5 | 80 - 105 | -
LSIS418.06 |  | OLR | LSIS | MT-150 |  |  | 5 | 95 - 130 | -
LSIS419 | D [ version C3(a)] | ICB | LSIS | UTS250L MCP | 240 | 3 | - | 220 | - | 240 | 3 | 100 | 130 | 50 | 3355 | 1
|  | MC | LSIS | MC-150a |  |  | 5 | 130 | -
LSIS419.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS419.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS419.03 |  | OLR | LSIS | MT-150 |  |  | 5 | 54 - 75 | -
LSIS419.04 |  | OLR | LSIS | MT-150 |  |  | 5 | 63 - 85 | -
LSIS419.05 |  | OLR | LSIS | MT-150 |  |  | 5 | 80 - 105 | -
LSIS419.06 |  | OLR | LSIS | MT-150 |  |  | 5 | 95 - 130 | -
LSIS420 | D [ version C3(a)] | ICB | LSIS | UTS250L MCP | 240 | 3 | - | 220 | - | 240 | 3 | 100 | 154 | 60 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 154 | -
LSIS420.01 |  | OLR | LSIS | MT-225 |  |  | 5 | 65 - 100 | -
LSIS420.02 |  | OLR | LSIS | MT-225 |  |  | 5 | 85 - 125 | -
LSIS420.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS421 | D [ version C3(a)] | ICB | LSIS | UTS250L MCP | 240 | 3 | - | 220 | - | 240 | 3 | 100 | 192 | 75 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 192 | -
LSIS421.01 |  | OLR | LSIS | MT-225 |  |  | 5 | 65 - 100 | -
LSIS421.02 |  | OLR | LSIS | MT-225 |  |  | 5 | 85 - 125 | -
LSIS421.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS421.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS421.05 |  | OLR | LSIS | MT-225 |  |  | 10 | 160 - 240 | -
LSIS422 | D [ version C3(a)] | ICB | LSIS | UTS400L MCP | 240 | 3 | - | 320 | - | 240 | 3 | 100 | 154 | 60 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 154 | -
LSIS422.01 |  | OLR | LSIS | MT-225 |  |  | 5 | 65 - 100 | -
LSIS422.02 |  | OLR | LSIS | MT-225 |  |  | 5 | 85 - 125 | -
LSIS422.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS422.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS423 | D [ version C3(a)] | ICB | LSIS | UTS400L MCP | 240 | 3 | - | 320 | - | 240 | 3 | 100 | 192 | 75 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 192 | -
LSIS423.01 |  | OLR | LSIS | MT-225 |  |  | 5 | 65 - 100 | -
LSIS423.02 |  | OLR | LSIS | MT-225 |  |  | 5 | 85 - 125 | -
LSIS423.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS423.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS423.05 |  | OLR | LSIS | MT-225 |  |  | 10 | 160 - 240 | -
LSIS424 | D [ version C3(a)] | ICB | LSIS | UTS400L MCP | 240 | 3 | - | 320 | - | 240 | 3 | 100 | 248 | 100 | 7447 | 1
|  | MC | LSIS | MC-265a | 240 |  | 10 | 248 | - | 240
LSIS424.01 |  | OLR | LSIS | MT-400 |  |  | 5 | 85 - 125 | -
LSIS424.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS424.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS424.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS424.05 |  | OLR | LSIS | MT-400 |  |  | 10 | 200 - 330 | -
LSIS425 | D [ version C3(a)] | ICB | LSIS | UTS400L MCP | 240 | 3 | - | 320 | - | 240 | 3 | 100 | 248 | 100 | 7447 | 1
|  | MC | LSIS | MC-330a | 240 |  | 10 | 312 | - | 240
LSIS425.01 |  | OLR | LSIS | MT-400 |  |  | 5 | 85 - 125 | -
LSIS425.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS425.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS425.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS425.05 |  | OLR | LSIS | MT-400 |  |  | 10 | 200 - 330 | -
LSIS426 | D [ version C3(a)] | ICB | LSIS | UTS600L MCP | 240 | 3 | - | 500 | - | 240 | 3 | 100 | 360 | 150 | 7447 | 1
|  | MC | LSIS | MC-400a |  |  | 10 | 360 | -
LSIS426.01 |  | OLR | LSIS | MT-400 |  |  | 5 | 85 - 125 | -
LSIS426.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS426.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS426.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS426.05 |  | OLR | LSIS | MT-400 |  |  | 10 | 200 - 330 | -
LSIS426.06 |  | OLR | LSIS | MT-400 |  |  | 10 | 260 - 400 | -
LSIS427 | D [ version C3(a)] | ICB | LSIS | UTS800L MCP | 240 | 3 | - | 800 | - | 240 | 3 | 100 | 480 | 200 | 15980 | 1
|  | MC | LSIS | MC-500a |  |  | 10 | 480 | -
LSIS427.01 |  | OLR | LSIS | MT-800 |  |  | 10 | 200 - 330 | -
LSIS427.02 |  | OLR | LSIS | MT-800 |  |  | 10 | 260 - 400 | -
LSIS427.03 |  | OLR | LSIS | MT-800 |  |  | 10 | 400 - 600 | -
LSIS428 | D [ version C3(a)] | ICB | LSIS | UTS800L MCP | 240 | 3 | - | 800 | - | 240 | 3 | 100 | 604 | 250 | 15980 | 1
|  | MC | LSIS | MC-630a |  |  | 18 | 604 | -
LSIS428.01 |  | OLR | LSIS | MT-800 |  |  | 10 | 200 - 330 | -
LSIS428.02 |  | OLR | LSIS | MT-800 |  |  | 10 | 260 - 400 | -
LSIS428.03 |  | OLR | LSIS | MT-800 |  |  | 18 | 400 - 600 | -
LSIS428.04 |  | OLR | LSIS | MT-800 |  |  | 18 | 520 - 800 | -
LSIS429 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 1.6 | - | 480 | 3 | 65 | 1.1 | 0.5 | 1785 | 1
|  | MC | LSIS | MC-6a |  |  | 5 | 1.1 | -
LSIS429.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS429.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS429.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS429.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS429.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS429.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS430 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 3.2 | - | 480 | 3 | 65 | 2.1 | 1 | 1785 | 1
|  | MC | LSIS | MC-6a |  |  | 5 | 2.1 | -
LSIS430.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS430.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS430.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS430.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS430.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS430.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS430.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS431 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 6.3 | - | 480 | 3 | 65 | 3.4 | 2 | 1785 | 1
|  | MC | LSIS | MC-6a |  |  | 5 | 3.4 | -
LSIS431.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS431.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS431.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS431.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS431.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS431.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS431.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS431.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS432 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 12 | - | 480 | 3 | 65 | 7.6 | 5 | 1785 | 1
|  | MC | LSIS | MC-6a |  |  | 5 | 7.6 | -
LSIS432.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS432.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS432.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS432.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS432.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS432.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS432.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS432.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS432.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS432.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS432.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS432.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS433 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 12 | - | 480 | 3 | 65 | 7.6 | 5 | 1785 | 1
|  | MC | LSIS | MC-9a |  |  | 5 | 7.6 | -
LSIS433.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS433.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS433.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS433.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS433.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS433.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS433.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS433.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS433.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS433.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS433.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS433.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS434 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 20 | - | 480 | 3 | 65 | 11 | 7.5 | 1785 | 1
|  | MC | LSIS | MC-12a |  |  | 5 | 11 | -
LSIS434.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS434.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS434.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS434.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS434.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS434.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS434.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS434.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS434.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS434.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS434.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS434.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS434.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS435 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 32 | - | 480 | 3 | 65 | 14 | 10 | 1785 | 1
|  | MC | LSIS | MC-18a |  |  | 5 | 14 | -
LSIS435.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS435.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS435.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS435.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS435.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS435.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS435.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS435.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS435.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS435.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS435.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS435.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS435.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS435.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS436 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 12 | - | 480 | 3 | 65 | 7.6 | 5 | 1785 | 1
|  | MC | LSIS | MC-9b |  |  | 5 | 7.6 | -
LSIS436.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS436.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS436.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS436.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS436.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS436.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS436.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS436.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS436.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS436.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS436.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS436.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS437 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 20 | - | 480 | 3 | 65 | 11 | 7.5 | 1785 | 1
|  | MC | LSIS | MC-12b |  |  | 5 | 11 | -
LSIS437.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS437.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS437.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS437.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS437.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS437.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS437.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS437.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS437.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS437.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS437.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS437.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS437.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS438 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 32 | - | 480 | 3 | 65 | 14 | 10 | 1785 | 1
|  | MC | LSIS | MC-18b |  |  | 5 | 14 | -
LSIS438.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS438.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS438.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS438.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS438.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS438.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS438.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS438.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS438.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS438.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS438.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS438.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS438.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS438.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS439 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 50 | - | 480 | 3 | 65 | 21 | 15 | 1785 | 1
|  | MC | LSIS | MC-22b |  |  | 5 | 21 | -
LSIS439.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS439.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS439.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS439.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS439.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS439.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS439.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS439.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS439.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS439.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS439.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS439.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS439.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS439.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS439.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS439.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS440 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 50 | - | 480 | 3 | 65 | 27 | 20 | 1785 | 1
|  | MC | LSIS | MC-32a |  |  | 5 | 27 | -
LSIS440.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS440.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS440.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS440.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS440.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS440.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS440.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS440.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS440.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS440.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS440.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS440.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS440.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS440.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS440.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS440.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS440.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS441 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 60 | - | 480 | 3 | 65 | 40 | 30 | 1785 | 1
|  | MC | LSIS | MC-40a |  |  | 5 | 40 | -
LSIS441.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS441.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS441.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS441.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS441.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS441.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS441.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS441.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS441.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS441.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS441.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS441.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS441.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS441.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS441.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS441.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS441.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS441.18 |  | OLR | LSIS | MT-32 |  |  | 5 | 28 - 40 | -
LSIS442 | D [ version C3(a)] | ICB | LSIS | UTS150H MCP | 480 | 3 | - | 100 | - | 480 | 3 | 65 | 52 | 40 | 1785 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 52 | -
LSIS442.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS442.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS442.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS442.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS442.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS442.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS442.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS442.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS442.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS442.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS442.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS442.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS443 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 100 | - | 480 | 3 | 100 | 52 | 40 | 1785 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 52 | -
LSIS443.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS443.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS443.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS443.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS443.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS443.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS443.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS443.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS443.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS443.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS443.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS443.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS444 | D [ version C3(a)] | ICB | LSIS | UTS150H MCP | 480 | 3 | - | 100 | - | 480 | 3 | 65 | 65 | 50 | 1785 | 1
|  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS444.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS444.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS444.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS444.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS444.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS444.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS444.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS444.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS444.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS444.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS444.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS444.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS445 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 100 | - | 480 | 3 | 100 | 65 | 50 | 1785 | 1
|  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS445.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS445.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS445.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS445.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS445.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS445.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS445.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS445.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 25 | -
LSIS445.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS445.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS445.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS445.12 |  | OLR | LSIS | MT-63 |  |  | 5 | 45 - 65 | -
LSIS446 | D [ version C3(a)] | ICB | LSIS | UTS150H MCP | 480 | 3 | - | 150 | - | 480 | 3 | 65 | 65 | 50 | 1785 | 1
|  | MC | LSIS | MC-75a |  |  | 5 | 65 | -
LSIS446.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS446.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS446.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS446.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS446.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS446.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS446.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS446.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS446.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS446.10 |  | OLR | LSIS | MT-95 |  |  | 5 | 54 - 75 | -
LSIS447 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 150 | - | 480 | 3 | 100 | 65 | 50 | 1785 | 1
|  | MC | LSIS | MC-75a |  |  | 5 | 65 | -
LSIS447.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS447.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS447.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS447.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS447.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS447.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS447.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS447.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS447.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS447.10 |  | OLR | LSIS | MT-95 |  |  | 5 | 54 - 75 | -
LSIS448 | D [ version C3(a)] | ICB | LSIS | UTS150H MCP | 480 | 3 | - | 150 | - | 480 | 3 | 65 | 77 | 60 | 1785 | 1
|  | MC | LSIS | MC-85a |  |  | 10 | 77 | -
LSIS448.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS448.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS448.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS448.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS448.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS448.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS448.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS448.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS448.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS448.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS448.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS449 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 150 | - | 480 | 3 | 100 | 77 | 60 | 1785 | 1
|  | MC | LSIS | MC-85a |  |  | 10 | 77 | -
LSIS449.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS449.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS449.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS449.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS449.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS449.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS449.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS449.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS449.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS449.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS449.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS450 | D [ version C3(a)] | ICB | LSIS | UTS150H MCP | 480 | 3 | - | 150 | - | 480 | 3 | 65 | 96 | 75 | 1785 | 1
|  | MC | LSIS | MC-100a |  |  | 10 | 96 | -
LSIS450.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS450.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS450.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS450.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS450.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS450.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS450.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS450.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS450.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS450.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS450.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS450.12 |  | OLR | LSIS | MT-95 |  |  | 10 | 70 - 95 | -
LSIS450.13 |  | OLR | LSIS | MT-95 |  |  | 10 | 80 - 100 | -
LSIS451 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 150 | - | 480 | 3 | 100 | 96 | 75 | 1785 | 1
|  | MC | LSIS | MC-100a |  |  | 10 | 96 | -
LSIS451.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS451.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS451.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS451.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS451.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS451.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS451.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS451.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS451.09 |  | OLR | LSIS | MT-95 |  |  | 5 | 45 - 65 | -
LSIS451.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS451.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS451.12 |  | OLR | LSIS | MT-95 |  |  | 10 | 70 - 95 | -
LSIS451.13 |  | OLR | LSIS | MT-95 |  |  | 10 | 80 - 100 | -
LSIS452 | D [ version C3(a)] | ICB | LSIS | UTS150H MCP | 480 | 3 | - | 150 | - | 480 | 3 | 65 | 96 | 75 | 1785 | 1
|  | MC | LSIS | MC-130a |  |  | 10 | 96 | -
LSIS452.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS452.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS452.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS452.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS452.05 |  | OLR | LSIS | MT-150 |  |  | 10 | 80 - 105 | -
LSIS452.06 |  | OLR | LSIS | MT-150 |  |  | 10 | 95 - 130 | -
LSIS453 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 480 | 3 | - | 150 | - | 480 | 3 | 100 | 96 | 75 | 1785 | 1
|  | MC | LSIS | MC-130a |  |  | 10 | 96 | -
LSIS453.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS453.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS453.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS453.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS453.05 |  | OLR | LSIS | MT-150 |  |  | 10 | 80 - 105 | -
LSIS453.06 |  | OLR | LSIS | MT-150 |  |  | 10 | 95 - 130 | -
LSIS454 | D [ version C3(a)] | ICB | LSIS | UTS250H MCP | 480 | 3 | - | 220 | - | 480 | 3 | 65 | 124 | 100 | 3355 | 1
|  | MC | LSIS | MC-150a |  |  | 10 | 124 | -
LSIS454.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS454.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS454.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS454.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS454.05 |  | OLR | LSIS | MT-150 |  |  | 10 | 80 - 105 | -
LSIS454.06 |  | OLR | LSIS | MT-150 |  |  | 10 | 95 - 130 | -
LSIS455 | D [ version C3(a)] | ICB | LSIS | UTS250L MCP | 480 | 3 | - | 220 | - | 480 | 3 | 100 | 124 | 100 | 3355 | 1
|  | MC | LSIS | MC-150a |  |  | 10 | 124 | -
LSIS455.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS455.02 |  | OLR | LSIS | MT-150 |  |  | 5 | 45 - 65 | -
LSIS455.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS455.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS455.05 |  | OLR | LSIS | MT-150 |  |  | 10 | 80 - 105 | -
LSIS455.06 |  | OLR | LSIS | MT-150 |  |  | 10 | 95 - 130 | -
LSIS456 | D [ version C3(a)] | ICB | LSIS | UTS250H MCP | 480 | 3 | - | 220 | - | 480 | 3 | 65 | 156 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 156 | -
LSIS456.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS456.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS456.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS456.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS457 | D [ version C3(a)] | ICB | LSIS | UTS250L MCP | 480 | 3 | - | 220 | - | 480 | 3 | 85 | 156 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 156 | -
LSIS457.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS457.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS457.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS457.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS458 | D [ version C3(a)] | ICB | LSIS | UTS250L MCP | 480 | 3 | - | 220 | - | 480 | 3 | 65 | 180 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 180 | -
LSIS458.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS458.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS458.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS458.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS458.05 |  | OLR | LSIS | MT-225 |  |  | 10 | 160 - 240 | -
LSIS459 | D [ version C3(a)] | ICB | LSIS | UTS250L MCP | 480 | 3 | - | 220 | - | 480 | 3 | 85 | 180 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 180 | -
LSIS459.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS459.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS459.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS459.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS459.05 |  | OLR | LSIS | MT-225 |  |  | 10 | 160 - 240 | -
LSIS460 | D [ version C3(a)] | ICB | LSIS | UTS400H MCP | 480 | 3 | - | 320 | - | 480 | 3 | 65 | 156 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 156 | -
LSIS460.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS460.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS460.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS460.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS461 | D [ version C3(a)] | ICB | LSIS | UTS400L MCP | 480 | 3 | - | 320 | - | 480 | 3 | 100 | 156 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 156 | -
LSIS461.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS461.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS461.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS461.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS462 | D [ version C3(a)] | ICB | LSIS | UTS400H MCP | 480 | 3 | - | 320 | - | 480 | 3 | 65 | 180 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 180 | -
LSIS462.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS462.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS462.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS462.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS462.05 |  | OLR | LSIS | MT-225 |  |  | 10 | 160 - 240 | -
LSIS463 | D [ version C3(a)] | ICB | LSIS | UTS400L MCP | 480 | 3 | - | 320 | - | 480 | 3 | 100 | 180 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 180 | -
LSIS463.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS463.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS463.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS463.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS463.05 |  | OLR | LSIS | MT-225 |  |  | 10 | 160 - 240 | -
LSIS464 | D [ version C3(a)] | ICB | LSIS | UTS400H MCP | 480 | 3 | - | 320 | - | 480 | 3 | 65 | 240 | 200 | 7447 | 1
|  | MC | LSIS | MC-265a | 240 |  | 10 | 240 | - | 240
LSIS464.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS464.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS464.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS464.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS464.05 |  | OLR | LSIS | MT-400 |  |  | 10 | 200 - 330 | -
LSIS465 | D [ version C3(a)] | ICB | LSIS | UTS400L MCP | 480 | 3 | - | 320 | - | 480 | 3 | 100 | 240 | 200 | 7447 | 1
|  | MC | LSIS | MC-265a | 240 |  | 10 | 240 | - | 240
LSIS465.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS465.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS465.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS465.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS465.05 |  | OLR | LSIS | MT-400 |  |  | 10 | 200 - 330 | -
LSIS466 | D [ version C3(a)] | ICB | LSIS | UTS400H MCP | 480 | 3 | - | 320 | - | 480 | 3 | 65 | 240 | 200 | 7447 | 1
|  | MC | LSIS | MC-330a | 240 |  | 18 | 302 | - | 240
LSIS466.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS466.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS466.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS466.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS466.05 |  | OLR | LSIS | MT-400 |  |  | 18 | 200 - 330 | -
LSIS467 | D [ version C3(a)] | ICB | LSIS | UTS400L MCP | 480 | 3 | - | 320 | - | 480 | 3 | 100 | 240 | 200 | 7447 | 1
|  | MC | LSIS | MC-330a | 240 |  | 18 | 302 | - | 240
LSIS467.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS467.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS467.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS467.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS467.05 |  | OLR | LSIS | MT-400 |  |  | 18 | 200 - 330 | -
LSIS468 | D [ version C3(a)] | ICB | LSIS | UTS600H MCP | 480 | 3 | - | 500 | - | 480 | 3 | 65 | 361 | 300 | 7447 | 1
|  | MC | LSIS | MC-400a |  |  | 18 | 361 | -
LSIS468.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS468.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS468.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS468.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS468.05 |  | OLR | LSIS | MT-400 |  |  | 18 | 200 - 330 | -
LSIS468.06 |  | OLR | LSIS | MT-400 |  |  | 18 | 260 - 400 | -
LSIS469 | D [ version C3(a)] | ICB | LSIS | UTS600L MCP | 480 | 3 | - | 500 | - | 480 | 3 | 100 | 361 | 300 | 7447 | 1
|  | MC | LSIS | MC-400a |  |  | 18 | 361 | -
LSIS469.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS469.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS469.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS469.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS469.05 |  | OLR | LSIS | MT-400 |  |  | 18 | 200 - 330 | -
LSIS469.06 |  | OLR | LSIS | MT-400 |  |  | 18 | 260 - 400 | -
LSIS470 | D [ version C3(a)] | ICB | LSIS | UTS800L MCP | 480 | 3 | - | 800 | - | 480 | 3 | 100 | 477 | 400 | 15980 | 1
|  | MC | LSIS | MC-500a |  |  | 18 | 477 | -
LSIS470.01 |  | OLR | LSIS | MT-800 |  |  | 10 | 200 - 330 | -
LSIS470.02 |  | OLR | LSIS | MT-800 |  |  | 10 | 260 - 400 | -
LSIS470.03 |  | OLR | LSIS | MT-800 |  |  | 18 | 400 - 600 | -
LSIS471 | D [ version C3(a)] | ICB | LSIS | UTS800L MCP | 480 | 3 | - | 800 | - | 480 | 3 | 100 | 590 | 500 | 15980 | 1
|  | MC | LSIS | MC-630a |  |  | 30 | 590 | -
LSIS471.01 |  | OLR | LSIS | MT-800 |  |  | 10 | 200 - 330 | -
LSIS471.02 |  | OLR | LSIS | MT-800 |  |  | 10 | 260 - 400 | -
LSIS471.03 |  | OLR | LSIS | MT-800 |  |  | 18 | 400 - 600 | -
LSIS471.04 |  | OLR | LSIS | MT-800 |  |  | 30 | 520 - 800 | -
LSIS472 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 1.6 | - | 600 | 3 | 25 | 0.9 | 0.5 | 1785 | 1
|  | MC | LSIS | MC-6a |  |  | 5 | 0.9 | -
LSIS472.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS472.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS472.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS472.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS472.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS473 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 3.2 | - | 600 | 3 | 25 | 1.7 | 1 | 1785 | 1
|  | MC | LSIS | MC-6a |  |  | 5 | 1.7 | -
LSIS473.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS473.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS473.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS473.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS473.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS473.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS473.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS474 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 6.3 | - | 600 | 3 | 25 | 3.9 | 3 | 1785 | 1
|  | MC | LSIS | MC-6a |  |  | 5 | 3.9 | -
LSIS474.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS474.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS474.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS474.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS474.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS474.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS474.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS474.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS475 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 12 | - | 600 | 3 | 25 | 9 | 7.5 | 1785 | 1
|  | MC | LSIS | MC-6a |  |  | 5 | 9 | -
LSIS475.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS475.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS475.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS475.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS475.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS475.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS475.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS475.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS475.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS475.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS475.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS475.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS476 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 12 | - | 600 | 3 | 25 | 9 | 7.5 | 1785 | 1
|  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSOS476.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSOS476.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSOS476.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSOS476.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSOS476.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSOS476.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSOS476.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSOS476.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSOS476.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSOS476.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSOS476.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSOS476.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS477 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 20 | - | 600 | 3 | 25 | 11 | 10 | 1785 | 1
|  | MC | LSIS | MC-12a |  |  | 5 | 11 | -
LSIS477.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS477.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS477.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS477.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS477.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS477.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS477.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS477.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS477.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS477.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS477.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS477.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS477.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS478 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 32 | - | 600 | 3 | 25 | 17 | 15 | 1785 | 1
|  | MC | LSIS | MC-18a |  |  | 5 | 17 | -
LSIS478.01 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.1 - 0.16 | -
LSIS478.02 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.16 - 0.25 | -
LSIS478.03 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.25 - 0.4 | -
LSIS478.04 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.4 - 0.63 | -
LSIS478.05 |  | OLR | LSIS | MT-12 |  |  | 1 | 0.63 - 1 | -
LSIS478.06 |  | OLR | LSIS | MT-12 |  |  | 1 | 1 - 1.6 | -
LSIS478.07 |  | OLR | LSIS | MT-12 |  |  | 5 | 1.6 - 2.5 | -
LSIS478.08 |  | OLR | LSIS | MT-12 |  |  | 5 | 2.5 - 4 | -
LSIS478.09 |  | OLR | LSIS | MT-12 |  |  | 5 | 4 - 6 | -
LSIS478.10 |  | OLR | LSIS | MT-12 |  |  | 5 | 5 - 8 | -
LSIS478.11 |  | OLR | LSIS | MT-12 |  |  | 5 | 6 - 9 | -
LSIS478.12 |  | OLR | LSIS | MT-12 |  |  | 5 | 7 - 10 | -
LSIS478.13 |  | OLR | LSIS | MT-12 |  |  | 5 | 9 - 13 | -
LSIS478.14 |  | OLR | LSIS | MT-12 |  |  | 5 | 12 - 18 | -
LSIS479 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 12 | - | 600 | 3 | 25 | 9 | 7.5 | 1785 | 1
|  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS479.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS479.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS479.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS479.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS479.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS479.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS479.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS479.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS479.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS479.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS479.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS479.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS480 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 20 | - | 600 | 3 | 25 | 11 | 10 | 1785 | 1
|  | MC | LSIS | MC-12b |  |  | 5 | 11 | -
LSIS480.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS480.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS480.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS480.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS480.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS480.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS480.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS480.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS480.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS480.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS480.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS480.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS480.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS481 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 32 | - | 600 | 3 | 25 | 17 | 15 | 1785 | 1
|  | MC | LSIS | MC-18b |  |  | 5 | 17 | -
LSIS481.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS481.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS481.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS481.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS481.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS481.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS481.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS481.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS481.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS481.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS481.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS481.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS481.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS481.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS482 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 50 | - | 600 | 3 | 25 | 22 | 20 | 1785 | 1
|  | MC | LSIS | MC-22b |  |  | 5 | 22 | -
LSIS482.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS482.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS482.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS482.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS482.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS482.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS482.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS482.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS482.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS482.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS482.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS482.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS482.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS482.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS482.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS482.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS483 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 50 | - | 600 | 3 | 25 | 27 | 25 | 1785 | 1
|  | MC | LSIS | MC-32a |  |  | 5 | 27 | -
LSIS483.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS483.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS483.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS483.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS483.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS483.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS483.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS483.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS483.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS483.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS483.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS483.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS483.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS483.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS483.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS483.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS483.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS484 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 60 | - | 600 | 3 | 25 | 32 | 30 | 1785 | 1
|  | MC | LSIS | MC-40a |  |  | 5 | 32 | -
LSIS484.01 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.1 - 0.16 | -
LSIS484.02 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.16 - 0.25 | -
LSIS484.03 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.25 - 0.4 | -
LSIS484.04 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.4 - 0.63 | -
LSIS484.05 |  | OLR | LSIS | MT-32 |  |  | 1 | 0.63 - 1 | -
LSIS484.06 |  | OLR | LSIS | MT-32 |  |  | 1 | 1 - 1.6 | -
LSIS484.07 |  | OLR | LSIS | MT-32 |  |  | 5 | 1.6 - 2.5 | -
LSIS484.08 |  | OLR | LSIS | MT-32 |  |  | 5 | 2.5 - 4 | -
LSIS484.09 |  | OLR | LSIS | MT-32 |  |  | 5 | 4 - 6 | -
LSIS484.10 |  | OLR | LSIS | MT-32 |  |  | 5 | 5 - 8 | -
LSIS484.11 |  | OLR | LSIS | MT-32 |  |  | 5 | 6 - 9 | -
LSIS484.12 |  | OLR | LSIS | MT-32 |  |  | 5 | 7 - 10 | -
LSIS484.13 |  | OLR | LSIS | MT-32 |  |  | 5 | 9 - 13 | -
LSIS484.14 |  | OLR | LSIS | MT-32 |  |  | 5 | 12 - 18 | -
LSIS484.15 |  | OLR | LSIS | MT-32 |  |  | 5 | 16 - 22 | -
LSIS484.16 |  | OLR | LSIS | MT-32 |  |  | 5 | 18 - 25 | -
LSIS484.17 |  | OLR | LSIS | MT-32 |  |  | 5 | 22 - 32 | -
LSIS485 | D [ version C3(a)] | ICB | LSIS | UTS150H MCP | 600 | 3 | - | 100 | - | 600 | 3 | 25 | 52 | 50 | 1785 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 52 | -
LSIS485.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS485.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS485.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS485.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS485.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS485.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS485.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS485.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 26 | -
LSIS485.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS485.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS485.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS485.12 |  | OLR | LSIS | MT-63 |  |  | 10 | 45 - 65 | -
LSIS486 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 100 | - | 600 | 3 | 50 | 52 | 50 | 1785 | 1
|  | MC | LSIS | MC-50a |  |  | 5 | 52 | -
LSIS486.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS486.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS486.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS486.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS486.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS486.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS486.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS486.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 26 | -
LSIS486.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS486.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS486.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS486.12 |  | OLR | LSIS | MT-63 |  |  | 10 | 45 - 65 | -
LSIS487 | D [ version C3(a)] | ICB | LSIS | UTS150H MCP | 600 | 3 | - | 100 | - | 600 | 3 | 25 | 62 | 60 | 1785 | 1
|  | MC | LSIS | MC-65a |  |  | 10 | 62 | -
LSIS487.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS487.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS487.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS487.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS487.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS487.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS487.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS487.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 26 | -
LSIS487.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS487.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS487.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS487.12 |  | OLR | LSIS | MT-63 |  |  | 10 | 45 - 65 | -
LSIS488 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 100 | - | 600 | 3 | 50 | 62 | 60 | 1785 | 1
|  | MC | LSIS | MC-65a |  |  | 10 | 62 | -
LSIS488.01 |  | OLR | LSIS | MT-63 |  |  | 5 | 4 - 6 | -
LSIS488.02 |  | OLR | LSIS | MT-63 |  |  | 5 | 5 - 8 | -
LSIS488.03 |  | OLR | LSIS | MT-63 |  |  | 5 | 6 - 9 | -
LSIS488.04 |  | OLR | LSIS | MT-63 |  |  | 5 | 7 - 10 | -
LSIS488.05 |  | OLR | LSIS | MT-63 |  |  | 5 | 9 - 13 | -
LSIS488.06 |  | OLR | LSIS | MT-63 |  |  | 5 | 12 - 18 | -
LSIS488.07 |  | OLR | LSIS | MT-63 |  |  | 5 | 16 - 22 | -
LSIS488.08 |  | OLR | LSIS | MT-63 |  |  | 5 | 18 - 26 | -
LSIS488.09 |  | OLR | LSIS | MT-63 |  |  | 5 | 24 - 36 | -
LSIS488.10 |  | OLR | LSIS | MT-63 |  |  | 5 | 28 - 40 | -
LSIS488.11 |  | OLR | LSIS | MT-63 |  |  | 5 | 34 - 50 | -
LSIS488.12 |  | OLR | LSIS | MT-63 |  |  | 10 | 45 - 65 | -
LSIS489 | D [ version C3(a)] | ICB | LSIS | UTS150H MCP | 600 | 3 | - | 150 | - | 600 | 3 | 25 | 62 | 60 | 1785 | 1
|  | MC | LSIS | MC-75a |  |  | 10 | 62 | -
LSIS489.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS489.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS489.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS489.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS489.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS489.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS489.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS489.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS489.09 |  | OLR | LSIS | MT-95 |  |  | 10 | 45 - 65 | -
LSIS489.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS490 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 150 | - | 600 | 3 | 50 | 62 | 60 | 1785 | 1
|  | MC | LSIS | MC-75a |  |  | 10 | 62 | -
LSIS490.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS490.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS490.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS490.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS490.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS490.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS490.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS490.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS490.09 |  | OLR | LSIS | MT-95 |  |  | 10 | 45 - 65 | -
LSIS490.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS491 | D [ version C3(a)] | ICB | LSIS | UTS150H MCP | 600 | 3 | - | 150 | - | 600 | 3 | 25 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-85a |  |  | 10 | 77 | -
LSIS491.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS491.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS491.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS491.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS491.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS491.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS491.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS491.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS491.09 |  | OLR | LSIS | MT-95 |  |  | 10 | 45 - 65 | -
LSIS491.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS491.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS492 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 150 | - | 600 | 3 | 50 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-85a |  |  | 10 | 77 | -
LSIS492.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS492.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS492.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS492.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS492.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS492.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS492.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS492.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS492.09 |  | OLR | LSIS | MT-95 |  |  | 10 | 45 - 65 | -
LSIS492.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS492.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS493 | D [ version C3(a)] | ICB | LSIS | UTS150H MCP | 600 | 3 | - | 150 | - | 600 | 3 | 25 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-100a |  |  | 10 | 77 | -
LSIS493.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS493.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS493.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS493.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS493.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS493.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS493.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS493.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS493.09 |  | OLR | LSIS | MT-95 |  |  | 10 | 45 - 65 | -
LSIS493.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS493.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS494 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 150 | - | 600 | 3 | 50 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-100a |  |  | 10 | 77 | -
LSIS494.01 |  | OLR | LSIS | MT-95 |  |  | 5 | 7 - 10 | -
LSIS494.02 |  | OLR | LSIS | MT-95 |  |  | 5 | 9 - 13 | -
LSIS494.03 |  | OLR | LSIS | MT-95 |  |  | 5 | 12 - 18 | -
LSIS494.04 |  | OLR | LSIS | MT-95 |  |  | 5 | 16 - 22 | -
LSIS494.05 |  | OLR | LSIS | MT-95 |  |  | 5 | 18 - 25 | -
LSIS494.06 |  | OLR | LSIS | MT-95 |  |  | 5 | 24 - 36 | -
LSIS494.07 |  | OLR | LSIS | MT-95 |  |  | 5 | 28 - 40 | -
LSIS494.08 |  | OLR | LSIS | MT-95 |  |  | 5 | 34 - 50 | -
LSIS494.09 |  | OLR | LSIS | MT-95 |  |  | 10 | 45 - 65 | -
LSIS494.10 |  | OLR | LSIS | MT-95 |  |  | 10 | 54 - 75 | -
LSIS494.11 |  | OLR | LSIS | MT-95 |  |  | 10 | 63 - 85 | -
LSIS495 | D [ version C3(a)] | ICB | LSIS | UTS150H MCP | 600 | 3 | - | 150 | - | 600 | 3 | 25 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-130a |  |  | 10 | 77 | -
LSIS495.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS495.02 |  | OLR | LSIS | MT-150 |  |  | 10 | 45 - 65 | -
LSIS495.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS495.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS496 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 150 | - | 600 | 3 | 50 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-130a |  |  | 10 | 77 | -
LSIS496.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS496.02 |  | OLR | LSIS | MT-150 |  |  | 10 | 45 - 65 | -
LSIS496.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS496.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS497 | D [ version C3(a)] | ICB | LSIS | UTS150H MCP | 600 | 3 | - | 150 | - | 600 | 3 | 25 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-150a |  |  | 10 | 77 | -
LSIS497.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS497.02 |  | OLR | LSIS | MT-150 |  |  | 10 | 45 - 65 | -
LSIS497.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS497.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS498 | D [ version C3(a)] | ICB | LSIS | UTS150L MCP | 600 | 3 | - | 150 | - | 600 | 3 | 50 | 77 | 75 | 1785 | 1
|  | MC | LSIS | MC-150a |  |  | 10 | 77 | -
LSIS498.01 |  | OLR | LSIS | MT-150 |  |  | 5 | 34 - 50 | -
LSIS498.02 |  | OLR | LSIS | MT-150 |  |  | 10 | 45 - 65 | -
LSIS498.03 |  | OLR | LSIS | MT-150 |  |  | 10 | 54 - 75 | -
LSIS498.04 |  | OLR | LSIS | MT-150 |  |  | 10 | 63 - 85 | -
LSIS499 | D [ version C3(a)] | ICB | LSIS | UTS250H MCP | 600 | 3 | - | 220 | - | 600 | 3 | 25 | 125 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 125 | -
LSIS499.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS499.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS499.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS499.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS500 | D [ version C3(a)] | ICB | LSIS | UTS250L MCP | 600 | 3 | - | 220 | - | 600 | 3 | 50 | 125 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 125 | -
LSIS500.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS500.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS500.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS500.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS501 | D [ version C3(a)] | ICB | LSIS | UTS250H MCP | 600 | 3 | - | 220 | - | 600 | 3 | 25 | 144 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 144 | -
LSIS501.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS501.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS501.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS501.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS502 | D [ version C3(a)] | ICB | LSIS | UTS250H MCP | 600 | 3 | - | 220 | - | 600 | 3 | 50 | 144 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 144 | -
LSIS502.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS502.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS502.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS502.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS503 | D [ version C3(a)] | ICB | LSIS | UTS400H MCP | 600 | 3 | - | 320 | - | 600 | 3 | 25 | 125 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 125 | -
LSIS503.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS503.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS503.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS503.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS504 | D [ version C3(a)] | ICB | LSIS | UTS400L MCP | 600 | 3 | - | 320 | - | 600 | 3 | 50 | 125 | 125 | 7447 | 1
|  | MC | LSIS | MC-185a |  |  | 10 | 125 | -
LSIS504.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS504.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS504.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS504.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS505 | D [ version C3(a)] | ICB | LSIS | UTS400H MCP | 600 | 3 | - | 320 | - | 600 | 3 | 25 | 144 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 144 | -
LSIS505.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS505.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS505.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS505.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS506 | D [ version C3(a)] | ICB | LSIS | UTS400L MCP | 600 | 3 | - | 320 | - | 600 | 3 | 50 | 144 | 150 | 7447 | 1
|  | MC | LSIS | MC-225a |  |  | 10 | 144 | -
LSIS506.01 |  | OLR | LSIS | MT-225 |  |  | 10 | 65 - 100 | -
LSIS506.02 |  | OLR | LSIS | MT-225 |  |  | 10 | 85 - 125 | -
LSIS506.03 |  | OLR | LSIS | MT-225 |  |  | 10 | 100 - 160 | -
LSIS506.04 |  | OLR | LSIS | MT-225 |  |  | 10 | 120 - 185 | -
LSIS507 | D [ version C3(a)] | ICB | LSIS | UTS400H MCP | 600 | 3 | - | 320 | - | 600 | 3 | 25 | 192 | 200 | 7447 | 1
|  | MC | LSIS | MC-265a | 240 |  | 10 | 192 | - | 240
LSIS507.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS507.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS507.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS507.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS508 | D [ version C3(a)] | ICB | LSIS | UTS400L MCP | 600 | 3 | - | 320 | - | 600 | 3 | 50 | 192 | 200 | 7447 | 1
|  | MC | LSIS | MC-265a | 240 |  | 10 | 192 | - | 240
LSIS508.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS508.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS508.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS508.04 |  | OLR | LSIS | MT-400 |  |  | 10 | 160 - 240 | -
LSIS509 | D [ version C3(a)] | ICB | LSIS | UTS400H MCP | 600 | 3 | - | 320 | - | 600 | 3 | 25 | 192 | 200 | 7447 | 1
|  | MC | LSIS | MC-330a | 240 |  | 18 | 242 | - | 240
LSIS509.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS509.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS509.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS509.04 |  | OLR | LSIS | MT-400 |  |  | 18 | 160 - 240 | -
LSIS510 | D [ version C3(a)] | ICB | LSIS | UTS400L MCP | 600 | 3 | - | 320 | - | 600 | 3 | 50 | 192 | 200 | 7447 | 1
|  | MC | LSIS | MC-330a | 240 |  | 18 | 242 | - | 240
LSIS510.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS510.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS510.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS510.04 |  | OLR | LSIS | MT-400 |  |  | 18 | 160 - 240 | -
LSIS511 | D [ version C3(a)] | ICB | LSIS | UTS600H MCP | 600 | 3 | - | 500 | - | 600 | 3 | 25 | 289 | 300 | 7447 | 1
|  | MC | LSIS | MC-400a |  |  | 18 | 289 | -
LSIS511.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS511.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS511.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS511.04 |  | OLR | LSIS | MT-400 |  |  | 18 | 160 - 240 | -
LSIS511.05 |  | OLR | LSIS | MT-400 |  |  | 18 | 200 - 330 | -
LSIS511.06 |  | OLR | LSIS | MT-400 |  |  | 18 | 260 - 400 | -
LSIS512 | D [ version C3(a)] | ICB | LSIS | UTS600L MCP | 600 | 3 | - | 500 | - | 600 | 3 | 50 | 289 | 300 | 7447 | 1
|  | MC | LSIS | MC-400a |  |  | 18 | 289 | -
LSIS512.01 |  | OLR | LSIS | MT-400 |  |  | 10 | 85 - 125 | -
LSIS512.02 |  | OLR | LSIS | MT-400 |  |  | 10 | 100 - 160 | -
LSIS512.03 |  | OLR | LSIS | MT-400 |  |  | 10 | 120 - 185 | -
LSIS512.04 |  | OLR | LSIS | MT-400 |  |  | 18 | 160 - 240 | -
LSIS512.05 |  | OLR | LSIS | MT-400 |  |  | 18 | 200 - 330 | -
LSIS512.06 |  | OLR | LSIS | MT-400 |  |  | 18 | 260 - 400 | -
LSIS513 | D [ version C3(a)] | ICB | LSIS | UTS800L MCP | 600 | 3 | - | 800 | - | 600 | 3 | 50 | 382 | 400 | 15980 | 1
|  | MC | LSIS | MC-500a |  |  | 18 | 382 | -
LSIS513.01 |  | OLR | LSIS | MT-800 |  |  | 18 | 200 - 330 | -
LSIS513.02 |  | OLR | LSIS | MT-800 |  |  | 18 | 260 - 400 | -
LSIS514 | D [ version C3(a)] | ICB | LSIS | UTS800L MCP | 600 | 3 | - | 800 | - | 600 | 3 | 50 | 472 | 500 | 15980 | 1
|  | MC | LSIS | MC-630a |  |  | 30 | 472 | -
LSIS514.01 |  | OLR | LSIS | MT-800 |  |  | 18 | 200 - 330 | -
LSIS514.02 |  | OLR | LSIS | MT-800 |  |  | 18 | 260 - 400 | -
LSIS514.03 |  | OLR | LSIS | MT-800 |  |  | 18 | 400 - 600 | -

## Type E
Issued: 2017-01-31
Revised: 2022-07-27
Database Identification Number | Listed Combination Motor Controller Information |  |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | Conditions of Use
Listing Report Information
| UL File Number |  | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating
LSIS1701 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 65 | 0.1~0.16 |  | 240 | 3 | 100 | 0.16 | - | 2929 | 1 | 0.1~0.16 | MMS-32H 0.1~0.16 240 | MMS-32H 0.1...0.16 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [7 empty] | 1 | - | TB-32 - | LAM -
LSIS1702 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 65 | 0.16~0.25 |  | 240 | 3 | 100 | 0.25 | - | 2929 | 1 | 0.16~0.25 | MMS-32H 0.16~0.25 240 | MMS-32H 0.16...0.25 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [7 empty] | 1 | - | TB-32 - | LAM -
LSIS1703 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 65 | 0.25~0.4 |  | 240 | 3 | 100 | 0.4 | - | 2929 | 1 | 0.25~0.4 | MMS-32H 0.25~0.4 240 | MMS-32H 0.25...0.4 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [7 empty] | 1 | - | TB-32 - | LAM -
LSIS1704 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 65 | 0.4~0.63 |  | 240 | 3 | 100 | 0.63 | - | 2929 | 1 | 0.4~0.63 | MMS-32H 0.4~0.63 240 | MMS-32H 0.4...0.63 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [7 empty] | 1 | - | TB-32 - | LAM -
LSIS1705 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 65 | 0.63~1 |  | 240 | 3 | 100 | 1 | - | 2929 | 1 | 0.63~1 | MMS-32H 0.63~1 240 | MMS-32H 0.63...1 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1706 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 65 | 1~1.6 |  | 240 | 3 | 100 | 1.6 | - | 2929 | 1 | 1~1.6 | MMS-32H 1~1.6 240 | MMS-32H 1...1.6 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1707 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 1.6~2.5 |  | 240 | 3 | 100 | 2.2 | 0.5 | 2929 | 1 | 1.6~2.5 | MMS-32H 1.6~2.5 240 | MMS-32H 1.6...2.5 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1708 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 2.5~4 |  | 240 | 3 | 100 | 3.2 | 0.75 | 2929 | 1 | 2.5~4 | MMS-32H 2.5~4 240 | MMS-32H 2.5...4 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1709 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 4~6 |  | 240 | 3 | 100 | 6 | 1.5 | 2929 | 1 | 4~6 | MMS-32H 4~6 240 | MMS-32H 4...6 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1710 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 5~8 |  | 240 | 3 | 100 | 6.8 | 2 | 2929 | 1 | 5~8 | MMS-32H 5~8 240 | MMS-32H 5...8 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1711 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 6~10 |  | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1 | 6~10 | MMS-32H 6~10 240 | MMS-32H 6...10 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1712 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 9~13 |  | 240 | 3 | 100 | 9.6 | 5 | 2929 | 1 | 9~13 | MMS-32H 9~13 240 | MMS-32H 9...13 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1713 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 11~17 |  | 240 | 3 | 100 | 15.2 | 7.5 | 2929 | 1 | 11~17 | MMS-32H 11~17 240 | MMS-32H 11...17 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1714 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 14~22 |  | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1 | 14~22 | MMS-32H 14~22 240 | MMS-32H 14...22 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1715 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 18~26 |  | 240 | 3 | 100 | 22 | 10 | 2929 | 1 | 18~26 | MMS-32H 18~26 240 | MMS-32H 18...26 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1716 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 22~32 |  | 240 | 3 | 100 | 28 | 10 | 2929 | 1 | 22~32 | MMS-32H 22~32 240 | MMS-32H 22...32 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1717 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 28~40 |  | 240 | 3 | 100 | 28 | 10 | 2929 | 1 | 28~40 | MMS-32H 28~40 240 | MMS-32H 28...40 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1718 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.1~0.16 |  | 480Y | 3 | 65 | 0.16 | - | 2929 | 1 | 0.1~0.16 | MMS-32H 0.1~0.16 480Y | MMS-32H 0.1...0.16 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [7 empty] | 1 | - | TB-32 - | LAM -
LSIS1719 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.16~0.25 |  | 480Y | 3 | 65 | 0.25 | - | 2929 | 1 | 0.16~0.25 | MMS-32H 0.16~0.25 480Y | MMS-32H 0.16...0.25 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [7 empty] | 1 | - | TB-32 - | LAM -
LSIS1720 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.25~0.4 |  | 480Y | 3 | 65 | 0.4 | - | 2929 | 1 | 0.25~0.4 | MMS-32H 0.25~0.4 480Y | MMS-32H 0.25...0.4 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [7 empty] | 1 | - | TB-32 - | LAM -
LSIS1721 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.4~0.63 |  | 480Y | 3 | 65 | 0.63 | - | 2929 | 1 | 0.4~0.63 | MMS-32H 0.4~0.63 480Y | MMS-32H 0.4...0.63 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [7 empty] | 1 | - | TB-32 - | LAM -
LSIS1722 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.63~1 |  | 480Y | 3 | 65 | 1 | - | 2929 | 1 | 0.63~1 | MMS-32H 0.63~1 480Y | MMS-32H 0.63...1 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1723 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 1~1.6 |  | 480Y | 3 | 65 | 1.6 | 0.75 | 2929 | 1 | 1~1.6 | MMS-32H 1~1.6 480Y | MMS-32H 1...1.6 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1724 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 1.6~2.5 |  | 480Y | 3 | 65 | 2.1 | 1 | 2929 | 1 | 1.6~2.5 | MMS-32H 1.6~2.5 480Y | MMS-32H 1.6...2.5 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1725 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 2.5~4 |  | 480Y | 3 | 65 | 3.4 | 2 | 2929 | 1 | 2.5~4 | MMS-32H 2.5~4 480Y | MMS-32H 2.5...4 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1726 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 4~6 |  | 480Y | 3 | 65 | 4.8 | 3 | 2929 | 1 | 4~6 | MMS-32H 4~6 480Y | MMS-32H 4...6 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1727 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 5~8 |  | 480Y | 3 | 65 | 7.6 | 5 | 2929 | 1 | 5~8 | MMS-32H 5~8 480Y | MMS-32H 5...8 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1728 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 6~10 |  | 480Y | 3 | 65 | 7.6 | 5 | 2929 | 1 | 6~10 | MMS-32H 6~10 480Y | MMS-32H 6...10 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1729 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 9~13 |  | 480Y | 3 | 65 | 11 | 7.5 | 2929 | 1 | 9~13 | MMS-32H 9~13 480Y | MMS-32H 9...13 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1730 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 11~17 |  | 480Y | 3 | 65 | 14 | 10 | 2929 | 1 | 11~17 | MMS-32H 11~17 480Y | MMS-32H 11...17 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1731 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 14~22 |  | 480Y | 3 | 65 | 21 | 15 | 2929 | 1 | 14~22 | MMS-32H 14~22 480Y | MMS-32H 14...22 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1732 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 18~26 |  | 480Y | 3 | 65 | 21 | 15 | 2929 | 1 | 18~26 | MMS-32H 18~26 480Y | MMS-32H 18...26 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1733 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 22~32 |  | 480Y | 3 | 65 | 27 | 20 | 2929 | 1 | 22~32 | MMS-32H 22~32 480Y | MMS-32H 22...32 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1734 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 28~40 |  | 480Y | 3 | 65 | 27 | 20 | 2929 | 1 | 28~40 | MMS-32H 28~40 480Y | MMS-32H 28...40 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1735 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.1~0.16 |  | 600Y | 3 | 25 | 0.16 | - | 2929 | 1 | 0.1~0.16 | MMS-32H 0.1~0.16 600Y | MMS-32H 0.1...0.16 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [7 empty] | 1 | - | TB-32 - | LAM -
LSIS1736 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.16~0.25 |  | 600Y | 3 | 25 | 0.25 | - | 2929 | 1 | 0.16~0.25 | MMS-32H 0.16~0.25 600Y | MMS-32H 0.16...0.25 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [7 empty] | 1 | - | TB-32 - | LAM -
LSIS1737 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.25~0.4 |  | 600Y | 3 | 25 | 0.4 | - | 2929 | 1 | 0.25~0.4 | MMS-32H 0.25~0.4 600Y | MMS-32H 0.25...0.4 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [7 empty] | 1 | - | TB-32 - | LAM -
LSIS1738 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.4~0.63 |  | 600Y | 3 | 25 | 0.63 | - | 2929 | 1 | 0.4~0.63 | MMS-32H 0.4~0.63 600Y | MMS-32H 0.4...0.63 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [7 empty] | 1 | - | TB-32 - | LAM -
LSIS1739 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.63~1 |  | 600Y | 3 | 25 | 0.9 | 0.5 | 2929 | 1 | 0.63~1 | MMS-32H 0.63~1 600Y | MMS-32H 0.63...1 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1740 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 1~1.6 |  | 600Y | 3 | 25 | 1.3 | 0.75 | 2929 | 1 | 1~1.6 | MMS-32H 1~1.6 600Y | MMS-32H 1...1.6 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1741 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 1.6~2.5 |  | 600Y | 3 | 25 | 2.4 | 1.5 | 2929 | 1 | 1.6~2.5 | MMS-32H 1.6~2.5 600Y | MMS-32H 1.6...2.5 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1742 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 2.5~4 |  | 600Y | 3 | 25 | 3.9 | 3 | 2929 | 1 | 2.5~4 | MMS-32H 2.5~4 600Y | MMS-32H 2.5...4 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1743 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 4~6 |  | 600Y | 3 | 25 | 6.1 | 5 | 2929 | 1 | 4~6 | MMS-32H 4~6 600Y | MMS-32H 4...6 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1744 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 5~8 |  | 600Y | 3 | 10 | 6.1 | 5 | 2929 | 1 | 5~8 | MMS-32H 5~8 600Y | MMS-32H 5...8 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1745 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 6~10 |  | 600Y | 3 | 10 | 9 | 7.5 | 2929 | 1 | 6~10 | MMS-32H 6~10 600Y | MMS-32H 6...10 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1746 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 9~13 |  | 600Y | 3 | 10 | 11 | 10 | 2929 | 1 | 9~13 | MMS-32H 9~13 600Y | MMS-32H 9...13 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1747 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 11~17 |  | 600Y | 3 | 10 | 17 | 15 | 2929 | 1 | 11~17 | MMS-32H 11~17 600Y | MMS-32H 11...17 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1748 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 14~22 |  | 600Y | 3 | 10 | 22 | 20 | 2929 | 1 | 14~22 | MMS-32H 14~22 600Y | MMS-32H 14...22 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1749 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 18~26 |  | 600Y | 3 | 10 | 22 | 20 | 2929 | 1 | 18~26 | MMS-32H 18~26 600Y | MMS-32H 18...26 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1750 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 22~32 |  | 600Y | 3 | 10 | 32 | 30 | 2929 | 1 | 22~32 | MMS-32H 22~32 600Y | MMS-32H 22...32 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1751 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 28~40 |  | 600Y | 3 | 10 | 32 | 30 | 2929 | 1 | 28~40 | MMS-32H 28~40 600Y | MMS-32H 28...40 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | LSIS | TB-32 |  |  | - | - | [6 empty] | 2929 | 1 | - | TB-32 - | LAM -
LSIS1752 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.1~0.16 |  | 240 | 3 | 100 | 0.16 | - | 2929 | 1 | 0.1~0.16 | MMS-32H 0.1~0.16 240 | MMS-32H 0.1...0.16 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [7 empty] | 1 | - | 3RV1928-1H - | LAM -
LSIS1753 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.16~0.25 |  | 240 | 3 | 100 | 0.25 | - | 2929 | 1 | 0.16~0.25 | MMS-32H 0.16~0.25 240 | MMS-32H 0.16...0.25 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [7 empty] | 1 | - | 3RV1928-1H - | LAM -
LSIS1754 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.25~0.4 |  | 240 | 3 | 100 | 0.4 | - | 2929 | 1 | 0.25~0.4 | MMS-32H 0.25~0.4 240 | MMS-32H 0.25...0.4 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [7 empty] | 1 | - | 3RV1928-1H - | LAM -
LSIS1755 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.4~0.63 |  | 240 | 3 | 100 | 0.63 | - | 2929 | 1 | 0.4~0.63 | MMS-32H 0.4~0.63 240 | MMS-32H 0.4...0.63 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [7 empty] | 1 | - | 3RV1928-1H - | LAM -
LSIS1756 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.63~1 |  | 240 | 3 | 100 | 1 | - | 2929 | 1 | 0.63~1 | MMS-32H 0.63~1 240 | MMS-32H 0.63...1 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS1757 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 1~1.6 |  | 240 | 3 | 100 | 1.6 | - | 2929 | 1 | 1~1.6 | MMS-32H 1~1.6 240 | MMS-32H 1...1.6 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS607 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 1.6~2.5 |  | 240 | 3 | 100 | 2.2 | 0.5 | 2929 | 1 | 1.6~2.5 | MMS-32H 1.6~2.5 240 | MMS-32H 1.6...2.5 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS608 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 2.5~4 |  | 240 | 3 | 100 | 3.2 | 0.75 | 2929 | 1 | 2.5~4 | MMS-32H 2.5~4 240 | MMS-32H 2.5...4 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS609 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 4~6 |  | 240 | 3 | 100 | 6 | 1.5 | 2929 | 1 | 4~6 | MMS-32H 4~6 240 | MMS-32H 4...6 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS610 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 5~8 |  | 240 | 3 | 100 | 6.8 | 2 | 2929 | 1 | 5~8 | MMS-32H 5~8 240 | MMS-32H 5...8 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS611 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 6~10 |  | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1 | 6~10 | MMS-32H 6~10 240 | MMS-32H 6...10 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS612 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 9~13 |  | 240 | 3 | 100 | 9.6 | 5 | 2929 | 1 | 9~13 | MMS-32H 9~13 240 | MMS-32H 9...13 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS613 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 11~17 |  | 240 | 3 | 100 | 15.2 | 7.5 | 2929 | 1 | 11~17 | MMS-32H 11~17 240 | MMS-32H 11...17 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS614 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 14~22 |  | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1 | 14~22 | MMS-32H 14~22 240 | MMS-32H 14...22 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS615 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 18~26 |  | 240 | 3 | 100 | 22 | 10 | 2929 | 1 | 18~26 | MMS-32H 18~26 240 | MMS-32H 18...26 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS616 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 22~32 |  | 240 | 3 | 100 | 28 | 10 | 2929 | 1 | 22~32 | MMS-32H 22~32 240 | MMS-32H 22...32 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS617 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 28~40 |  | 240 | 3 | 100 | 28 | 10 | 2929 | 1 | 28~40 | MMS-32H 28~40 240 | MMS-32H 28...40 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS618 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 6~10 |  | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1 | 6~10 | MMS-63S 6~10 240 | MMS-63S 6...10 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS619 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 9~13 |  | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1 | 9~13 | MMS-63S 9~13 240 | MMS-63S 9...13 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS620 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 11~17 |  | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1 | 11~17 | MMS-63S 11~17 240 | MMS-63S 11...17 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS621 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 14~22 |  | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1 | 14~22 | MMS-63S 14~22 240 | MMS-63S 14...22 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS622 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 18~26 |  | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1 | 18~26 | MMS-63S 18~26 240 | MMS-63S 18...26 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS623 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 22~32 |  | 240 | 3 | 100 | 28 | 10 | 2929 | 1 | 22~32 | MMS-63S 22~32 240 | MMS-63S 22...32 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS624 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 28~40 |  | 240 | 3 | 100 | 28 | 10 | 2929 | 1 | 28~40 | MMS-63S 28~40 240 | MMS-63S 28...40 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS625 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 34~50 |  | 240 | 3 | 100 | 42 | 15 | 2929 | 1 | 34~50 | MMS-63S 34~50 240 | MMS-63S 34...50 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS626 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 45~63 |  | 240 | 3 | 100 | 52 | 20 | 2929 | 1 | 45~63 | MMS-63S 45~63 240 | MMS-63S 45...63 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS627 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 47~65 |  | 240 | 3 | 100 | 52 | 20 | 2929 | 1 | 47~65 | MMS-63S 47~65 240 | MMS-63S 47...65 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS628 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 6~10 |  | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1 | 6~10 | MMS-63H 6~10 240 | MMS-63H 6...10 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS629 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 9~13 |  | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1 | 9~13 | MMS-63H 9~13 240 | MMS-63H 9...13 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS630 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 11~17 |  | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1 | 11~17 | MMS-63H 11~17 240 | MMS-63H 11...17 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS631 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 14~22 |  | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1 | 14~22 | MMS-63H 14~22 240 | MMS-63H 14...22 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS632 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 18~26 |  | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1 | 18~26 | MMS-63H 18~26 240 | MMS-63H 18...26 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS633 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 22~32 |  | 240 | 3 | 100 | 28 | 10 | 2929 | 1 | 22~32 | MMS-63H 22~32 240 | MMS-63H 22...32 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS634 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 28~40 |  | 240 | 3 | 100 | 28 | 10 | 2929 | 1 | 28~40 | MMS-63H 28~40 240 | MMS-63H 28...40 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS635 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 34~50 |  | 240 | 3 | 100 | 42 | 15 | 2929 | 1 | 34~50 | MMS-63H 34~50 240 | MMS-63H 34...50 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS636 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 45~63 |  | 240 | 3 | 100 | 52 | 20 | 2929 | 1 | 45~63 | MMS-63H 45~63 240 | MMS-63H 45...63 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS637 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 47~65 |  | 240 | 3 | 100 | 52 | 20 | 2929 | 1 | 47~65 | MMS-63H 47~65 240 | MMS-63H 47...65 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS638 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 11~17 |  | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1 | 11~17 | MMS-100S 11~17 240 | MMS-100S 11...17 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS639 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 14~22 |  | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1 | 14~22 | MMS-100S 14~22 240 | MMS-100S 14...22 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS640 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 18~26 |  | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1 | 18~26 | MMS-100S 18~26 240 | MMS-100S 18...26 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS641 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 22~32 |  | 240 | 3 | 100 | 28 | 10 | 2929 | 1 | 22~32 | MMS-100S 22~32 240 | MMS-100S 22...32 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS642 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 28~40 |  | 240 | 3 | 100 | 28 | 10 | 2929 | 1 | 28~40 | MMS-100S 28~40 240 | MMS-100S 28...40 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS643 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 34~50 |  | 240 | 3 | 100 | 42 | 15 | 2929 | 1 | 34~50 | MMS-100S 34~50 240 | MMS-100S 34...50 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS644 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 45~63 |  | 240 | 3 | 100 | 54 | 20 | 2929 | 1 | 45~63 | MMS-100S 45~63 240 | MMS-100S 45...63 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS645 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 55~75 |  | 240 | 3 | 100 | 68 | 25 | 2929 | 1 | 55~75 | MMS-100S 55~75 240 | MMS-100S 55...75 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS646 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 70~90 |  | 240 | 3 | 100 | 80 | 30 | 2929 | 1 | 70~90 | MMS-100S 70~90 240 | MMS-100S 70...90 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS647 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 80~100 |  | 240 | 3 | 100 | 80 | 30 | 2929 | 1 | 80~100 | MMS-100S 80~100 240 | MMS-100S 80...100 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS648 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 11~17 |  | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1 | 11~17 | MMS-100H 11~17 240 | MMS-100H 11...17 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS649 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 14~22 |  | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1 | 14~22 | MMS-100H 14~22 240 | MMS-100H 14...22 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS650 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 18~26 |  | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1 | 18~26 | MMS-100H 18~26 240 | MMS-100H 18...26 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS651 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 22~32 |  | 240 | 3 | 100 | 28 | 10 | 2929 | 1 | 22~32 | MMS-100H 22~32 240 | MMS-100H 22...32 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS652 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 28~40 |  | 240 | 3 | 100 | 28 | 10 | 2929 | 1 | 28~40 | MMS-100H 28~40 240 | MMS-100H 28...40 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS653 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 34~50 |  | 240 | 3 | 100 | 42 | 15 | 2929 | 1 | 34~50 | MMS-100H 34~50 240 | MMS-100H 34...50 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS654 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 45~63 |  | 240 | 3 | 100 | 54 | 20 | 2929 | 1 | 45~63 | MMS-100H 45~63 240 | MMS-100H 45...63 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS655 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 55~75 |  | 240 | 3 | 100 | 68 | 25 | 2929 | 1 | 55~75 | MMS-100H 55~75 240 | MMS-100H 55...75 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS656 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 70~90 |  | 240 | 3 | 100 | 80 | 30 | 2929 | 1 | 70~90 | MMS-100H 70~90 240 | MMS-100H 70...90 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS657 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 80~100 |  | 240 | 3 | 100 | 80 | 30 | 2929 | 1 | 80~100 | MMS-100H 80~100 240 | MMS-100H 80...100 240
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS658 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.1~0.16 |  | 480Y | 3 | 65 | 0.16 | - | 2929 | 1 | 0.1~0.16 | MMS-32H 0.1~0.16 480Y | MMS-32H 0.1...0.16 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [7 empty] | 1 | - | 3RV1928-1H - | LAM -
LSIS659 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.16~0.25 |  | 480Y | 3 | 65 | 0.25 | - | 2929 | 1 | 0.16~0.25 | MMS-32H 0.16~0.25 480Y | MMS-32H 0.16...0.25 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [7 empty] | 1 | - | 3RV1928-1H - | LAM -
LSIS660 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.25~0.4 |  | 480Y | 3 | 65 | 0.4 | - | 2929 | 1 | 0.25~0.4 | MMS-32H 0.25~0.4 480Y | MMS-32H 0.25...0.4 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [7 empty] | 1 | - | 3RV1928-1H - | LAM -
LSIS661 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.4~0.63 |  | 480Y | 3 | 65 | 0.63 | - | 2929 | 1 | 0.4~0.63 | MMS-32H 0.4~0.63 480Y | MMS-32H 0.4...0.63 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [7 empty] | 1 | - | 3RV1928-1H - | LAM -
LSIS662 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.63~1 |  | 480Y | 3 | 65 | 1 | - | 2929 | 1 | 0.63~1 | MMS-32H 0.63~1 480Y | MMS-32H 0.63...1 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS663 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 1~1.6 |  | 480Y | 3 | 65 | 1.6 | 0.75 | 2929 | 1 | 1~1.6 | MMS-32H 1~1.6 480Y | MMS-32H 1...1.6 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS664 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 1.6~2.5 |  | 480Y | 3 | 65 | 2.1 | 1 | 2929 | 1 | 1.6~2.5 | MMS-32H 1.6~2.5 480Y | MMS-32H 1.6...2.5 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS665 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 2.5~4 |  | 480Y | 3 | 65 | 3.4 | 2 | 2929 | 1 | 2.5~4 | MMS-32H 2.5~4 480Y | MMS-32H 2.5...4 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS666 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 4~6 |  | 480Y | 3 | 65 | 4.8 | 3 | 2929 | 1 | 4~6 | MMS-32H 4~6 480Y | MMS-32H 4...6 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS667 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 5~8 |  | 480Y | 3 | 65 | 7.6 | 5 | 2929 | 1 | 5~8 | MMS-32H 5~8 480Y | MMS-32H 5...8 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS668 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 6~10 |  | 480Y | 3 | 65 | 7.6 | 5 | 2929 | 1 | 6~10 | MMS-32H 6~10 480Y | MMS-32H 6...10 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS669 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 9~13 |  | 480Y | 3 | 65 | 11 | 7.5 | 2929 | 1 | 9~13 | MMS-32H 9~13 480Y | MMS-32H 9...13 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS670 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 11~17 |  | 480Y | 3 | 65 | 14 | 10 | 2929 | 1 | 11~17 | MMS-32H 11~17 480Y | MMS-32H 11...17 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS671 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 14~22 |  | 480Y | 3 | 65 | 21 | 15 | 2929 | 1 | 14~22 | MMS-32H 14~22 480Y | MMS-32H 14...22 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS672 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 18~26 |  | 480Y | 3 | 65 | 21 | 15 | 2929 | 1 | 18~26 | MMS-32H 18~26 480Y | MMS-32H 18...26 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS673 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 22~32 |  | 480Y | 3 | 65 | 27 | 20 | 2929 | 1 | 22~32 | MMS-32H 22~32 480Y | MMS-32H 22...32 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS674 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 28~40 |  | 480Y | 3 | 65 | 27 | 20 | 2929 | 1 | 28~40 | MMS-32H 28~40 480Y | MMS-32H 28...40 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS675 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 480Y | 3 | 50 | 6~10 |  | 480Y | 3 | 50 | 7.6 | 5 | 2929 | 1 | 6~10 | MMS-63S 6~10 480Y | MMS-63S 6...10 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS676 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 480Y | 3 | 50 | 9~13 |  | 480Y | 3 | 50 | 11 | 7.5 | 2929 | 1 | 9~13 | MMS-63S 9~13 480Y | MMS-63S 9...13 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS677 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 11~17 |  | 480Y | 3 | 40 | 14 | 10 | 2929 | 1 | 11~17 | MMS-63S 11~17 480Y | MMS-63S 11...17 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS678 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 14~22 |  | 480Y | 3 | 40 | 21 | 15 | 2929 | 1 | 14~22 | MMS-63S 14~22 480Y | MMS-63S 14...22 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS679 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 18~26 |  | 480Y | 3 | 40 | 21 | 15 | 2929 | 1 | 18~26 | MMS-63S 18~26 480Y | MMS-63S 18...26 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS680 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 22~32 |  | 480Y | 3 | 40 | 27 | 20 | 2929 | 1 | 22~32 | MMS-63S 22~32 480Y | MMS-63S 22...32 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS681 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 28~40 |  | 480Y | 3 | 40 | 40 | 30 | 2929 | 1 | 28~40 | MMS-63S 28~40 480Y | MMS-63S 28...40 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS682 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 34~50 |  | 480Y | 3 | 40 | 40 | 30 | 2929 | 1 | 34~50 | MMS-63S 34~50 480Y | MMS-63S 34...50 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS683 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 45~63 |  | 480Y | 3 | 40 | 52 | 40 | 2929 | 1 | 45~63 | MMS-63S 45~63 480Y | MMS-63S 45...63 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS684 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 47~65 |  | 480Y | 3 | 40 | 52 | 40 | 2929 | 1 | 47~65 | MMS-63S 47~65 480Y | MMS-63S 47...65 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS685 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 480Y | 3 | 65 | 6~10 |  | 480Y | 3 | 65 | 7.6 | 5 | 2929 | 1 | 6~10 | MMS-63H 6~10 480Y | MMS-63H 6...10 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS686 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 480Y | 3 | 65 | 9~13 |  | 480Y | 3 | 65 | 11 | 7.5 | 2929 | 1 | 9~13 | MMS-63H 9~13 480Y | MMS-63H 9...13 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS687 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 11~17 |  | 480Y | 3 | 50 | 14 | 10 | 2929 | 1 | 11~17 | MMS-63H 11~17 480Y | MMS-63H 11...17 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS688 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 14~22 |  | 480Y | 3 | 50 | 21 | 15 | 2929 | 1 | 14~22 | MMS-63H 14~22 480Y | MMS-63H 14...22 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS689 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 18~26 |  | 480Y | 3 | 50 | 21 | 15 | 2929 | 1 | 18~26 | MMS-63H 18~26 480Y | MMS-63H 18...26 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS690 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 22~32 |  | 480Y | 3 | 50 | 27 | 20 | 2929 | 1 | 22~32 | MMS-63H 22~32 480Y | MMS-63H 22...32 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS691 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 28~40 |  | 480Y | 3 | 50 | 40 | 30 | 2929 | 1 | 28~40 | MMS-63H 28~40 480Y | MMS-63H 28...40 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS692 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 34~50 |  | 480Y | 3 | 50 | 40 | 30 | 2929 | 1 | 34~50 | MMS-63H 34~50 480Y | MMS-63H 34...50 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS693 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 45~63 |  | 480Y | 3 | 50 | 52 | 40 | 2929 | 1 | 45~63 | MMS-63H 45~63 480Y | MMS-63H 45...63 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS694 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 47~65 |  | 480Y | 3 | 50 | 52 | 40 | 2929 | 1 | 47~65 | MMS-63H 47~65 480Y | MMS-63H 47...65 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS695 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 11~17 |  | 480Y | 3 | 50 | 14 | 10 | 2929 | 1 | 11~17 | MMS-100S 11~17 480Y | MMS-100S 11...17 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS696 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 14~22 |  | 480Y | 3 | 50 | 21 | 15 | 2929 | 1 | 14~22 | MMS-100S 14~22 480Y | MMS-100S 14...22 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS697 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 18~26 |  | 480Y | 3 | 50 | 21 | 15 | 2929 | 1 | 18~26 | MMS-100S 18~26 480Y | MMS-100S 18...26 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS698 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 22~32 |  | 480Y | 3 | 50 | 27 | 20 | 2929 | 1 | 22~32 | MMS-100S 22~32 480Y | MMS-100S 22...32 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS699 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 28~40 |  | 480Y | 3 | 50 | 40 | 30 | 2929 | 1 | 28~40 | MMS-100S 28~40 480Y | MMS-100S 28...40 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS700 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 34~50 |  | 480Y | 3 | 50 | 40 | 30 | 2929 | 1 | 34~50 | MMS-100S 34~50 480Y | MMS-100S 34...50 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS701 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 480Y | 3 | 40 | 45~63 |  | 480Y | 3 | 40 | 52 | 40 | 2929 | 1 | 45~63 | MMS-100S 45~63 480Y | MMS-100S 45...63 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS702 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 480Y | 3 | 40 | 55~75 |  | 480Y | 3 | 40 | 65 | 50 | 2929 | 1 | 55~75 | MMS-100S 55~75 480Y | MMS-100S 55...75 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS703 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 480Y | 3 | 40 | 70~90 |  | 480Y | 3 | 40 | 77 | 60 | 2929 | 1 | 70~90 | MMS-100S 70~90 480Y | MMS-100S 70...90 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS704 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 480Y | 3 | 40 | 80~100 |  | 480Y | 3 | 40 | 96 | 75 | 2929 | 1 | 80~100 | MMS-100S 80~100 480Y | MMS-100S 80...100 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS705 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 11~17 |  | 480Y | 3 | 65 | 14 | 10 | 2929 | 1 | 11~17 | MMS-100H 11~17 480Y | MMS-100H 11...17 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS706 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 14~22 |  | 480Y | 3 | 65 | 21 | 15 | 2929 | 1 | 14~22 | MMS-100H 14~22 480Y | MMS-100H 14...22 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS707 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 18~26 |  | 480Y | 3 | 65 | 21 | 15 | 2929 | 1 | 18~26 | MMS-100H 18~26 480Y | MMS-100H 18...26 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS708 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 22~32 |  | 480Y | 3 | 65 | 27 | 20 | 2929 | 1 | 22~32 | MMS-100H 22~32 480Y | MMS-100H 22...32 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS709 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 28~40 |  | 480Y | 3 | 65 | 40 | 30 | 2929 | 1 | 28~40 | MMS-100H 28~40 480Y | MMS-100H 28...40 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS710 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 34~50 |  | 480Y | 3 | 65 | 40 | 30 | 2929 | 1 | 34~50 | MMS-100H 34~50 480Y | MMS-100H 34...50 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS711 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 480Y | 3 | 50 | 45~63 |  | 480Y | 3 | 50 | 52 | 40 | 2929 | 1 | 45~63 | MMS-100H 45~63 480Y | MMS-100H 45...63 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS712 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 480Y | 3 | 50 | 55~75 |  | 480Y | 3 | 50 | 65 | 50 | 2929 | 1 | 55~75 | MMS-100H 55~75 480Y | MMS-100H 55...75 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS713 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 480Y | 3 | 50 | 70~90 |  | 480Y | 3 | 50 | 77 | 60 | 2929 | 1 | 70~90 | MMS-100H 70~90 480Y | MMS-100H 70...90 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS714 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 480Y | 3 | 50 | 80~100 |  | 480Y | 3 | 50 | 96 | 75 | 2929 | 1 | 80~100 | MMS-100H 80~100 480Y | MMS-100H 80...100 480Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS715 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.1~0.16 |  | 600Y | 3 | 25 | 0.16 | - | 2929 | 1 | 0.1~0.16 | MMS-32H 0.1~0.16 600Y | MMS-32H 0.1...0.16 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [7 empty] | 1 | - | 3RV1928-1H - | LAM -
LSIS716 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.16~0.25 |  | 600Y | 3 | 25 | 0.25 | - | 2929 | 1 | 0.16~0.25 | MMS-32H 0.16~0.25 600Y | MMS-32H 0.16...0.25 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [7 empty] | 1 | - | 3RV1928-1H - | LAM -
LSIS717 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.25~0.4 |  | 600Y | 3 | 25 | 0.4 | - | 2929 | 1 | 0.25~0.4 | MMS-32H 0.25~0.4 600Y | MMS-32H 0.25...0.4 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [7 empty] | 1 | - | 3RV1928-1H - | LAM -
LSIS718 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.4~0.63 |  | 600Y | 3 | 25 | 0.63 | - | 2929 | 1 | 0.4~0.63 | MMS-32H 0.4~0.63 600Y | MMS-32H 0.4...0.63 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [7 empty] | 1 | - | 3RV1928-1H - | LAM -
LSIS719 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.63~1 |  | 600Y | 3 | 25 | 0.9 | 0.5 | 2929 | 1 | 0.63~1 | MMS-32H 0.63~1 600Y | MMS-32H 0.63...1 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS720 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 1~1.6 |  | 600Y | 3 | 25 | 1.3 | 0.75 | 2929 | 1 | 1~1.6 | MMS-32H 1~1.6 600Y | MMS-32H 1...1.6 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS721 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 1.6~2.5 |  | 600Y | 3 | 25 | 2.4 | 1.5 | 2929 | 1 | 1.6~2.5 | MMS-32H 1.6~2.5 600Y | MMS-32H 1.6...2.5 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS722 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 2.5~4 |  | 600Y | 3 | 25 | 3.9 | 3 | 2929 | 1 | 2.5~4 | MMS-32H 2.5~4 600Y | MMS-32H 2.5...4 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS723 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 4~6 |  | 600Y | 3 | 25 | 6.1 | 5 | 2929 | 1 | 4~6 | MMS-32H 4~6 600Y | MMS-32H 4...6 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS724 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 5~8 |  | 600Y | 3 | 10 | 6.1 | 5 | 2929 | 1 | 5~8 | MMS-32H 5~8 600Y | MMS-32H 5...8 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS725 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 6~10 |  | 600Y | 3 | 10 | 9 | 7.5 | 2929 | 1 | 6~10 | MMS-32H 6~10 600Y | MMS-32H 6...10 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS726 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 9~13 |  | 600Y | 3 | 10 | 11 | 10 | 2929 | 1 | 9~13 | MMS-32H 9~13 600Y | MMS-32H 9...13 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS727 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 11~17 |  | 600Y | 3 | 10 | 17 | 15 | 2929 | 1 | 11~17 | MMS-32H 11~17 600Y | MMS-32H 11...17 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS728 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 14~22 |  | 600Y | 3 | 10 | 22 | 20 | 2929 | 1 | 14~22 | MMS-32H 14~22 600Y | MMS-32H 14...22 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS729 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 18~26 |  | 600Y | 3 | 10 | 22 | 20 | 2929 | 1 | 18~26 | MMS-32H 18~26 600Y | MMS-32H 18...26 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS730 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 22~32 |  | 600Y | 3 | 10 | 32 | 30 | 2929 | 1 | 22~32 | MMS-32H 22~32 600Y | MMS-32H 22...32 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS731 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 28~40 |  | 600Y | 3 | 10 | 32 | 30 | 2929 | 1 | 28~40 | MMS-32H 28~40 600Y | MMS-32H 28...40 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | -
[5 empty] | Line Side Adapter | Siemens | 3RV1928-1H |  |  | - | - | [6 empty] | 2929 | 1 | - | 3RV1928-1H - | LAM -
LSIS732 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 6~10 |  | 600Y | 3 | 10 | 9 | 7.5 | 2929 | 1 | 6~10 | MMS-63S 6~10 600Y | MMS-63S 6...10 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS733 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 9~13 |  | 600Y | 3 | 10 | 11 | 10 | 2929 | 1 | 9~13 | MMS-63S 9~13 600Y | MMS-63S 9...13 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS734 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 11~17 |  | 600Y | 3 | 10 | 17 | 15 | 2929 | 1 | 11~17 | MMS-63S 11~17 600Y | MMS-63S 11...17 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS735 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 14~22 |  | 600Y | 3 | 10 | 22 | 20 | 2929 | 1 | 14~22 | MMS-63S 14~22 600Y | MMS-63S 14...22 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS736 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 18~26 |  | 600Y | 3 | 10 | 22 | 20 | 2929 | 1 | 18~26 | MMS-63S 18~26 600Y | MMS-63S 18...26 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS737 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 22~32 |  | 600Y | 3 | 10 | 32 | 30 | 2929 | 1 | 22~32 | MMS-63S 22~32 600Y | MMS-63S 22...32 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS738 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 28~40 |  | 600Y | 3 | 10 | 32 | 30 | 2929 | 1 | 28~40 | MMS-63S 28~40 600Y | MMS-63S 28...40 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS739 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 34~50 |  | 600Y | 3 | 10 | 41 | 40 | 2929 | 1 | 34~50 | MMS-63S 34~50 600Y | MMS-63S 34...50 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS740 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 45~63 |  | 600Y | 3 | 10 | 62 | 60 | 2929 | 1 | 45~63 | MMS-63S 45~63 600Y | MMS-63S 45...63 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS741 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 47~65 |  | 600Y | 3 | 10 | 62 | 60 | 2929 | 1 | 47~65 | MMS-63S 47~65 600Y | MMS-63S 47...65 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS742 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 600Y | 3 | 25 | 6~10 |  | 600Y | 3 | 25 | 9 | 7.5 | 2929 | 1 | 6~10 | MMS-63H 6~10 600Y | MMS-63H 6...10 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS743 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 600Y | 3 | 25 | 9~13 |  | 600Y | 3 | 25 | 11 | 10 | 2929 | 1 | 9~13 | MMS-63H 9~13 600Y | MMS-63H 9...13 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS744 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 11~17 |  | 600Y | 3 | 10 | 17 | 15 | 2929 | 1 | 11~17 | MMS-63H 11~17 600Y | MMS-63H 11...17 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS745 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 14~22 |  | 600Y | 3 | 10 | 22 | 20 | 2929 | 1 | 14~22 | MMS-63H 14~22 600Y | MMS-63H 14...22 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS746 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 18~26 |  | 600Y | 3 | 10 | 22 | 20 | 2929 | 1 | 18~26 | MMS-63H 18~26 600Y | MMS-63H 18...26 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS747 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 22~32 |  | 600Y | 3 | 10 | 32 | 30 | 2929 | 1 | 22~32 | MMS-63H 22~32 600Y | MMS-63H 22...32 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS748 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 28~40 |  | 600Y | 3 | 10 | 32 | 30 | 2929 | 1 | 28~40 | MMS-63H 28~40 600Y | MMS-63H 28...40 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS749 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 34~50 |  | 600Y | 3 | 10 | 41 | 40 | 2929 | 1 | 34~50 | MMS-63H 34~50 600Y | MMS-63H 34...50 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS750 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 45~63 |  | 600Y | 3 | 10 | 62 | 60 | 2929 | 1 | 45~63 | MMS-63H 45~63 600Y | MMS-63H 45...63 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS751 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 47~65 |  | 600Y | 3 | 10 | 62 | 60 | 2929 | 1 | 47~65 | MMS-63H 47~65 600Y | MMS-63H 47...65 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS752 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 11~17 |  | 600Y | 3 | 10 | 17 | 15 | 2929 | 1 | 11~17 | MMS-100S 11~17 600Y | MMS-100S 11...17 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS753 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 14~22 |  | 600Y | 3 | 10 | 22 | 20 | 2929 | 1 | 14~22 | MMS-100S 14~22 600Y | MMS-100S 14...22 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS754 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 18~26 |  | 600Y | 3 | 10 | 22 | 20 | 2929 | 1 | 18~26 | MMS-100S 18~26 600Y | MMS-100S 18...26 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS755 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 22~32 |  | 600Y | 3 | 10 | 32 | 30 | 2929 | 1 | 22~32 | MMS-100S 22~32 600Y | MMS-100S 22...32 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS756 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 28~40 |  | 600Y | 3 | 10 | 32 | 30 | 2929 | 1 | 28~40 | MMS-100S 28~40 600Y | MMS-100S 28...40 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS757 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 34~50 |  | 600Y | 3 | 10 | 41 | 40 | 2929 | 1 | 34~50 | MMS-100S 34~50 600Y | MMS-100S 34...50 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS758 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 45~63 |  | 600Y | 3 | 10 | 62 | 60 | 2929 | 1 | 45~63 | MMS-100S 45~63 600Y | MMS-100S 45...63 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS759 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 55~75 |  | 600Y | 3 | 10 | 62 | 60 | 2929 | 1 | 55~75 | MMS-100S 55~75 600Y | MMS-100S 55...75 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS760 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 70~90 |  | 600Y | 3 | 10 | 77 | 75 | 2929 | 1 | 70~90 | MMS-100S 70~90 600Y | MMS-100S 70...90 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS761 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 80~100 |  | 600Y | 3 | 10 | 99 | 100 | 2929 | 1 | 80~100 | MMS-100S 80~100 600Y | MMS-100S 80...100 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS762 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 600Y | 3 | 25 | 11~17 |  | 600Y | 3 | 25 | 17 | 15 | 2929 | 1 | 11~17 | MMS-100H 11~17 600Y | MMS-100H 11...17 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS763 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 600Y | 3 | 20 | 14~22 |  | 600Y | 3 | 20 | 22 | 20 | 2929 | 1 | 14~22 | MMS-100H 14~22 600Y | MMS-100H 14...22 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS764 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 600Y | 3 | 20 | 18~26 |  | 600Y | 3 | 20 | 22 | 20 | 2929 | 1 | 18~26 | MMS-100H 18~26 600Y | MMS-100H 18...26 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS765 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 600Y | 3 | 20 | 22~32 |  | 600Y | 3 | 20 | 32 | 30 | 2929 | 1 | 22~32 | MMS-100H 22~32 600Y | MMS-100H 22...32 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS766 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 600Y | 3 | 20 | 28~40 |  | 600Y | 3 | 20 | 32 | 30 | 2929 | 1 | 28~40 | MMS-100H 28~40 600Y | MMS-100H 28...40 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS767 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 600Y | 3 | 20 | 34~50 |  | 600Y | 3 | 20 | 41 | 40 | 2929 | 1 | 34~50 | MMS-100H 34~50 600Y | MMS-100H 34...50 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS768 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 600Y | 3 | 10 | 45~63 |  | 600Y | 3 | 10 | 62 | 60 | 2929 | 1 | 45~63 | MMS-100H 45~63 600Y | MMS-100H 45...63 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS769 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 600Y | 3 | 10 | 55~75 |  | 600Y | 3 | 10 | 62 | 60 | 2929 | 1 | 55~75 | MMS-100H 55~75 600Y | MMS-100H 55...75 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS770 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 600Y | 3 | 10 | 70~90 |  | 600Y | 3 | 10 | 77 | 75 | 2929 | 1 | 70~90 | MMS-100H 70~90 600Y | MMS-100H 70...90 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
LSIS771 | E252942 |  | 1.1 | E [ version C4] | MSP | LSIS | MMS-100H | 600Y | 3 | 10 | 80~100 |  | 600Y | 3 | 10 | 99 | 100 | 2929 | 1 | 80~100 | MMS-100H 80~100 600Y | MMS-100H 80...100 600Y
[5 empty] | Short Circuit Alarm | LSIS | LAM |  |  | - | - | [6 empty] | 2929 | 1 | - | LAM - | LAM -
Notes:
[1] Horsepower ratings shown are for reference only, final selection of Combination Motor Controller depends on the actual motor full load current and service factor
[2] Full load current values from NEC Table 430.250 or represent the maximum current rating of the combination motor controller
Conditions of Acceptability:
| 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
| 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
| 3 | Unless otherwise specified, all connections between components are made using insulated wire
having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
| 4 | The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application
(Type E Combination Motor Controllers).

## Type F
Issued: 2017-01-31
Revised: 2022-07-27
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | Conditions of Use
Listing Report Information
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating
LSIS801 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.1 - 0.16 | - | 240 | 3 | 100 | 0.16 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-6a |  |  | 5 | 6 | -
LSIS802 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.1 - 0.16 | - | 240 | 3 | 100 | 0.16 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS803 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.1 - 0.16 | - | 240 | 3 | 100 | 0.16 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS804 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.1 - 0.16 | - | 240 | 3 | 100 | 0.16 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9 |  |  | 5 | 9 | -
LSIS805 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.1 - 0.16 | - | 240 | 3 | 100 | 0.16 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-6M |  |  | 5 | 6 | -
LSIS806 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.1 - 0.16 | - | 240 | 3 | 100 | 0.16 | - | 2929 | 1
|  |  |  | MC | LSIS | GMC-9 |  |  | 5 | 9 | -
LSIS807 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.16 - 0.25 | - | 240 | 3 | 100 | 0.25 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-6a |  |  | 5 | 6 | -
LSIS808 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.16 - 0.25 | - | 240 | 3 | 100 | 0.25 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS809 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.16 - 0.25 | - | 240 | 3 | 100 | 0.25 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS810 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.16 - 0.25 | - | 240 | 3 | 100 | 0.25 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9 |  |  | 5 | 9 | -
LSIS811 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.16 - 0.25 | - | 240 | 3 | 100 | 0.25 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-6M |  |  | 5 | 6 | -
LSIS812 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.16 - 0.25 | - | 240 | 3 | 100 | 0.25 | - | 2929 | 1
|  |  |  | MC | LSIS | GMC-9 |  |  | 5 | 9 | -
LSIS813 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.25 - 0.4 | - | 240 | 3 | 100 | 0.4 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-6a |  |  | 5 | 6 | -
LSIS814 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.25 - 0.4 | - | 240 | 3 | 100 | 0.4 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS815 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.25 - 0.4 | - | 240 | 3 | 100 | 0.4 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS816 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.25 - 0.4 | - | 240 | 3 | 100 | 0.4 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9 |  |  | 5 | 9 | -
LSIS817 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.25 - 0.4 | - | 240 | 3 | 100 | 0.4 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-6M |  |  | 5 | 6 | -
LSIS818 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.25 - 0.4 | - | 240 | 3 | 100 | 0.4 | - | 2929 | 1
|  |  |  | MC | LSIS | GMC-9 |  |  | 5 | 9 | -
LSIS819 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.4 - 0.63 | - | 240 | 3 | 100 | 0.63 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-6a |  |  | 5 | 6 | -
LSIS820 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.4 - 0.63 | - | 240 | 3 | 100 | 0.63 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS821 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.4 - 0.63 | - | 240 | 3 | 100 | 0.63 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS822 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.4 - 0.63 | - | 240 | 3 | 100 | 0.63 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9 |  |  | 5 | 9 | -
LSIS823 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.4 - 0.63 | - | 240 | 3 | 100 | 0.63 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-6M |  |  | 5 | 6 | -
LSIS824 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.4 - 0.63 | - | 240 | 3 | 100 | 0.63 | - | 2929 | 1
|  |  |  | MC | LSIS | GMC-9 |  |  | 5 | 9 | -
LSIS825 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.63 - 1 | - | 240 | 3 | 100 | 1 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-6a |  |  | 5 | 6 | -
LSIS826 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.63 - 1 | - | 240 | 3 | 100 | 1 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS827 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.63 - 1 | - | 240 | 3 | 100 | 1 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS828 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.63 - 1 | - | 240 | 3 | 100 | 1 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9 |  |  | 5 | 9 | -
LSIS829 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.63 - 1 | - | 240 | 3 | 100 | 1 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-6M |  |  | 5 | 6 | -
LSIS830 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 0.63 - 1 | - | 240 | 3 | 100 | 1 | - | 2929 | 1
|  |  |  | MC | LSIS | GMC-9 |  |  | 5 | 9 | -
LSIS831 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 1 - 1.6 | - | 240 | 3 | 100 | 1.6 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
LSIS832 |  |  |  | MC | LSIS | MC-6a |  |  | 5 | 6 | -
| E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 1 - 1.6 | - | 240 | 3 | 100 | 1.6 | - | 2929 | 1
LSIS833 |  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS833 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 1 - 1.6 | - | 240 | 3 | 100 | 1.6 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS834 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 1 - 1.6 | - | 240 | 3 | 100 | 1.6 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9 |  |  | 5 | 9 | -
LSIS835 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 1 - 1.6 | - | 240 | 3 | 100 | 1.6 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-6M |  |  | 5 | 6 | -
LSIS836 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 1 - 1.6 | - | 240 | 3 | 100 | 1.6 | - | 2929 | 1
|  |  |  | MC | LSIS | GMC-9 |  |  | 5 | 9 | -
LSIS837 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 1.6 - 2.5 | - | 240 | 3 | 100 | 2.2 | 0.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-12a |  |  | 5 | 12 | -
LSIS838 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 1.6 - 2.5 | - | 240 | 3 | 100 | 2.2 | 0.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-12b |  |  | 5 | 12 | -
LSIS839 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 1.6 - 2.5 | - | 240 | 3 | 100 | 2.2 | 0.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-12 |  |  | 5 | 12 | -
LSIS840 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 1.6 - 2.5 | - | 240 | 3 | 100 | 2.2 | 0.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-12M |  |  | 5 | 12 | -
LSIS841 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 1.6 - 2.5 | - | 240 | 3 | 100 | 2.2 | 0.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-12 |  |  | 5 | 12 | -
LSIS842 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 2.5 - 4 | - | 240 | 3 | 100 | 3.2 | 0.75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-12a |  |  | 5 | 12 | -
LSIS843 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 2.5 - 4 | - | 240 | 3 | 100 | 3.2 | 0.75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-12b |  |  | 5 | 12 | -
LSIS844 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 2.5 - 4 | - | 240 | 3 | 100 | 3.2 | 0.75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-12 |  |  | 5 | 12 | -
LSIS845 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 2.5 - 4 | - | 240 | 3 | 100 | 3.2 | 0.75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-12M |  |  | 5 | 12 | -
LSIS846 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 2.5 - 4 | - | 240 | 3 | 100 | 3.2 | 0.75 | 2929 | 1
|  |  |  | MC | LSIS | GMC-12 |  |  | 5 | 12 | -
LSIS847 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 4 - 6 | - | 240 | 3 | 100 | 6 | 1.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18a |  |  | 5 | 18 | -
LSIS848 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 4 - 6 | - | 240 | 3 | 100 | 6 | 1.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18b |  |  | 5 | 18 | -
LSIS849 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 4 - 6 | - | 240 | 3 | 100 | 6 | 1.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18 |  |  | 5 | 18 | -
LSIS890 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 4 - 6 | - | 240 | 3 | 100 | 6 | 1.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-18 |  |  | 5 | 18 | -
LSIS891 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 5 - 8 | - | 240 | 3 | 100 | 6.8 | 2 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18a |  |  | 5 | 18 | -
LSIS892 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 5 - 8 | - | 240 | 3 | 100 | 6.8 | 2 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18b |  |  | 5 | 18 | -
LSIS893 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 5 - 8 | - | 240 | 3 | 100 | 6.8 | 2 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18 |  |  | 5 | 18 | -
LSIS894 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 5 - 8 | - | 240 | 3 | 100 | 6.8 | 2 | 2929 | 1
|  |  |  | MC | LSIS | GMC-18 |  |  | 5 | 18 | -
LSIS895 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 6 - 10 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18a |  |  | 5 | 18 | -
LSIS896 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 6 - 10 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18b |  |  | 5 | 18 | -
LSIS897 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 6 - 10 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18 |  |  | 5 | 18 | -
LSIS898 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 6 - 10 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | MC | LSIS | GMC-18 |  |  | 5 | 18 | -
LSIS899 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 9 - 13 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-25a |  |  | 5 | 25 | -
LSIS890 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 9 - 13 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-22b |  |  | 5 | 22 | -
LSIS891 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 9 - 13 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-25 |  |  | 5 | 25 | -
LSIS892 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 9 - 13 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | MC | LSIS | GMC-22 |  |  | 5 | 22 | -
LSIS893 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 11 - 17 | - | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-25a |  |  | 5 | 25 | -
LSIS894 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 11 - 17 | - | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-22b |  |  | 5 | 22 | -
LSIS895 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 11 - 17 | - | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-25 |  |  | 5 | 25 | -
LSIS896 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 11 - 17 | - | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-22 |  |  | 5 | 22 | -
LSIS897 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 14 - 22 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-25a |  |  | 5 | 25 | -
LSIS898 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 14 - 22 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-22b |  |  | 5 | 22 | -
LSIS899 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 14 - 22 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-25 |  |  | 5 | 25 | -
LSIS900 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 14 - 22 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS901 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 18 - 26 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-32a |  |  | 5 | 32 | -
LSIS902 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 18 - 26 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-32 |  |  | 5 | 32 | -
LSIS903 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 18 - 26 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS904 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 22 - 32 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-32a |  |  | 5 | 32 | -
LSIS905 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 22 - 32 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-32 |  |  | 5 | 32 | -
LSIS906 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 22 - 32 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS907 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 28 - 40 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35a |  |  | 5 | 35 | -
LSIS908 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 240 | 3 | 100 | 28 - 40 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-40a |  |  | 5 | 40 | -
LSIS909 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 6 - 10 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS910 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 6 - 10 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS911 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 6 - 10 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS912 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 9 - 13 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS913 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 9 - 13 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS914 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 9 - 13 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS915 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 11 - 17 | - | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS916 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 11 - 17 | - | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS917 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 11 - 17 | - | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS918 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 14 - 22 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS919 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 14 - 22 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS920 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 14 - 22 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS921 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 18 - 26 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS922 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 18 - 26 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS923 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 18 - 26 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS924 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 22 - 32 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS925 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 22 - 32 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS926 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 22 - 32 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS927 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 28 - 40 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS928 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 28 - 40 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-40 |  |  | 5 | 40 | -
LSIS929 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 28 - 40 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | MC | LSIS | GMC-40 |  |  | 5 | 40 | -
LSIS930 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 34 - 50 | - | 240 | 3 | 100 | 42 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS931 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 34 - 50 | - | 240 | 3 | 100 | 42 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50 |  |  | 5 | 50 | -
LSIS932 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 34 - 50 | - | 240 | 3 | 100 | 42 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS933 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 45 - 63 | - | 240 | 3 | 100 | 54 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS934 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 45 - 63 | - | 240 | 3 | 100 | 54 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-63 |  |  | 5 | 63 | -
LSIS935 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 45 - 63 | - | 240 | 3 | 100 | 54 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-65 |  |  | 5 | 65 | -
LSIS936 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 240 | 3 | 100 | 47 - 65 | - | 240 | 3 | 100 | 54 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS937 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 6 - 10 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS938 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 6 - 10 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS939 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 6 - 10 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS940 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 9 - 13 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS941 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 9 - 13 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS942 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 9 - 13 | - | 240 | 3 | 100 | 9.6 | 3 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS943 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 11 - 17 | - | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS944 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 11 - 17 | - | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS945 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 11 - 17 | - | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS946 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 14 - 22 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS947 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 14 - 22 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS948 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 14 - 22 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS949 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 18 - 26 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS950 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 18 - 26 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS951 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 18 - 26 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS952 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 22 - 32 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS953 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 22 - 32 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS954 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 22 - 32 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS955 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 28 - 40 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS956 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 28 - 40 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-40 |  |  | 5 | 40 | -
LSIS957 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 28 - 40 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | MC | LSIS | GMC-40 |  |  | 5 | 40 | -
LSIS958 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 34 - 50 | - | 240 | 3 | 100 | 42 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS959 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 34 - 50 | - | 240 | 3 | 100 | 42 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50 |  |  | 5 | 50 | -
LSIS960 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 34 - 50 | - | 240 | 3 | 100 | 42 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS961 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 45 - 63 | - | 240 | 3 | 100 | 54 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS962 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 45 - 63 | - | 240 | 3 | 100 | 54 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-63 |  |  | 5 | 63 | -
LSIS963 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 45 - 63 | - | 240 | 3 | 100 | 54 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-65 |  |  | 5 | 65 | -
LSIS964 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 240 | 3 | 100 | 47 - 65 | - | 240 | 3 | 100 | 54 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS965 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 11 - 17 | - | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS966 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 11 - 17 | - | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS967 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 11 - 17 | - | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS968 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 14 - 22 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS969 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 14 - 22 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS970 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 14 - 22 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS971 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 18 - 26 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS972 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 18 - 26 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS973 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 18 - 26 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS974 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 22 - 32 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS975 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 22 - 32 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS976 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 22 - 32 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS977 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 28 - 40 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS978 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 28 - 40 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS980 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 28 - 40 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS980 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 34 - 50 | - | 240 | 3 | 100 | 42 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS981 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 34 - 50 | - | 240 | 3 | 100 | 42 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS982 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 34 - 50 | - | 240 | 3 | 100 | 42 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS983 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 45 - 63 | - | 240 | 3 | 100 | 54 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS984 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 45 - 63 | - | 240 | 3 | 100 | 54 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS985 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 45 - 63 | - | 240 | 3 | 100 | 54 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-65 |  |  | 5 | 65 | -
LSIS986 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 55 - 75 | - | 240 | 3 | 100 | 68 | 25 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS987 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 55 - 75 | - | 240 | 3 | 100 | 68 | 25 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75 |  |  | 5 | 75 | -
LSIS989 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 55 - 75 | - | 240 | 3 | 100 | 68 | 25 | 2929 | 1
|  |  |  | MC | LSIS | GMC-75 |  |  | 5 | 75 | -
LSIS989 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 70 - 90 | - | 240 | 3 | 100 | 80 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-85a |  |  | 5 | 85 | -
LSIS990 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 70 - 90 | - | 240 | 3 | 100 | 80 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-85 |  |  | 5 | 85 | -
LSIS992 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 70 - 90 | - | 240 | 3 | 100 | 80 | 30 | 2929 | 1
|  |  |  | MC | LSIS | GMC-85 |  |  | 5 | 85 | -
LSIS992 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 80 - 100 | - | 240 | 3 | 100 | 80 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-100a |  |  | 5 | 100 | -
LSIS993 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 80 - 100 | - | 240 | 3 | 100 | 80 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-95 |  |  | 5 | 95 | -
LSIS994 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 240 | 3 | 100 | 80 - 100 | - | 240 | 3 | 100 | 80 | 30 | 2929 | 1
|  |  |  | MC | LSIS | GMC-85 |  |  | 5 | 85 | -
LSIS995 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 11 - 17 | - | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS996 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 11 - 17 | - | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS997 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 11 - 17 | - | 240 | 3 | 100 | 15.2 | 5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS998 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 14 - 22 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS999 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 14 - 22 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1000 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 14 - 22 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1001 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 18 - 26 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1002 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 18 - 26 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1003 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 18 - 26 | - | 240 | 3 | 100 | 22 | 7.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1004 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 22 - 32 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1005 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 22 - 32 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1006 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 22 - 32 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1007 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 28 - 40 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1008 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 28 - 40 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1009 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 28 - 40 | - | 240 | 3 | 100 | 28 | 10 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1010 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 34 - 50 | - | 240 | 3 | 100 | 42 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1011 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 34 - 50 | - | 240 | 3 | 100 | 42 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1012 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 34 - 50 | - | 240 | 3 | 100 | 42 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1013 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 45 - 63 | - | 240 | 3 | 100 | 54 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1014 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 45 - 63 | - | 240 | 3 | 100 | 54 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1015 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 45 - 63 | - | 240 | 3 | 100 | 54 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-65 |  |  | 5 | 65 | -
LSIS1016 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 55 - 75 | - | 240 | 3 | 100 | 68 | 25 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1017 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 55 - 75 | - | 240 | 3 | 100 | 68 | 25 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75 |  |  | 5 | 75 | -
LSIS1018 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 55 - 75 | - | 240 | 3 | 100 | 68 | 25 | 2929 | 1
|  |  |  | MC | LSIS | GMC-75 |  |  | 5 | 75 | -
LSIS1019 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 70 - 90 | - | 240 | 3 | 100 | 80 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-85a |  |  | 5 | 85 | -
LSIS1020 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 70 - 90 | - | 240 | 3 | 100 | 80 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-85 |  |  | 5 | 85 | -
LSIS1022 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 70 - 90 | - | 240 | 3 | 100 | 80 | 30 | 2929 | 1
|  |  |  | MC | LSIS | GMC-85 |  |  | 5 | 85 | -
LSIS1022 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 80 - 100 | - | 240 | 3 | 100 | 80 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-100a |  |  | 5 | 100 | -
LSIS1023 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 80 - 100 | - | 240 | 3 | 100 | 80 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-95 |  |  | 5 | 95 | -
LSIS1024 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 240 | 3 | 100 | 80 - 100 | - | 240 | 3 | 100 | 80 | 30 | 2929 | 1
|  |  |  | MC | LSIS | GMC-85 |  |  | 5 | 85 | -
LSIS1025 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.1 - 0.16 | - | 480Y | 3 | 65 | 0.16 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-6a |  |  | 5 | 6 | -
LSIS1026 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.1 - 0.16 | - | 480Y | 3 | 65 | 0.16 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS1027 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.1 - 0.16 | - | 480Y | 3 | 65 | 0.16 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS1028 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.1 - 0.16 | - | 480Y | 3 | 65 | 0.16 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9 |  |  | 5 | 9 | -
LSIS1029 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.1 - 0.16 | - | 480Y | 3 | 65 | 0.16 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-6M |  |  | 5 | 6 | -
LSIS1031 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.1 - 0.16 | - | 480Y | 3 | 65 | 0.16 | - | 2929 | 1
|  |  |  | MC | LSIS | GMC-9 |  |  | 5 | 9 | -
LSIS1031 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.16 - 0.25 | - | 480Y | 3 | 65 | 0.25 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-6a |  |  | 5 | 6 | -
LSIS1032 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.16 - 0.25 | - | 480Y | 3 | 65 | 0.25 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS1033 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.16 - 0.25 | - | 480Y | 3 | 65 | 0.25 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS1034 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.16 - 0.25 | - | 480Y | 3 | 65 | 0.25 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9 |  |  | 5 | 9 | -
LSIS1035 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.16 - 0.25 | - | 480Y | 3 | 65 | 0.25 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-6M |  |  | 5 | 6 | -
LSIS1036 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.16 - 0.25 | - | 480Y | 3 | 65 | 0.25 | - | 2929 | 1
|  |  |  | MC | LSIS | GMC-9 |  |  | 5 | 9 | -
LSIS1037 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.25 - 0.4 | - | 480Y | 3 | 65 | 0.4 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-6a |  |  | 5 | 6 | -
LSIS1038 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.25 - 0.4 | - | 480Y | 3 | 65 | 0.4 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS1039 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.25 - 0.4 | - | 480Y | 3 | 65 | 0.4 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS1040 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.25 - 0.4 | - | 480Y | 3 | 65 | 0.4 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9 |  |  | 5 | 9 | -
LSIS1041 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.25 - 0.4 | - | 480Y | 3 | 65 | 0.4 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-6M |  |  | 5 | 6 | -
LSIS1043 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.25 - 0.4 | - | 480Y | 3 | 65 | 0.4 | - | 2929 | 1
|  |  |  | MC | LSIS | GMC-9 |  |  | 5 | 9 | -
LSIS1043 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.4 - 0.63 | - | 480Y | 3 | 65 | 0.63 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-6a |  |  | 5 | 6 | -
LSIS1044 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.4 - 0.63 | - | 480Y | 3 | 65 | 0.63 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS1045 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.4 - 0.63 | - | 480Y | 3 | 65 | 0.63 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS1046 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.4 - 0.63 | - | 480Y | 3 | 65 | 0.63 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9 |  |  | 5 | 9 | -
LSIS1047 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.4 - 0.63 | - | 480Y | 3 | 65 | 0.63 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-6M |  |  | 5 | 6 | -
LSIS1049 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.4 - 0.63 | - | 480Y | 3 | 65 | 0.63 | - | 2929 | 1
|  |  |  | MC | LSIS | GMC-9 |  |  | 5 | 9 | -
LSIS1049 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.63 - 1 | - | 480Y | 3 | 65 | 1 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-6a |  |  | 5 | 6 | -
LSIS1050 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.63 - 1 | - | 480Y | 3 | 65 | 1 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS1051 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.63 - 1 | - | 480Y | 3 | 65 | 1 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS1052 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.63 - 1 | - | 480Y | 3 | 65 | 1 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9 |  |  | 5 | 9 | -
LSIS1053 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.63 - 1 | - | 480Y | 3 | 65 | 1 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-6M |  |  | 5 | 6 | -
LSIS1055 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 0.63 - 1 | - | 480Y | 3 | 65 | 1 | - | 2929 | 1
|  |  |  | MC | LSIS | GMC-9 |  |  | 5 | 9 | -
LSIS1055 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 1 - 1.6 | - | 480Y | 3 | 65 | 1.6 | 0.75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-6a |  |  | 5 | 6 | -
LSIS1056 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 1 - 1.6 | - | 480Y | 3 | 65 | 1.6 | 0.75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS1057 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 1 - 1.6 | - | 480Y | 3 | 65 | 1.6 | 0.75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS1058 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 1 - 1.6 | - | 480Y | 3 | 65 | 1.6 | 0.75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9 |  |  | 5 | 9 | -
LSIS1059 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 1 - 1.6 | - | 480Y | 3 | 65 | 1.6 | 0.75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-6M |  |  | 5 | 6 | -
LSIS1061 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 1 - 1.6 | - | 480Y | 3 | 65 | 1.6 | 0.75 | 2929 | 1
|  |  |  | MC | LSIS | GMC-9 |  |  | 5 | 9 | -
LSIS1061 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 1.6 - 2.5 | - | 480Y | 3 | 65 | 2.1 | 1 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-12a |  |  | 5 | 12 | -
LSIS1062 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 1.6 - 2.5 | - | 480Y | 3 | 65 | 2.1 | 1 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-12b |  |  | 5 | 12 | -
LSIS1063 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 1.6 - 2.5 | - | 480Y | 3 | 65 | 2.1 | 1 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-12 |  |  | 5 | 12 | -
LSIS1064 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 1.6 - 2.5 | - | 480Y | 3 | 65 | 2.1 | 1 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-12M |  |  | 5 | 12 | -
LSIS1066 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 1.6 - 2.5 | - | 480Y | 3 | 65 | 2.1 | 1 | 2929 | 1
|  |  |  | MC | LSIS | GMC-12 |  |  | 5 | 12 | -
LSIS1066 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 2.5 - 4 | - | 480Y | 3 | 65 | 3.4 | 2 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-12a |  |  | 5 | 12 | -
LSIS1067 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 2.5 - 4 | - | 480Y | 3 | 65 | 3.4 | 2 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-12b |  |  | 5 | 12 | -
LSIS1068 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 2.5 - 4 | - | 480Y | 3 | 65 | 3.4 | 2 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-12 |  |  | 5 | 12 | -
LSIS1069 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 2.5 - 4 | - | 480Y | 3 | 65 | 3.4 | 2 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-12M |  |  | 5 | 12 | -
LSIS1071 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 2.5 - 4 | - | 480Y | 3 | 65 | 3.4 | 2 | 2929 | 1
|  |  |  | MC | LSIS | GMC-12 |  |  | 5 | 12 | -
LSIS1071 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 4 - 6 | - | 480Y | 3 | 65 | 4.8 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18a |  |  | 5 | 18 | -
LSIS1072 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 4 - 6 | - | 480Y | 3 | 65 | 4.8 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18b |  |  | 5 | 18 | -
LSIS1073 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 4 - 6 | - | 480Y | 3 | 65 | 4.8 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18 |  |  | 5 | 18 | -
LSIS1075 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 4 - 6 | - | 480Y | 3 | 65 | 4.8 | 3 | 2929 | 1
|  |  |  | MC | LSIS | GMC-18 |  |  | 5 | 18 | -
LSIS1075 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 5 - 8 | - | 480Y | 3 | 65 | 7.6 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18a |  |  | 5 | 18 | -
LSIS1076 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 5 - 8 | - | 480Y | 3 | 65 | 7.6 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18b |  |  | 5 | 18 | -
LSIS1077 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 5 - 8 | - | 480Y | 3 | 65 | 7.6 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18 |  |  | 5 | 18 | -
LSIS1079 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 5 - 8 | - | 480Y | 3 | 65 | 7.6 | 5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-18 |  |  | 5 | 18 | -
LSIS1079 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 6 - 10 | - | 480Y | 3 | 65 | 7.6 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18a |  |  | 5 | 18 | -
LSIS1080 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 6 - 10 | - | 480Y | 3 | 65 | 7.6 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18b |  |  | 5 | 18 | -
LSIS1081 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 6 - 10 | - | 480Y | 3 | 65 | 7.6 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18 |  |  | 5 | 18 | -
LSIS1083 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 6 - 10 | - | 480Y | 3 | 65 | 7.6 | 5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-18 |  |  | 5 | 18 | -
LSIS1083 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 9 - 13 | - | 480Y | 3 | 65 | 11 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-25a |  |  | 5 | 25 | -
LSIS1084 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 9 - 13 | - | 480Y | 3 | 65 | 11 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-22b |  |  | 5 | 22 | -
LSIS1085 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 9 - 13 | - | 480Y | 3 | 65 | 11 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-25 |  |  | 5 | 25 | -
LSIS1087 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 65 | 9 - 13 | - | 480Y | 3 | 65 | 11 | 7.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-22 |  |  | 5 | 22 | -
LSIS1087 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 11 - 17 | - | 480Y | 3 | 30 | 14 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-25a |  |  | 5 | 25 | -
LSIS1088 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 11 - 17 | - | 480Y | 3 | 30 | 14 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-22b |  |  | 5 | 22 | -
LSIS1089 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 11 - 17 | - | 480Y | 3 | 30 | 14 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-25 |  |  | 5 | 25 | -
LSIS1091 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 11 - 17 | - | 480Y | 3 | 30 | 14 | 10 | 2929 | 1
|  |  |  | MC | LSIS | GMC-22 |  |  | 5 | 22 | -
LSIS1091 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 14 - 22 | - | 480Y | 3 | 30 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-25a |  |  | 5 | 25 | -
LSIS1092 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 14 - 22 | - | 480Y | 3 | 30 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-22b |  |  | 5 | 22 | -
LSIS1093 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 14 - 22 | - | 480Y | 3 | 30 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-25 |  |  | 5 | 25 | -
LSIS1095 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 14 - 22 | - | 480Y | 3 | 30 | 21 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1095 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 18 - 26 | - | 480Y | 3 | 30 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-32a |  |  | 5 | 32 | -
LSIS1096 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 18 - 26 | - | 480Y | 3 | 30 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-32 |  |  | 5 | 32 | -
LSIS1098 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 18 - 26 | - | 480Y | 3 | 30 | 21 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1098 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 22 - 32 | - | 480Y | 3 | 30 | 27 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-32a |  |  | 5 | 32 | -
LSIS1099 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 22 - 32 | - | 480Y | 3 | 30 | 27 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-32 |  |  | 5 | 32 | -
LSIS1101 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 22 - 32 | - | 480Y | 3 | 30 | 27 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1101 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 28 - 40 | - | 480Y | 3 | 30 | 34 | 25 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35a |  |  | 5 | 35 | -
LSIS1102 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 480Y | 3 | 30 | 28 - 40 | - | 480Y | 3 | 30 | 40 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-40a |  |  | 5 | 40 | -
LSIS1103 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 50 | 6 - 10 | - | 480Y | 3 | 50 | 7.6 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1104 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 50 | 6 - 10 | - | 480Y | 3 | 50 | 7.6 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1106 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 50 | 6 - 10 | - | 480Y | 3 | 50 | 7.6 | 5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1106 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 50 | 9 - 13 | - | 480Y | 3 | 50 | 11 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1107 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 50 | 9 - 13 | - | 480Y | 3 | 50 | 11 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1109 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 50 | 9 - 13 | - | 480Y | 3 | 50 | 11 | 7.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1109 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 11 - 17 | - | 480Y | 3 | 40 | 14 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1110 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 11 - 17 | - | 480Y | 3 | 40 | 14 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1112 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 11 - 17 | - | 480Y | 3 | 40 | 14 | 10 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1112 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 14 - 22 | - | 480Y | 3 | 40 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1113 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 14 - 22 | - | 480Y | 3 | 40 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1115 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 14 - 22 | - | 480Y | 3 | 40 | 21 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1115 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 18 - 26 | - | 480Y | 3 | 40 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1116 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 18 - 26 | - | 480Y | 3 | 40 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1118 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 18 - 26 | - | 480Y | 3 | 40 | 21 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1118 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 22 - 32 | - | 480Y | 3 | 40 | 27 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1119 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 22 - 32 | - | 480Y | 3 | 40 | 27 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1121 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 22 - 32 | - | 480Y | 3 | 40 | 27 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1121 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 28 - 40 | - | 480Y | 3 | 40 | 40 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1122 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 28 - 40 | - | 480Y | 3 | 40 | 40 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-40 |  |  | 5 | 40 | -
LSIS1124 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 28 - 40 | - | 480Y | 3 | 40 | 34 | 25 | 2929 | 1
|  |  |  | MC | LSIS | GMC-40 |  |  | 5 | 40 | -
LSIS1124 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 34 - 50 | - | 480Y | 3 | 40 | 40 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1125 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 34 - 50 | - | 480Y | 3 | 40 | 40 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50 |  |  | 5 | 50 | -
LSIS1127 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 34 - 50 | - | 480Y | 3 | 40 | 40 | 30 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1127 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 45 - 63 | - | 480Y | 3 | 40 | 52 | 40 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS1128 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 45 - 63 | - | 480Y | 3 | 40 | 52 | 40 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-63 |  |  | 5 | 63 | -
LSIS1130 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 45 - 63 | - | 480Y | 3 | 40 | 52 | 40 | 2929 | 1
|  |  |  | MC | LSIS | GMC-65 |  |  | 5 | 65 | -
LSIS1130 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 480Y | 3 | 40 | 47 - 65 | - | 480Y | 3 | 40 | 52 | 40 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS1131 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 65 | 6 - 10 | - | 480Y | 3 | 65 | 7.6 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1132 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 65 | 6 - 10 | - | 480Y | 3 | 65 | 7.6 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1134 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 65 | 6 - 10 | - | 480Y | 3 | 65 | 7.6 | 5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1134 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 65 | 9 - 13 | - | 480Y | 3 | 65 | 11 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1135 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 65 | 9 - 13 | - | 480Y | 3 | 65 | 11 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1137 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 65 | 9 - 13 | - | 480Y | 3 | 65 | 11 | 7.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1137 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 11 - 17 | - | 480Y | 3 | 50 | 14 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1138 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 11 - 17 | - | 480Y | 3 | 50 | 14 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1140 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 11 - 17 | - | 480Y | 3 | 50 | 14 | 10 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1140 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 14 - 22 | - | 480Y | 3 | 50 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1141 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 14 - 22 | - | 480Y | 3 | 50 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1143 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 14 - 22 | - | 480Y | 3 | 50 | 21 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1143 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 18 - 26 | - | 480Y | 3 | 50 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1144 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 18 - 26 | - | 480Y | 3 | 50 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1146 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 18 - 26 | - | 480Y | 3 | 50 | 21 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1146 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 22 - 32 | - | 480Y | 3 | 50 | 27 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1147 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 22 - 32 | - | 480Y | 3 | 50 | 27 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1149 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 22 - 32 | - | 480Y | 3 | 50 | 27 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1149 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 28 - 40 | - | 480Y | 3 | 50 | 40 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1150 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 28 - 40 | - | 480Y | 3 | 50 | 40 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-40 |  |  | 5 | 40 | -
LSIS1152 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 28 - 40 | - | 480Y | 3 | 50 | 34 | 25 | 2929 | 1
|  |  |  | MC | LSIS | GMC-40 |  |  | 5 | 40 | -
LSIS1152 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 34 - 50 | - | 480Y | 3 | 50 | 40 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1153 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 34 - 50 | - | 480Y | 3 | 50 | 40 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50 |  |  | 5 | 50 | -
LSIS1155 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 34 - 50 | - | 480Y | 3 | 50 | 40 | 30 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1155 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 45 - 63 | - | 480Y | 3 | 50 | 52 | 40 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS1156 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 45 - 63 | - | 480Y | 3 | 50 | 52 | 40 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-63 |  |  | 5 | 63 | -
LSIS1158 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 45 - 63 | - | 480Y | 3 | 50 | 52 | 40 | 2929 | 1
|  |  |  | MC | LSIS | GMC-65 |  |  | 5 | 65 | -
LSIS1158 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 480Y | 3 | 50 | 47 - 65 | - | 480Y | 3 | 50 | 52 | 40 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS1159 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 11 - 17 | - | 480Y | 3 | 50 | 14 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1160 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 11 - 17 | - | 480Y | 3 | 50 | 14 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1162 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 11 - 17 | - | 480Y | 3 | 50 | 14 | 10 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1162 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 14 - 22 | - | 480Y | 3 | 50 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1163 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 14 - 22 | - | 480Y | 3 | 50 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1165 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 14 - 22 | - | 480Y | 3 | 50 | 21 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1165 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 18 - 26 | - | 480Y | 3 | 50 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1166 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 18 - 26 | - | 480Y | 3 | 50 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1168 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 18 - 26 | - | 480Y | 3 | 50 | 21 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1168 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 22 - 32 | - | 480Y | 3 | 50 | 27 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1169 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 22 - 32 | - | 480Y | 3 | 50 | 27 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1171 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 22 - 32 | - | 480Y | 3 | 50 | 27 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1171 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 28 - 40 | - | 480Y | 3 | 50 | 40 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1172 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 28 - 40 | - | 480Y | 3 | 50 | 40 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1174 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 28 - 40 | - | 480Y | 3 | 50 | 40 | 30 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1174 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 34 - 50 | - | 480Y | 3 | 50 | 40 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1175 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 34 - 50 | - | 480Y | 3 | 50 | 40 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1177 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 50 | 34 - 50 | - | 480Y | 3 | 50 | 40 | 30 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1177 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 40 | 45 - 63 | - | 480Y | 3 | 40 | 52 | 40 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1178 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 40 | 45 - 63 | - | 480Y | 3 | 40 | 52 | 40 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1180 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 40 | 45 - 63 | - | 480Y | 3 | 40 | 52 | 40 | 2929 | 1
|  |  |  | MC | LSIS | GMC-65 |  |  | 5 | 65 | -
LSIS1180 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 40 | 55 - 75 | - | 480Y | 3 | 40 | 65 | 50 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1181 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 40 | 55 - 75 | - | 480Y | 3 | 40 | 65 | 50 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75 |  |  | 5 | 75 | -
LSIS1183 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 40 | 55 - 75 | - | 480Y | 3 | 40 | 65 | 50 | 2929 | 1
|  |  |  | MC | LSIS | GMC-75 |  |  | 5 | 75 | -
LSIS1183 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 40 | 70 - 90 | - | 480Y | 3 | 40 | 77 | 60 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-85a |  |  | 5 | 85 | -
LSIS1184 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 40 | 70 - 90 | - | 480Y | 3 | 40 | 77 | 60 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-85 |  |  | 5 | 85 | -
LSIS1186 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 40 | 70 - 90 | - | 480Y | 3 | 40 | 65 | 50 | 2929 | 1
|  |  |  | MC | LSIS | GMC-85 |  |  | 5 | 85 | -
LSIS1186 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 40 | 80 - 100 | - | 480Y | 3 | 40 | 96 | 75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-100a |  |  | 5 | 100 | -
LSIS1187 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 40 | 80 - 100 | - | 480Y | 3 | 40 | 96 | 75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-95 |  |  | 5 | 95 | -
LSIS1189 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 480Y | 3 | 40 | 80 - 100 | - | 480Y | 3 | 40 | 65 | 50 | 2929 | 1
|  |  |  | MC | LSIS | GMC-85 |  |  | 5 | 85 | -
LSIS1189 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 11 - 17 | - | 480Y | 3 | 65 | 14 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1190 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 11 - 17 | - | 480Y | 3 | 65 | 14 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1192 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 11 - 17 | - | 480Y | 3 | 65 | 14 | 10 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1192 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 14 - 22 | - | 480Y | 3 | 65 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1193 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 14 - 22 | - | 480Y | 3 | 65 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1195 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 14 - 22 | - | 480Y | 3 | 65 | 21 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1195 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 18 - 26 | - | 480Y | 3 | 65 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1196 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 18 - 26 | - | 480Y | 3 | 65 | 21 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1198 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 18 - 26 | - | 480Y | 3 | 65 | 21 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1198 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 22 - 32 | - | 480Y | 3 | 65 | 27 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1199 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 22 - 32 | - | 480Y | 3 | 65 | 27 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1201 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 22 - 32 | - | 480Y | 3 | 65 | 27 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1201 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 28 - 40 | - | 480Y | 3 | 65 | 40 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1202 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 28 - 40 | - | 480Y | 3 | 65 | 40 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1204 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 28 - 40 | - | 480Y | 3 | 65 | 40 | 30 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1204 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 34 - 50 | - | 480Y | 3 | 65 | 40 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1205 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 34 - 50 | - | 480Y | 3 | 65 | 40 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1207 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 65 | 34 - 50 | - | 480Y | 3 | 65 | 40 | 30 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1207 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 50 | 45 - 63 | - | 480Y | 3 | 50 | 52 | 40 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1208 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 50 | 45 - 63 | - | 480Y | 3 | 50 | 52 | 40 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1210 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 50 | 45 - 63 | - | 480Y | 3 | 50 | 52 | 40 | 2929 | 1
|  |  |  | MC | LSIS | GMC-65 |  |  | 5 | 65 | -
LSIS1210 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 50 | 55 - 75 | - | 480Y | 3 | 50 | 65 | 50 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1211 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 50 | 55 - 75 | - | 480Y | 3 | 50 | 65 | 50 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75 |  |  | 5 | 75 | -
LSIS1213 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 50 | 55 - 75 | - | 480Y | 3 | 50 | 65 | 50 | 2929 | 1
|  |  |  | MC | LSIS | GMC-75 |  |  | 5 | 75 | -
LSIS1213 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 50 | 70 - 90 | - | 480Y | 3 | 50 | 77 | 60 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-85a |  |  | 5 | 85 | -
LSIS1214 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 50 | 70 - 90 | - | 480Y | 3 | 50 | 77 | 60 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-85 |  |  | 5 | 85 | -
LSIS1216 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 50 | 70 - 90 | - | 480Y | 3 | 50 | 65 | 50 | 2929 | 1
|  |  |  | MC | LSIS | GMC-85 |  |  | 5 | 85 | -
LSIS1216 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 50 | 80 - 100 | - | 480Y | 3 | 50 | 96 | 75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-100a |  |  | 5 | 100 | -
LSIS1217 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 50 | 80 - 100 | - | 480Y | 3 | 50 | 96 | 75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-95 |  |  | 5 | 95 | -
LSIS1219 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 480Y | 3 | 50 | 80 - 100 | - | 480Y | 3 | 50 | 65 | 50 | 2929 | 1
|  |  |  | MC | LSIS | GMC-85 |  |  | 5 | 85 | -
LSIS1219 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.1 - 0.16 | - | 600Y | 3 | 25 | 0.16 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-6a |  |  | 5 | 6 | -
LSIS1220 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.1 - 0.16 | - | 600Y | 3 | 25 | 0.16 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS1221 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.1 - 0.16 | - | 600Y | 3 | 25 | 0.16 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS1222 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.1 - 0.16 | - | 600Y | 3 | 25 | 0.16 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9 |  |  | 5 | 9 | -
LSIS1223 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.1 - 0.16 | - | 600Y | 3 | 25 | 0.16 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-6M |  |  | 5 | 6 | -
LSIS1225 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.1 - 0.16 | - | 600Y | 3 | 25 | 0.16 | - | 2929 | 1
|  |  |  | MC | LSIS | GMC-9 |  |  | 5 | 9 | -
LSIS1225 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.16 - 0.25 | - | 600Y | 3 | 25 | 0.25 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-6a |  |  | 5 | 6 | -
LSIS1226 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.16 - 0.25 | - | 600Y | 3 | 25 | 0.25 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS1227 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.16 - 0.25 | - | 600Y | 3 | 25 | 0.25 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS1228 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.16 - 0.25 | - | 600Y | 3 | 25 | 0.25 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9 |  |  | 5 | 9 | -
LSIS1229 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.16 - 0.25 | - | 600Y | 3 | 25 | 0.25 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-6M |  |  | 5 | 6 | -
LSIS1231 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.16 - 0.25 | - | 600Y | 3 | 25 | 0.25 | - | 2929 | 1
|  |  |  | MC | LSIS | GMC-9 |  |  | 5 | 9 | -
LSIS1231 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.25 - 0.4 | - | 600Y | 3 | 25 | 0.4 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-6a |  |  | 5 | 6 | -
LSIS1232 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.25 - 0.4 | - | 600Y | 3 | 25 | 0.4 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS1233 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.25 - 0.4 | - | 600Y | 3 | 25 | 0.4 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS1234 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.25 - 0.4 | - | 600Y | 3 | 25 | 0.4 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9 |  |  | 5 | 9 | -
LSIS1235 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.25 - 0.4 | - | 600Y | 3 | 25 | 0.4 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-6M |  |  | 5 | 6 | -
LSIS1237 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.25 - 0.4 | - | 600Y | 3 | 25 | 0.4 | - | 2929 | 1
|  |  |  | MC | LSIS | GMC-9 |  |  | 5 | 9 | -
LSIS1237 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.4 - 0.63 | - | 600Y | 3 | 25 | 0.63 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-6a |  |  | 5 | 6 | -
LSIS1238 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.4 - 0.63 | - | 600Y | 3 | 25 | 0.63 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS1239 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.4 - 0.63 | - | 600Y | 3 | 25 | 0.63 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS1240 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.4 - 0.63 | - | 600Y | 3 | 25 | 0.63 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9 |  |  | 5 | 9 | -
LSIS1241 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.4 - 0.63 | - | 600Y | 3 | 25 | 0.63 | - | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-6M |  |  | 5 | 6 | -
LSIS1243 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.4 - 0.63 | - | 600Y | 3 | 25 | 0.63 | - | 2929 | 1
|  |  |  | MC | LSIS | GMC-9 |  |  | 5 | 9 | -
LSIS1243 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.63 - 1 | - | 600Y | 3 | 25 | 0.9 | 0.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-6a |  |  | 5 | 6 | -
LSIS1244 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.63 - 1 | - | 600Y | 3 | 25 | 0.9 | 0.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS1245 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.63 - 1 | - | 600Y | 3 | 25 | 0.9 | 0.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS1246 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.63 - 1 | - | 600Y | 3 | 25 | 0.9 | 0.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9 |  |  | 5 | 9 | -
LSIS1247 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.63 - 1 | - | 600Y | 3 | 25 | 0.9 | 0.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-6M |  |  | 5 | 6 | -
LSIS1249 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 0.63 - 1 | - | 600Y | 3 | 25 | 0.9 | 0.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-9 |  |  | 5 | 9 | -
LSIS1249 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 1 - 1.6 | - | 600Y | 3 | 25 | 1.3 | 0.75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-6a |  |  | 5 | 6 | -
LSIS1250 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 1 - 1.6 | - | 600Y | 3 | 25 | 1.3 | 0.75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9a |  |  | 5 | 9 | -
LSIS1251 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 1 - 1.6 | - | 600Y | 3 | 25 | 1.3 | 0.75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9b |  |  | 5 | 9 | -
LSIS1252 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 1 - 1.6 | - | 600Y | 3 | 25 | 1.3 | 0.75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-9 |  |  | 5 | 9 | -
LSIS1253 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 1 - 1.6 | - | 600Y | 3 | 25 | 1.3 | 0.75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-6M |  |  | 5 | 6 | -
LSIS1255 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 1 - 1.6 | - | 600Y | 3 | 25 | 1.3 | 0.75 | 2929 | 1
|  |  |  | MC | LSIS | GMC-9 |  |  | 5 | 9 | -
LSIS1255 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 1.6 - 2.5 | - | 600Y | 3 | 25 | 2.4 | 1.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-12a |  |  | 5 | 12 | -
LSIS1256 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 1.6 - 2.5 | - | 600Y | 3 | 25 | 2.4 | 1.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-12b |  |  | 5 | 12 | -
LSIS1257 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 1.6 - 2.5 | - | 600Y | 3 | 25 | 2.4 | 1.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-12 |  |  | 5 | 12 | -
LSIS1258 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 1.6 - 2.5 | - | 600Y | 3 | 25 | 2.4 | 1.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-12M |  |  | 5 | 12 | -
LSIS1260 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 1.6 - 2.5 | - | 600Y | 3 | 25 | 2.4 | 1.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-12 |  |  | 5 | 12 | -
LSIS1260 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 2.5 - 4 | - | 600Y | 3 | 25 | 3.9 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-12a |  |  | 5 | 12 | -
LSIS1261 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 2.5 - 4 | - | 600Y | 3 | 25 | 3.9 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-12b |  |  | 5 | 12 | -
LSIS1262 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 2.5 - 4 | - | 600Y | 3 | 25 | 3.9 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-12 |  |  | 5 | 12 | -
LSIS1263 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 2.5 - 4 | - | 600Y | 3 | 25 | 3.9 | 3 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-16H |  |  | - | - | -
|  |  |  | MC | LSIS | GMC-12M |  |  | 5 | 12 | -
LSIS1265 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 2.5 - 4 | - | 600Y | 3 | 25 | 3.9 | 3 | 2929 | 1
|  |  |  | MC | LSIS | GMC-12 |  |  | 5 | 12 | -
LSIS1265 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 4 - 6 | - | 600Y | 3 | 25 | 6.1 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18a |  |  | 5 | 18 | -
LSIS1266 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 4 - 6 | - | 600Y | 3 | 25 | 6.1 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18b |  |  | 5 | 18 | -
LSIS1267 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 4 - 6 | - | 600Y | 3 | 25 | 6.1 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18 |  |  | 5 | 18 | -
LSIS1269 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 4 - 6 | - | 600Y | 3 | 25 | 6.1 | 5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-18 |  |  | 5 | 18 | -
LSIS1269 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 5 - 8 | - | 600Y | 3 | 10 | 6.1 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18a |  |  | 5 | 18 | -
LSIS1270 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 5 - 8 | - | 600Y | 3 | 10 | 6.1 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18b |  |  | 5 | 18 | -
LSIS1271 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 5 - 8 | - | 600Y | 3 | 10 | 6.1 | 5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18 |  |  | 5 | 18 | -
LSIS1273 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 5 - 8 | - | 600Y | 3 | 10 | 6.1 | 5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-18 |  |  | 5 | 18 | -
LSIS1273 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 6 - 10 | - | 600Y | 3 | 10 | 9 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-18H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18a |  |  | 5 | 18 | -
LSIS1274 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 6 - 10 | - | 600Y | 3 | 10 | 9 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18b |  |  | 5 | 18 | -
LSIS1275 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 6 - 10 | - | 600Y | 3 | 10 | 9 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-18 |  |  | 5 | 18 | -
LSIS1277 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 6 - 10 | - | 600Y | 3 | 10 | 9 | 7.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-18 |  |  | 5 | 18 | -
LSIS1277 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 9 - 13 | - | 600Y | 3 | 10 | 11 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-25a |  |  | 5 | 25 | -
LSIS1278 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 9 - 13 | - | 600Y | 3 | 10 | 11 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-22b |  |  | 5 | 22 | -
LSIS1279 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 9 - 13 | - | 600Y | 3 | 10 | 11 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-25 |  |  | 5 | 25 | -
LSIS1281 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 25 | 9 - 13 | - | 600Y | 3 | 10 | 11 | 10 | 2929 | 1
|  |  |  | MC | LSIS | GMC-22 |  |  | 5 | 22 | -
LSIS1281 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 11 - 17 | - | 600Y | 3 | 10 | 17 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-25a |  |  | 5 | 25 | -
LSIS1282 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 11 - 17 | - | 600Y | 3 | 10 | 17 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-22b |  |  | 5 | 22 | -
LSIS1283 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 11 - 17 | - | 600Y | 3 | 10 | 17 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-25 |  |  | 5 | 25 | -
LSIS1285 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 11 - 17 | - | 600Y | 3 | 10 | 17 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-22 |  |  | 5 | 22 | -
LSIS1285 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 14 - 22 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-25a |  |  | 5 | 25 | -
LSIS1286 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 14 - 22 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-22H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-22b |  |  | 5 | 22 | -
LSIS1287 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 14 - 22 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-25 |  |  | 5 | 25 | -
LSIS1289 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 14 - 22 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1289 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 18 - 26 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-32a |  |  | 5 | 32 | -
LSIS1290 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 18 - 26 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-32 |  |  | 5 | 32 | -
LSIS1292 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 18 - 26 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1292 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 22 - 32 | - | 600Y | 3 | 10 | 27 | 25 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-32a |  |  | 5 | 32 | -
LSIS1293 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 22 - 32 | - | 600Y | 3 | 10 | 27 | 25 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-32 |  |  | 5 | 32 | -
LSIS1295 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 22 - 32 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1295 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 28 - 40 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35a |  |  | 5 | 35 | -
LSIS1296 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-32H | 600Y | 3 | 10 | 28 - 40 | - | 600Y | 3 | 10 | 32 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-32H |  |  | - | - | -
|  |  |  | MC | LSIS | MC-40a |  |  | 5 | 40 | -
LSIS1297 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 6 - 10 | - | 600Y | 3 | 10 | 9 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1298 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 6 - 10 | - | 600Y | 3 | 10 | 9 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1300 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 6 - 10 | - | 600Y | 3 | 10 | 9 | 7.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1300 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 9 - 13 | - | 600Y | 3 | 10 | 11 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1301 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 9 - 13 | - | 600Y | 3 | 10 | 11 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1303 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 9 - 13 | - | 600Y | 3 | 10 | 11 | 10 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1303 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 11 - 17 | - | 600Y | 3 | 10 | 17 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1304 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 11 - 17 | - | 600Y | 3 | 10 | 17 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1306 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 11 - 17 | - | 600Y | 3 | 10 | 17 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1306 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 14 - 22 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1307 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 14 - 22 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1309 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 14 - 22 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1309 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 18 - 26 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1310 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 18 - 26 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1312 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 18 - 26 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1312 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 22 - 32 | - | 600Y | 3 | 10 | 32 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1313 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 22 - 32 | - | 600Y | 3 | 10 | 32 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1315 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 22 - 32 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1315 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 28 - 40 | - | 600Y | 3 | 10 | 32 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1316 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 28 - 40 | - | 600Y | 3 | 10 | 32 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-40 |  |  | 5 | 40 | -
LSIS1318 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 28 - 40 | - | 600Y | 3 | 10 | 27 | 25 | 2929 | 1
|  |  |  | MC | LSIS | GMC-40 |  |  | 5 | 40 | -
LSIS1318 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 34 - 50 | - | 600Y | 3 | 10 | 41 | 40 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1319 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 34 - 50 | - | 600Y | 3 | 10 | 41 | 40 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50 |  |  | 5 | 50 | -
LSIS1321 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 34 - 50 | - | 600Y | 3 | 10 | 32 | 30 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1321 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 45 - 63 | - | 600Y | 3 | 10 | 62 | 60 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS1322 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 45 - 63 | - | 600Y | 3 | 10 | 52 | 50 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-63 |  |  | 5 | 63 | -
LSIS1324 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 45 - 63 | - | 600Y | 3 | 10 | 41 | 40 | 2929 | 1
|  |  |  | MC | LSIS | GMC-65 |  |  | 5 | 65 | -
LSIS1324 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63S | 600Y | 3 | 10 | 47 - 65 | - | 600Y | 3 | 10 | 62 | 60 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS1325 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 25 | 6 - 10 | - | 600Y | 3 | 25 | 9 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1326 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 25 | 6 - 10 | - | 600Y | 3 | 25 | 9 | 7.5 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1328 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 25 | 6 - 10 | - | 600Y | 3 | 25 | 9 | 7.5 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1328 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 25 | 9 - 13 | - | 600Y | 3 | 25 | 11 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1329 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 25 | 9 - 13 | - | 600Y | 3 | 25 | 11 | 10 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1331 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 25 | 9 - 13 | - | 600Y | 3 | 25 | 11 | 10 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1331 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 11 - 17 | - | 600Y | 3 | 10 | 17 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1332 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 11 - 17 | - | 600Y | 3 | 10 | 17 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1334 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 11 - 17 | - | 600Y | 3 | 10 | 17 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1334 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 14 - 22 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1335 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 14 - 22 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1337 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 14 - 22 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1337 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 18 - 26 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1338 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 18 - 26 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1340 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 18 - 26 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1340 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 22 - 32 | - | 600Y | 3 | 10 | 32 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1341 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 22 - 32 | - | 600Y | 3 | 10 | 32 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-35 |  |  | 5 | 35 | -
LSIS1343 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 22 - 32 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-32 |  |  | 5 | 32 | -
LSIS1343 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 28 - 40 | - | 600Y | 3 | 10 | 32 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1344 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 28 - 40 | - | 600Y | 3 | 10 | 32 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-40 |  |  | 5 | 40 | -
LSIS1346 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 28 - 40 | - | 600Y | 3 | 10 | 27 | 25 | 2929 | 1
|  |  |  | MC | LSIS | GMC-40 |  |  | 5 | 40 | -
LSIS1346 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 34 - 50 | - | 600Y | 3 | 10 | 41 | 40 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50a |  |  | 5 | 50 | -
LSIS1347 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 34 - 50 | - | 600Y | 3 | 10 | 41 | 40 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-50 |  |  | 5 | 50 | -
LSIS1349 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 34 - 50 | - | 600Y | 3 | 10 | 32 | 30 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1349 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 45 - 63 | - | 600Y | 3 | 10 | 62 | 60 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS1350 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 45 - 63 | - | 600Y | 3 | 10 | 52 | 50 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-63 |  |  | 5 | 63 | -
LSIS1352 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 45 - 63 | - | 600Y | 3 | 10 | 41 | 40 | 2929 | 1
|  |  |  | MC | LSIS | GMC-65 |  |  | 5 | 65 | -
LSIS1352 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-63H | 600Y | 3 | 10 | 47 - 65 | - | 600Y | 3 | 10 | 62 | 60 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-63 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65a |  |  | 5 | 65 | -
LSIS1353 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 11 - 17 | - | 600Y | 3 | 10 | 17 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1354 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 11 - 17 | - | 600Y | 3 | 10 | 17 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1356 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 11 - 17 | - | 600Y | 3 | 10 | 17 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1356 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 14 - 22 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1357 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 14 - 22 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1359 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 14 - 22 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1359 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 18 - 26 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1360 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 18 - 26 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1362 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 18 - 26 | - | 600Y | 3 | 10 | 22 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1362 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 22 - 32 | - | 600Y | 3 | 10 | 32 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1363 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 22 - 32 | - | 600Y | 3 | 10 | 32 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1365 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 22 - 32 | - | 600Y | 3 | 10 | 32 | 30 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1365 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 28 - 40 | - | 600Y | 3 | 10 | 32 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1366 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 28 - 40 | - | 600Y | 3 | 10 | 32 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1368 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 28 - 40 | - | 600Y | 3 | 10 | 32 | 30 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1368 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 34 - 50 | - | 600Y | 3 | 10 | 41 | 40 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1369 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 34 - 50 | - | 600Y | 3 | 10 | 41 | 40 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1371 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 34 - 50 | - | 600Y | 3 | 10 | 32 | 30 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1371 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 45 - 63 | - | 600Y | 3 | 10 | 62 | 60 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1372 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 45 - 63 | - | 600Y | 3 | 10 | 62 | 60 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1374 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 45 - 63 | - | 600Y | 3 | 10 | 41 | 40 | 2929 | 1
|  |  |  | MC | LSIS | GMC-65 |  |  | 5 | 65 | -
LSIS1374 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 55 - 75 | - | 600Y | 3 | 10 | 62 | 60 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1375 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 55 - 75 | - | 600Y | 3 | 10 | 62 | 60 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75 |  |  | 5 | 75 | -
LSIS1376 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 55 - 75 | - | 600Y | 3 | 10 | 52 | 50 | 2929 | 1
|  |  |  | MC | LSIS | GMC-75 |  |  | 5 | 75 | -
LSIS1377 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 70 - 90 | - | 600Y | 3 | 10 | 77 | 75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-85a |  |  | 5 | 85 | -
LSIS1378 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 70 - 90 | - | 600Y | 3 | 10 | 77 | 75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-85 |  |  | 5 | 85 | -
LSIS1380 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 70 - 90 | - | 600Y | 3 | 10 | 52 | 50 | 2929 | 1
|  |  |  | MC | LSIS | GMC-85 |  |  | 5 | 85 | -
LSIS1380 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 80 - 100 | - | 600Y | 3 | 10 | 77 | 75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-100a |  |  | 5 | 100 | -
LSIS1381 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 80 - 100 | - | 600Y | 3 | 10 | 77 | 75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-95 |  |  | 5 | 95 | -
LSIS1383 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100S | 600Y | 3 | 10 | 80 - 100 | - | 600Y | 3 | 10 | 52 | 50 | 2929 | 1
|  |  |  | MC | LSIS | GMC-85 |  |  | 5 | 85 | -
LSIS1383 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 25 | 11 - 17 | - | 600Y | 3 | 25 | 17 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1384 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 25 | 11 - 17 | - | 600Y | 3 | 25 | 17 | 15 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1386 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 25 | 11 - 17 | - | 600Y | 3 | 25 | 17 | 15 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1386 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 25 | 14 - 22 | - | 600Y | 3 | 20 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1387 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 25 | 14 - 22 | - | 600Y | 3 | 20 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1388 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 25 | 14 - 22 | - | 600Y | 3 | 20 | 22 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1389 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 25 | 18 - 26 | - | 600Y | 3 | 20 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1390 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 25 | 18 - 26 | - | 600Y | 3 | 20 | 22 | 20 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1392 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 25 | 18 - 26 | - | 600Y | 3 | 20 | 22 | 20 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1392 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 20 | 22 - 32 | - | 600Y | 3 | 20 | 32 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1393 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 20 | 22 - 32 | - | 600Y | 3 | 20 | 32 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1395 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 20 | 22 - 32 | - | 600Y | 3 | 20 | 32 | 30 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1395 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 20 | 28 - 40 | - | 600Y | 3 | 20 | 32 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1396 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 20 | 28 - 40 | - | 600Y | 3 | 20 | 32 | 30 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1397 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 20 | 28 - 40 | - | 600Y | 3 | 20 | 32 | 30 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1398 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 20 | 34 - 50 | - | 600Y | 3 | 20 | 41 | 40 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1399 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 20 | 34 - 50 | - | 600Y | 3 | 20 | 41 | 40 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1400 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 20 | 34 - 50 | - | 600Y | 3 | 20 | 32 | 30 | 2929 | 1
|  |  |  | MC | LSIS | GMC-50 |  |  | 5 | 50 | -
LSIS1401 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 10 | 45 - 63 | - | 600Y | 3 | 10 | 62 | 60 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1402 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 10 | 45 - 63 | - | 600Y | 3 | 10 | 62 | 60 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-65 |  |  | 5 | 65 | -
LSIS1404 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 10 | 45 - 63 | - | 600Y | 3 | 10 | 41 | 40 | 2929 | 1
|  |  |  | MC | LSIS | GMC-65 |  |  | 5 | 65 | -
LSIS1404 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 10 | 55 - 75 | - | 600Y | 3 | 10 | 62 | 60 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75a |  |  | 5 | 75 | -
LSIS1405 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 10 | 55 - 75 | - | 600Y | 3 | 10 | 62 | 60 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-75 |  |  | 5 | 75 | -
LSIS1406 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 10 | 55 - 75 | - | 600Y | 3 | 10 | 52 | 50 | 2929 | 1
|  |  |  | MC | LSIS | GMC-75 |  |  | 5 | 75 | -
LSIS1407 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 10 | 70 - 90 | - | 600Y | 3 | 10 | 77 | 75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-85a |  |  | 5 | 85 | -
LSIS1408 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 10 | 70 - 90 | - | 600Y | 3 | 10 | 77 | 75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-85 |  |  | 5 | 85 | -
LSIS1409 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 10 | 70 - 90 | - | 600Y | 3 | 10 | 52 | 50 | 2929 | 1
|  |  |  | MC | LSIS | GMC-85 |  |  | 5 | 85 | -
LSIS1410 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 10 | 80 - 100 | - | 600Y | 3 | 10 | 77 | 75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-100a |  |  | 5 | 100 | -
LSIS1411 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 10 | 80 - 100 | - | 600Y | 3 | 10 | 77 | 75 | 2929 | 1
|  |  |  | Adaptor | LSIS | DA-95 |  |  | - | - | -
|  |  |  | MC | LSIS | MC-95 |  |  | 5 | 95 | -
LSIS1412 | E252942 | 1.1 | F [ version C5] | MSP | LSIS | MMS-100H | 600Y | 3 | 10 | 80 - 100 | - | 600Y | 3 | 10 | 52 | 50 | 2929 | 1
|  |  |  | MC | LSIS | GMC-85 |  |  | 5 | 85 | -